## Master List Templates
Id | Type | Name | Values | Prompting Name
4f727a59-4299-4227-9052-e8b429dd1fd6 | checklist | Fire Dampers |  | Fire Dampers
3e7f85da-877b-4efa-b47b-efce9a349cce | section | Pre-Start Fire Damper
a125b3ab-1bd0-4c4d-8c71-2051fddc6705 | checkpoint | Area clear, access good, enough space for install
6ba5c600-debb-430a-a872-ca1c59e0c7a7 | checkpoint | Duct Route clear, Penetrations complete
79b55644-e611-4038-81bf-3c09f44b52a3 | section | First Fix Fire Damper
7eb77dd2-6432-4ae1-9810-c78af312c5e5 | checkpoint | Correct Fire Damper installed. (Insert Photo)
edb13b58-7d6c-4d0f-a300-f69795250fb9 | checkpoint | Fire Damper installed straight and level with correct orientation.
02e08761-75ee-43d2-9591-b920d72f825a | checkpoint | Breakaway joints either side of fire dampers, taped then cable tied.
d697b986-ba81-4a91-8993-ce055e73dfab | checkpoint | Fire Dampers installed to manufacturers specifications. Drop tested where applicable
cb49af99-b40d-4d66-97f2-46692fef3658 | checkpoint | Access Panels in duct for fire dampers.
28cba624-b158-4d97-8a03-bfa1a24e76d4 | checkpoint | Building Access Panel requirements are marked and given to builders
6a38b280-855c-4c00-8255-23a3f8cf5289 | checkpoint | Plans marked up for As Builts with Access Panel locations
d33ba6eb-28c8-4854-8b42-2940a154e9b8 | section | Second Fix Fire Damper
1d369191-28df-40f0-9afa-3521d492b676 | checkpoint | Fire Damper Label affixed, Asset Number applied.
99fcfadd-4ea2-45ef-b749-c0a4c1d2672b | checkpoint | Fire Dampers Access Panels still accessible for maintenance
5d2eb6ef-1c00-4070-a498-8e46333efb04 | checkpoint | Area left clean and tidy, finger prints removed
ae2acbc5-9afe-4989-8c9f-a1b92fad8b30 | checkpoint | Fire Damper sealed to structure both sides.
f68972b4-6d81-41aa-aa09-4be60adafed1 | section | Commission Fire Damper
35abf88d-b375-479f-8b77-924971281f8a | checkpoint | Drop Tested as applicable
3399aa37-48d7-492c-8a16-93ef940f0411 | checkpoint | Drop Test Motorised Fire Dampers with Fire Engineer.
7be34150-c368-48a3-ba66-611937573253 | checkpoint | Fire Damper Label filled out, photo uploaded.
40670fb4-21e7-4227-bdb5-faa6329dd3e3 | checkpoint | Form TSL05.8A, Fire/Smoke Damper Test Sheet, updated for Project Completion
91a77d34-03fe-4f7c-b402-578d38b427d1 | checkpoint | Commissioning paperwork reviewed and accepted by Project Manager

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
27dabb63-9266-458b-8436-0e33178f731b | checklist | AHU |  | AHU
6c7513f1-4890-4a65-b664-afb65e517a2d | section | Pre-Start
afab0adb-11e1-4b08-aad4-7b3d7fa39ae5 | checkpoint | Area clear, access good, enough space for install
8fa66f2c-c13e-49d6-8df8-5bfacfd6d2e1 | checkpoint | Duct Route clear, Penetrations complete
73220eba-2003-45a5-b73a-770a5f926263 | checkpoint | Nogs/Supports in place
370dfe04-39a6-4c16-8ed5-ca89938e81b9 | section | First Fix
23556a8c-8e65-4442-87d6-8cdfc2a266df | checkpoint | AHU installed straight and level and correct orientation.
dcbb5865-9555-4246-a350-b1fae03caf08 | checkpoint | Cowl sealed to Upstand
52103c20-7767-4df2-92ac-68b1adde335a | checkpoint | Correct AHU installed. (Insert Photo)
17c04cdf-f231-48eb-a111-358481d4b5be | checkpoint | Filter installed and easily accessable
b438e9a3-813e-46fb-bbb1-411dc59a6608 | checkpoint | AHU seismically braced and vibration isolated
0b412b06-7608-4382-a6a2-ffc1d80af5df | checkpoint | Heater Bank installed to Manufacturers instructions
c21996fb-3484-4815-9491-97e36c747788 | checkpoint | Fire dampers installed to manufacturers instructions. Drop tested where applicable
6f75eb11-b38e-4090-ba14-f16e6cff3dc5 | checkpoint | Breakaway joins either side of fire dampers
6d0d0947-a763-46fe-9de1-6f77b594d7c6 | checkpoint | Access Panels in duct for fire dampers, filters, cleaning etc
010ae3e7-8fb7-4ad0-828a-78d447ab4b86 | checkpoint | Ductwork straight/level and well supported incl any seismic restraints
fae8bad0-3e9c-497a-9efe-21f741a61f1d | checkpoint | Duct fittings/joins sealed and mechanically fixed to duct. SAB joins sealed
8860ad13-d1f5-414e-a9ab-4d3dceb9a615 | checkpoint | Balancing Dampers locked open and accessible
a292c71d-9ba0-4025-92f5-2380288ef8e9 | checkpoint | Flexible ducts taped then cable tied
8240f48c-e21e-4651-80fa-e333968f58e6 | checkpoint | Second fix grille and access panel locations recorded and given to TSL PM
2674a6ea-3a05-4bae-b8f2-7d0ada099fa9 | checkpoint | All open ducts sealed off with plastic film or similar
b36d23a5-fa61-49f9-a45b-85be39d426b0 | checkpoint | Control Cables installed
e8decb6f-2d4b-4c8d-b9e5-00816d1d1197 | checkpoint | Power Cables installed
c1d7e91c-66a2-4862-91f4-f39d2f4d7b5f | checkpoint | Building Access Panel requirements are marked and given to builders
45049eaf-e5c1-43ae-845b-dad4a32923b9 | checkpoint | Plans marked up for As Builts and 2nd fix grille locations
c2cf01cb-b722-49b4-949d-914aa2779f9a | section | Second Fix
006ef289-ef9e-4d9a-9536-3f32bbc2e937 | checkpoint | Grilles installed square and level
5478b120-f3ab-4877-88e1-d02a7bd77ce9 | checkpoint | Fans/Filters/Dampers/Access Panels etc all still accessible for maintenance
935502a9-3993-4ea7-a7bc-6045ae4d84d0 | checkpoint | Area left clean and tidy, finger prints removed
cfd24657-0313-4090-a99b-5318783d5fb2 | checkpoint | Controllers fitted off
ee3562da-2c79-4721-84ae-38924f26989a | checkpoint | Power fitted off
bcc8a576-d5cb-4c43-b69e-892b49de7db2 | checkpoint | Plant and controllers labelled
4086bb3d-24b3-416c-9b92-256aa3f7aa8a | section | Commissioning
24517de2-005a-4c6b-8432-21eb2cf94b0e | checkpoint | Commissioned and Paperwork submitted
0d6a6b7a-cb0c-469e-a3dd-b6571a440217 | checkpoint | COC issued
dc058592-7ea2-4037-ac53-845b60f1f531 | checklist | COOLROOM |  | COOLROOM
42dbe844-3006-4c55-9f2d-5d68e18ab95c | section | Pre-Start
789ba7d6-f733-458f-8b60-f3525a60d262 | checkpoint | Area clear, access good, enough space for install
7b4ecc21-c5c9-45b7-b0c4-fe19f9991437 | checkpoint | Area/base ready for outdoor unit
07e0bba5-bc2f-4e6d-8a57-84e229440707 | checkpoint | Area/Base/Walls ready for Coolroom Panels. Floor requirements met.
91ad2a0c-7095-47d7-ad14-8bc756235d47 | checkpoint | Check set down for any rough surfaces (Smooth set down required).
beef81ca-c80e-4488-a6d9-5b0c35644eff | checkpoint | Pipework route all clear, penetrations complete
c5c9875c-9bb8-4b51-aa2a-b837cf3855b4 | checkpoint | Nogs in place
342532ee-944e-4c81-a317-217036cf880c | checkpoint | Drain in place by plumber
2827af94-ff75-4ec1-98e8-94c08972515c | checkpoint | Measure set down and mark out door cut out
92e6f917-0f2a-4741-8dd9-f2813847972d | checkpoint | Check if set down is dry and area is water tight
710107e0-f384-454b-abab-eb01581825f6 | section | First Fix
809b1105-d841-4234-aacc-69c1086f5e65 | checkpoint | Panels installed square, level, tidy. No sharp edges
d78f259d-4c14-424c-8886-430619d1012e | checkpoint | Vapour sealed
19c6e688-4df1-4c08-86b9-bd89fdf2e54a | checkpoint | Evaporator hung straight and level
8d6964c1-358d-4965-8a72-b87a72eef3f0 | checkpoint | Correct Indoor unit installed. (Insert Photo)
699a25d9-0853-453f-81b1-456dbc605c12 | checkpoint | All Panel Penetrations well sealed
c44730f2-b18c-4f5e-b846-02584123c1f5 | checkpoint | Pipework Insulated complete length, glued and taped
98727c4f-6513-43fb-9fdc-72d9172ef4ba | checkpoint | Pipework supported incl any seismic restraints
3e2131da-1838-48dd-bb6a-1c415ff1ba8d | checkpoint | Drain installed and insulated
10d17cd4-a456-44f2-aa5e-f1204bb6d309 | checkpoint | Pipe lengths are recorded accuratley. INSERT PIPE LENGTH (IN NOTES):
93c2558c-3497-47ea-87a7-87ac4c99dc09 | checkpoint | Plans marked up for As Builts
97e06788-2991-4989-9aa1-2cc59159ec3e | section | Second Fix
92b8f56d-44ea-47ff-b27c-733b64766ae6 | checkpoint | Outdoor unit secure and level
69525e26-16c6-45a3-8466-4bb3c38eccc7 | checkpoint | Correct Outdoor unit installed. (Insert Photo)
b2d47e90-7848-4476-b0e8-c50d6ee47b62 | checkpoint | Drain tested
827ab2f0-ec55-4819-aad9-8be9e60c9f4a | checkpoint | Access for future maintenance all clear
3b79d294-62e0-4ddc-93fc-60d585b09e4b | checkpoint | Area left clean and tidy, finger prints removed
335f8a57-db51-44e6-9bbb-e3c6618ee703 | checkpoint | Controllers fitted off
430c04ac-afcb-4e68-b39d-93542a8b6a67 | checkpoint | Power fitted off
bb3761e4-f9f0-4fb7-91c5-29128ebbad07 | section | Commissioning
e3ed9362-4d05-40cc-9c40-36ffe278839f | checkpoint | Commissioned and paperwork submitted
9ebdfb8c-3f66-475d-aacf-b14dc7d66306 | checkpoint | COC issued
b57c3924-f3b8-4814-b051-3642464576ad | checkpoint | Plant and controller labelled
140df735-f3a4-42ea-bff8-1cc042ce9ae3 | checkpoint | Plant and controller labelled
f17d7816-cd1d-4d01-b7c7-a5054aa3ee43 | checklist | EXT FAN |  | EXT FAN
a678af67-2e27-4841-a521-19e41b820c20 | section | Pre-Start
68d46987-18ba-4d2a-9cda-5cef96e98192 | checkpoint | Area clear, access good, enough space for install
e3f60eb2-0862-4d99-895d-781103d63a97 | checkpoint | Duct Route clear, Penetrations complete
140715d2-5668-47a3-93f7-5748e13f4304 | checkpoint | Nogs/Supports in place
cb6b0010-be3f-4d06-af71-1dbea6520e6e | section | First Fix
4a7d5713-03ed-4fc4-9ac8-e901923bee21 | checkpoint | Fan installed straight and level and correct orientation.
e6a0eaff-17c1-4464-b5d5-c063052f32cd | checkpoint | Fan or Cowl sealed to Upstand
252b1436-1327-4d23-b870-bd75aba4be18 | checkpoint | Correct Fan installed. (Insert Photo)
9ad1c5bc-dc66-4eff-84ab-6700ecca6aa2 | checkpoint | Fan seismically braced and vibration isolated
6c7e3c6f-7926-4eee-9527-e9d075d80e20 | checkpoint | Fire dampers installed to manufacturers instructions. Drop tested where applicable
87ab041a-eba8-4ec7-a46f-c69d3f16de99 | checkpoint | Breakaway joins either side of fire dampers
576c24b3-53fe-4f20-b7b8-7c90fb51bf3e | checkpoint | Access Panels in duct for fire dampers, filters, cleaning etc
80fd2ead-3dfa-4a7d-845b-3d0429bfd91e | checkpoint | Ductwork straight/level and well supported incl any seismic restraints
a46969f1-0c77-466e-b996-8efa54a333f9 | checkpoint | Duct fittings/joins sealed and mechanically fixed to duct. SAB joins sealed
ecefc4bb-2bb8-4ed4-ae04-987f8e568a0e | checkpoint | Balancing Dampers locked open and accessible
ea47258d-78a6-446e-b203-18c111d4d27a | checkpoint | Flexible ducts taped then cable tied
1e4da441-a88d-442b-bda2-cb68cf192903 | checkpoint | Second fix grille and access panel locations recorded and given to TSL PM
b35a1af7-90bd-4253-820c-1e8b8973f22f | checkpoint | All open ducts sealed off with plastic film or similar
bdbd9ee4-aa4f-4c80-aa1b-64a80ec14e6f | checkpoint | Control Cables installed
5ba05baf-1dac-4d3f-b2a9-d225ecf05301 | checkpoint | Power Cables installed
0817335f-3cd2-4ff5-8b4a-0c4f5bc1b939 | checkpoint | Building Access Panel requirements are marked and given to builders
13ee7ddb-455a-4e75-9b87-98117dda8e1a | checkpoint | Plans marked up for As Builts and 2nd fix grille locations
248532de-842c-4066-ac76-470ae35b4d2d | section | Second Fix
02de5b13-a0ec-4e96-a3e1-de74f705fd44 | checkpoint | Grilles installed square and level
51c1c19d-334d-48c7-97e7-519a9c18009d | checkpoint | Fans/Filters/Dampers/Access Panels etc all still accessible for maintenance
42c7a5a2-ef93-4d9a-bfae-831ccc178a00 | checkpoint | Area left clean and tidy, finger prints removed
37f2b18e-1b4f-407d-b063-6376f491db63 | checkpoint | Controllers fitted off
fb6b5d7f-3a22-4694-a2c2-518a3f6dbc6e | checkpoint | Power fitted off
51b803fb-497f-424f-ba58-7ce794736209 | checkpoint | Plant and controllers labelled
5725542c-67e8-414a-8bc7-816021f4fdf3 | section | Commissioning
1a4e0111-e81a-4f46-8bd5-7bf6cc3f2158 | checkpoint | Commissioned and Paperwork submitted
4e129a0b-73e7-496d-ad41-53098ea321f1 | checkpoint | COC issued
2afb2fa4-0b28-47ac-bf77-118e05e4a630 | checkpoint | Plant and controller labelled
61c8dfd0-4944-4320-bac1-f2af27992d4b | checklist | HRV |  | HRV
45143f95-1124-4acb-a118-fc8b05867413 | section | Pre-Start
2b99f94f-234b-495d-96b7-58ded04e350f | checkpoint | Area clear, access good, enough space for install
5b13c5cf-79fb-4445-b856-b708089f9556 | checkpoint | Duct Route clear, Penetrations complete
23021063-a4b9-49e0-a65f-3ca3f803a45e | checkpoint | Nogs/Supports in place
42797648-db89-44a1-81e0-1ba803277f0f | section | First Fix
e583bc87-4bea-4c0f-b2c4-4a0bcafce40f | checkpoint | HRV installed straight and level and correct orientation.
c8c7f8d6-cc28-4dee-8c7d-a08c3f115693 | checkpoint | Cowl sealed to Upstand
51461331-02fb-4b5b-b574-9d963ac73467 | checkpoint | Correct HRV installed. (Insert Photo)
9971ff2c-82bb-4768-8ee1-4283a9a88a4e | checkpoint | Filter installed and easily accessable
8461174d-be6e-4f31-8595-518bf2719f2f | checkpoint | HRV seismically braced and vibration isolated
fc2339d2-704e-4518-be49-173cb29c04c8 | checkpoint | Heater Bank installed to Manufacturers instructions
15c91ad3-69b4-43a0-a478-fbedd3ff1f41 | checkpoint | Fire dampers installed to manufacturers instructions. Drop tested where applicable
57c9aef6-8977-43aa-8b5a-b7dbd11ece18 | checkpoint | Breakaway joins either side of fire dampers
39cdd8dc-3a7a-42a5-a3e0-02841962cf41 | checkpoint | Access Panels in duct for fire dampers, filters, cleaning etc
a7078af4-f9de-42e4-9764-148175f3c523 | checkpoint | Ductwork straight/level and well supported incl any seismic restraints
3ec5794d-ad80-4cce-a630-119422f13157 | checkpoint | Duct fittings/joins sealed and mechanically fixed to duct. SAB joins sealed
ec21e306-a4cf-4f69-8384-7dd8b1cae724 | checkpoint | Balancing Dampers locked open and accessible
240a3c77-3304-4226-88f5-ea14afabe9c7 | checkpoint | Flexible ducts taped then cable tied
a5773363-2145-4728-9fe4-e28362ee03e6 | checkpoint | Second fix grille and access panel locations recorded and given to TSL PM
fc5418fe-55dc-4b6c-868b-1914bb119bc3 | checkpoint | All open ducts sealed off with plastic film or similar
8b18eeb4-2963-4e71-b0b5-173c919ef5c0 | checkpoint | Control Cables installed
4c235633-1b89-498d-b755-684d6b0d79cd | checkpoint | Power Cables installed
ed990488-00da-4e79-838e-6689733197c7 | checkpoint | Building Access Panel requirements are marked and given to builders
bc22274d-aaa3-439d-9ec1-bfc9b7c8dabc | checkpoint | Plans marked up for As Builts and 2nd fix grille locations
453f67f9-b528-4acb-a806-bf914b22f691 | section | Second Fix
c7aa79d0-b2d1-4706-b7ac-d8778b5c9604 | checkpoint | Grilles installed square and level
0e2cda70-bbba-4a71-9b79-4d3724f4fcbe | checkpoint | Fans/Filters/Dampers/Access Panels etc all still accessible for maintenance
b147856f-4dc3-49a6-895e-edc23d56cce4 | checkpoint | Area left clean and tidy, finger prints removed
80e1684d-672c-47ef-bc72-8764138024b5 | checkpoint | Controllers fitted off
a1e4b51c-d718-4027-931b-f3b891327976 | checkpoint | Power fitted off
44caab2f-0aba-47cd-9c10-8d090b7d9db3 | checkpoint | Plant and controllers labelled
5dcd9904-c1e8-43ea-9e59-745729d74d64 | section | Commissioning
53e62bf4-aad7-4f7d-8878-c6d9c9fb7835 | checkpoint | Commissioned and Paperwork submitted
e1ee3b99-da01-4636-991c-f93c0cff29b9 | checkpoint | COC issued
cf2c2d6e-9a44-4cec-a32c-185fcea56633 | checklist | KITCH EXT FAN |  | KITCH EXT FAN
ff65ce21-ec8d-48be-9133-4fca64ba7fae | section | Pre-Start
4e9bcd5c-1ce8-4651-bef0-71910d3b9180 | checkpoint | Area clear, access good, enough space for install
2d8e4808-e09c-4cdb-86e5-ee0416fa28d9 | checkpoint | Duct Route clear, Penetrations complete
03bb9afb-5084-4ffa-9354-d03bf5c8a256 | checkpoint | Nogs/Supports in place
53b5f79a-c2c8-4ff1-954b-3358f878d379 | section | First Fix
b40158d7-b7b4-4d98-8678-69fd65467831 | checkpoint | Fan installed straight and level and correct orientation.
6b67550d-5705-4f1a-8ff5-04e05431b8bb | checkpoint | Fan or Cowl sealed to Upstand
7e3e88b9-3c5a-4928-8b92-43ac631849e7 | checkpoint | Correct Fan installed. (Insert Photo)
74a52798-be08-471f-8044-4068d21f7e61 | checkpoint | Fan seismically braced and vibration isolated
8f8070c2-95cd-49e7-a213-17867e74764a | checkpoint | Access Panels in duct for fire dampers, filters, cleaning etc
85f5119a-5819-4985-8c68-1d8bebda41c8 | checkpoint | Ductwork straight/level and well supported incl any seismic restraints
77534059-4da4-4900-92a2-b44c954daa10 | checkpoint | Duct fittings/joins sealed and mechanically fixed to duct. SAB joins sealed
fafadca5-ea19-4d74-b833-f3ef30e0b543 | checkpoint | Second fix grille and access panel locations recorded and given to TSL PM
84ed68f0-7f89-41af-9bdd-5813246591b7 | checkpoint | All open ducts sealed off with plastic film or similar
44ab5bb4-f886-4c74-84a1-c9c65495e151 | checkpoint | Control Cables installed
9987c906-2a6e-41a0-8a5e-cbfaa81c0659 | checkpoint | Power Cables installed
f1102118-1059-4345-a13d-99505b2b744a | checkpoint | Building Access Panel requirements are marked and given to builders
9dfc4d22-9a53-4bc2-b2b8-f4661abf9f50 | checkpoint | Plans marked up for As Builts and 2nd fix grille locations
3fd005a1-34ae-4f1f-ac79-1f7996f4ab96 | section | Second Fix
6570c52c-df32-425b-afa0-602f2e4a752e | checkpoint | Hoods and Grilles installed square and level
e34a8cc9-b409-43a3-a205-73c3d4f7bc7f | checkpoint | Fans/Filters/Dampers/Access Panels etc all still accessible for maintenance
671da5fa-32ec-414e-8f04-4e7f18055f31 | checkpoint | Area left clean and tidy, finger prints removed
5f06d68c-4ef9-4f77-8b03-380414f3811c | checkpoint | Controllers fitted off
3c7206fa-4ce0-4cea-b1ff-6d502c5a216d | checkpoint | Power fitted off
1032bed1-26e0-4f5b-9185-781677957ab1 | checkpoint | Plant and controllers labelled
4213ee65-04f7-4d7a-aaf2-974df0dbdfb8 | section | Commissioning
840ec5c2-313c-4b6e-b186-4ca782f73136 | checkpoint | Commissioned and Paperwork submitted
33116c6e-e973-4a02-8234-b629e2f09a43 | checkpoint | COC issued
b33b6884-3543-4f7b-89b8-4bcb5739022b | checkpoint | Plant and controller labelled
60e9a1de-3c43-4b98-a65a-c82e5ce07c6f | checklist | SA FAN |  | SA FAN
00aed445-ed6d-4772-aebd-d640ac217b3f | section | Pre-Start
c57b6d71-69f4-4b51-9591-242b7a65b59a | checkpoint | Area clear, access good, enough space for install
3df31411-fb3c-49db-8d07-c316d373da68 | checkpoint | Duct Route clear, Penetrations complete
a3fc5db9-50fa-4baa-9b29-91a086ed2b90 | checkpoint | Nogs/Supports in place
b0cf0ee8-eeaf-44a7-9e96-4b2edcbde7c5 | section | First Fix
eeffc1dd-dd58-4cb2-b729-65d1cd5fbabc | checkpoint | Fan installed straight and level and correct orientation.
5c3f38a2-6e36-4ee5-9099-0abf24e4e994 | checkpoint | Fan or Cowl sealed to Upstand
54b85c23-c6e7-4dd3-af8f-3cad9863b9f9 | checkpoint | Correct Fan installed. (Insert Photo)
bb4bd969-954a-41db-b245-9355f7d5b4cc | checkpoint | Correct Heater Bank Installed. (Insert Photo)
71f9ce17-5750-4744-b4e9-e6ff583892a9 | checkpoint | Fan seismically braced and vibration isolated
abd251ee-4ade-4d18-94e3-2ce5edcb3c74 | checkpoint | Fire dampers installed to manufacturers instructions. Drop tested where applicable
99c38bbf-a9d9-49b1-837d-13811b727180 | checkpoint | Breakaway joins either side of fire dampers
1e3d33cc-fa37-49cf-966a-f779f9d3e347 | checkpoint | Access Panels in duct for fire dampers, filters, cleaning etc
3f129768-0519-4b30-89a9-191e7d19da54 | checkpoint | Ductwork straight/level and well supported incl any seismic restraints
f5dc2ca1-8368-4bd9-a523-84927aae4135 | checkpoint | Duct fittings/joins sealed and mechanically fixed to duct. SAB joins sealed
f2e28594-6246-4a48-94f0-880a4123711e | checkpoint | Balancing Dampers locked open and accessible
6bf5f539-7417-4c0d-9397-03079b6795dc | checkpoint | Flexible ducts taped then cable tied
f7fee62b-c7a1-4388-813e-37bdde1ce405 | checkpoint | Second fix grille and access panel locations recorded and given to TSL PM
f8353fcb-c7e2-4e11-ab96-724607868e1e | checkpoint | All open ducts sealed off with plastic film or similar
ea6d72d4-308f-4273-8021-c702a0079dc0 | checkpoint | Control Cables installed
8cd68626-2e29-43b1-b6c0-627d37418a10 | checkpoint | Power Cables installed
c1aeb8eb-3635-4e2d-8508-f48fa62b5c11 | checkpoint | Building Access Panel requirements are marked and given to builders
9a58f555-df24-4c6e-aabb-8438dfcfc906 | checkpoint | Plans marked up for As Builts and 2nd fix grille locations
dbd0815a-2263-4dc8-bfaa-345306c45319 | section | Second Fix
edc88a76-4571-488c-b3e9-f0f2f1e55c3b | checkpoint | Grilles installed square and level
2f7bf463-b397-43c1-8066-71c3b84d9981 | checkpoint | Fans/Filters/Dampers/Access Panels etc all still accessible for maintenance
330482c2-1b08-436b-abc8-20da88a04d75 | checkpoint | Area left clean and tidy, finger prints removed
46568bc5-690d-4885-9316-fb63dd194ddb | checkpoint | Controllers fitted off
c6a296bd-d6f7-4465-ae24-edb929e97a9d | checkpoint | Power fitted off
dfce6884-12a1-482e-aa1e-43b7611a59d6 | checkpoint | Plant and controllers labelled
51764038-00d5-48d7-a159-99b287da3db1 | section | Commissioning
4e8de353-670d-40da-88af-99f624cbdf57 | checkpoint | Commissioned and Paperwork submitted
4f56cc53-e32b-4dcf-b75b-3ae0beab90f3 | checkpoint | COC issued
c50148b2-79da-4d7d-9f4e-ad88ebc04769 | checkpoint | Plant and controller labelled
14cb1f59-2751-4152-91ff-5437f87a4d7c | checklist | SPLIT DUCTED |  | SPLIT DUCTED
3e0eab71-1ee9-4e08-9a45-afad1e67198c | section | Pre-Start
c085e8e6-41a3-4982-8ab5-15180796c497 | checkpoint | Area clear, access good, enough space for install
5e225b82-dbb8-4076-9af7-4ea20923feb1 | checkpoint | Area/base/wall ready for outdoor unit
ce7f1d01-383c-4261-a096-1f0963c17227 | checkpoint | Pipework route all clear, penetrations complete
b13bab4d-a89b-4114-b495-056b71f044cd | checkpoint | Nogs in place
974c06b6-a2ad-4024-8145-68d30d423775 | checkpoint | Drain 1m from Indoor unit location by plumber
0908f553-3fb4-47ef-a296-d134468c164a | section | First Fix
ca2a6a34-1a8f-4758-849d-b95a77c17879 | checkpoint | Pipework Insulated, glued and taped complete length
4d1f8701-f77a-44ac-a760-369aa7ddc5c5 | checkpoint | Pipework supported incl any seismic restraints
46cc75e5-25e0-4a1e-8d5d-2aee78849a03 | checkpoint | Indoor unit level, secure, vibration isolated and seismically retsrained
be2f056d-6942-4062-b477-6f8430b988f8 | checkpoint | Correct unit installed. (INSERT PHOTO)
62a4c92b-9b3d-4999-885a-be7f26b578f2 | checkpoint | Drain installed and insulated
6b11a2d6-0777-4ef6-a028-30aeec2cacda | checkpoint | Pipe lengths are recorded accuratley. INSERT PIPE LENGTH (IN NOTES):
235f340b-1af4-4a98-b2a6-eb0571fc8a35 | checkpoint | Control cables installed
65f2e851-e8ef-4d98-bec4-db572ba7c820 | checkpoint | Power Cables installed
cb62ed00-0fcc-4525-b3cc-4216f2113ffe | checkpoint | Access Panel requirements are marked and given to builders
47433099-d069-4b0b-b266-0126230a1cac | checkpoint | Fire dampers installed to manufacturers instructions. Drop tested where applicable
d86b6d0c-e839-4eda-8036-f793f82ab993 | checkpoint | Breakaway joins either side of fire dampers
cce36fcc-79d7-4080-b4da-1a990acc6aaf | checkpoint | Access Panels in duct for fire dampers, filters, cleaning etc
d1d15598-74ef-42d4-bf55-234fdf570ab0 | checkpoint | Ductwork straight/level and well supported incl any seismic restraints
1b5d6374-8693-45b6-a90e-8fa2985e2986 | checkpoint | Duct fittings/joins sealed and mechanically fixed to duct. SAB joins sealed
4f75db65-c097-4431-acfb-2039cfa12c67 | checkpoint | Balancing Dampers locked open and accessible
4678f13a-ac29-4fd8-9d5c-5cd40a53cdfb | checkpoint | Flexible ducts taped then cable tied
bf3cc38c-e7b8-4013-b4e4-3030f8b92f2c | checkpoint | Second fix grille and access panel locations recorded
199f5b38-25e2-4b0c-8553-ca10854b30b3 | checkpoint | All open ducts sealed off with plastic film or similar
1e0f9d09-bd11-4eca-8636-e2109a38d85f | checkpoint | Plans marked up for As Builts
3e060eab-3e23-41fc-a653-29acee3c5485 | section | Second Fix
a9e36e48-2a88-42c8-9021-ccb1aa733a41 | checkpoint | Correct Outdoor unit installed. (Insert Photo)
b0e52bb9-82da-45e2-8d3b-2633904d10eb | checkpoint | Outdoor unit level and secure
98d8ade4-77a6-4a20-8c88-a8348f13e706 | checkpoint | Grilles installed flush and square
3020b850-7f36-417f-961a-bf862531eb80 | checkpoint | Access for future maintenance all clear. Filter can be easily removed
fc4719a6-ff65-4057-9f21-86f85bbeca92 | checkpoint | Area left clean and tidy, finger prints removed
627817f4-4297-4553-9207-0ed7cb8aee8b | checkpoint | Controllers fitted off
8d9d4c91-f15e-4478-a3d0-0d98c328334b | checkpoint | Power fitted off
e90c5764-3f8d-4ebd-a277-c7cbcb947ddf | section | Commissioning
001396ab-3221-420e-a8d0-c036319aebd1 | checkpoint | Commissioned and paperwork submitted
71d7f4cd-eaf1-4b6e-884a-2b4f7f8cc505 | checkpoint | COC issued
8ffa972d-8f5a-431f-8899-2488d8fed3a2 | checkpoint | Plant and controller labelled
92e4d258-914e-4dc4-ab5c-ce3ac7bde920 | checklist | SPLIT HW |  | SPLIT HW
1f1d1707-9b2b-4a36-b693-f633b8807d69 | section | Pre-Start
4967edcc-180e-4d61-ab4d-226481d1b0db | checkpoint | Area clear, access good, enough space for install
763877b6-896e-4da9-baf4-3f2ecff62a29 | checkpoint | Area/base/wall ready for outdoor unit
fc81ee51-f331-490b-8d9b-f14b11e144a7 | checkpoint | Pipework route all clear, penetrations complete
0add02ff-8436-45d8-8f84-5e462fc9b217 | checkpoint | Nogs in place
9243785e-8a91-45ff-9b8c-5aa6f60a9767 | checkpoint | Drain 1m from Indoor unit location by plumber
219d26ee-bdff-40d5-9ee9-e9a6e44405a9 | section | First Fix
23f1b5bc-4ef9-4c65-9598-ccc5415899dc | checkpoint | Pipework Insulated complete length, glued and taped
9c53a12e-56c4-41e0-96bd-221a5799e008 | checkpoint | Pipework supported incl any seismic restraints
97fd8bcf-0210-40cd-adcc-beb39c9ff0d8 | checkpoint | Drain installed and insulated
816de49f-d4c8-4692-8d96-b722febb1008 | checkpoint | Pipe lengths are recorded accuratley. INSERT PIPE LENGTH (IN NOTES):
81418be7-dfd7-48e6-94d9-47f6a77cee3f | checkpoint | Control cables installed
f4716553-10f0-453e-adda-2f8786625e9a | checkpoint | Power Cables installed
2be8f586-6f51-4dc8-b72c-1e3665d7311f | checkpoint | Plans marked up for As Builts
9108bd05-1cf1-4300-a599-30ac0d95bddb | section | Second Fix
4f20b66e-670e-4c17-9e84-5497a1077a41 | checkpoint | Correct Indoor unit installed. (Insert Photo)
dcfb2f95-9a89-4c31-8a86-9b2eead00f51 | checkpoint | Correct Outdoor unit installed. (Insert Photo)
a66658b9-7f70-4c5a-9beb-cd4df0f4bc34 | checkpoint | Outdoor unit level and secure
b41dbc6c-325d-440c-8959-fe706eb5fed3 | checkpoint | High Wall cover installed flush and square
2e8496d6-715d-48d2-b5f9-293a87496d43 | checkpoint | Area left clean and tidy, finger prints removed
4c2fe31f-5d92-4acc-8cab-1eff5bda64bc | checkpoint | Controllers fitted off
42f7f501-f784-407d-ac0a-4fe95a902fee | checkpoint | Power fitted off
1ec56ff1-3f55-4335-abb9-18332f44f282 | section | Commissioning
1440d5c1-80e0-4e7b-9572-88279ec9e089 | checkpoint | Commissioned and paperwork submitted
024da3b7-a2f8-4573-9c06-6e673de9f1a8 | checkpoint | COC issued
2cf0db31-c6aa-4de4-8bac-813527ba76a3 | checkpoint | Plant and controller labelled
6e8bb05a-5e79-43c7-9bba-44f6a1e054a5 | checklist | VRV Cass |  | VRV Cass
cd1dbbbc-d8e9-44ff-bba8-20c200b8e9ce | section | Pre-Start
8bbcf9d9-349d-4fe0-baeb-10d1680d24a6 | checkpoint | Area clear, access good, enough space for install
ebb59860-0649-4c02-81b3-dce0b91c38ed | checkpoint | Pipework route from BS to Indoor unit all clear, penetrations complete
1c3e6f54-77ae-4bb2-84b3-72e7a47acc5e | section | First Fix
6b65455c-25ca-4807-aaf6-af77a1520056 | checkpoint | Pipework connected to BS Box and Indoor unit
2fe16faf-8196-4e26-888a-42fcdd00a867 | checkpoint | Pipework Insulated, glued and taped complete length
3628a637-4a4a-4e77-a703-48dedf318767 | checkpoint | Pipework supported incl any seismic restraints
41b619e3-bb71-4501-8222-a498bd4244d7 | checkpoint | Indoor unit level, secure, vibration isolated and seismically retsrained
8cae04d9-46d6-491a-aec5-79d7ad56565f | checkpoint | Correct unit installed. (INSERT PHOTO)
665715f8-81d5-4e5a-bf2b-da62bb1062d7 | checkpoint | Drain installed and insulated
537d5894-f4b3-4b14-bc28-68b6970a0528 | checkpoint | Pipe lengths are recorded accuratley. INSERT PIPE LENGTH (IN NOTES):
e3ccf87e-9e7e-44a1-b228-efd219449115 | checkpoint | Control cables installed
e34af858-6ea7-49dd-bed6-3b64c4b81a60 | checkpoint | Power Cables installed
d9c64222-6a24-4b65-b286-fe2e621523a9 | checkpoint | Access Panel requirements are marked and given to builders
dc6f5b7c-8cc9-4133-953c-7c6039f77335 | checkpoint | Plans marked up for As Builts
1dad3c2e-e220-4424-ba99-7737d9a128ed | section | Second Fix
e0b89276-38fa-4691-be66-2c1675e0f949 | checkpoint | Face plate installed flush and square
d7e8cab7-9fc8-403e-a288-44237723e09d | checkpoint | Access for future maintenance all clear. Filter can be easily removed
5cee7a02-1592-4b6a-8618-0335313cfec2 | checkpoint | Area left clean and tidy, finger prints removed
ab5c7778-d1ae-4ea4-9a25-a0a9786c0880 | checkpoint | Controller fitted off
bbe983e0-7f35-4248-b670-306be1a13e48 | checkpoint | Plant and controller labelled
e31e8fb8-12ab-4c31-bbcc-bcf50f6ee7ee | checklist | VRV DUCTED |  | VRV DUCTED
f4bc2dec-2193-4638-b18d-128e6c16496b | section | Pre-Start
933d1976-8605-4363-a8d2-b349e7917c1c | checkpoint | Area clear, access good, enough space for install
6388201b-ccf0-4c55-bfbc-ebba32367e98 | checkpoint | Pipework route from BS to Indoor unit all clear, penetrations complete
4d7add47-df96-4570-8625-08ab35da8390 | section | First Fix
10783e86-0f9d-4c54-879c-d97ddb9e1f83 | checkpoint | Pipework connected to BS Box and Indoor unit
630ff73a-0f22-40b5-a217-1e91597ee749 | checkpoint | Pipework Insulated, glued and taped complete length
0865b24b-bc25-4083-ac3c-97cce94111fb | checkpoint | Pipework supported incl any seismic restraints
4509f8c0-9380-4773-b0e8-6ca2c04af98a | checkpoint | Indoor unit level, secure, vibration isolated and seismically retsrained
0a939e4b-fc4b-4252-9847-89ecf13da221 | checkpoint | Correct unit installed. (INSERT PHOTO)
1a9fe792-9358-457a-8d71-3f3b3f0a2c12 | checkpoint | Drain installed and insulated
248676ad-7aa7-43d4-a7f8-0da99c134559 | checkpoint | Pipe lengths are recorded accuratley. INSERT PIPE LENGTH (IN NOTES):
b3db546b-bdbe-4cad-9e55-ce6c27fc1359 | checkpoint | Control cables installed
6bb317fe-7c8f-4799-abf2-642191147700 | checkpoint | Power Cables installed
f230b15d-8790-4e54-9215-3d0a1e5f6a5e | checkpoint | Access Panel requirements are marked and given to builders
02d62058-2406-477d-b911-917dead02a25 | checkpoint | Fire dampers installed to manufacturers instructions. Drop tested where applicable
d83faac2-3cd3-46cb-bf63-896dc8de0a7a | checkpoint | Breakaway joins either side of fire dampers
06dce02f-cd1e-4447-80f3-026f48617554 | checkpoint | Access Panels in duct for fire dampers, filters, cleaning etc
7fdb94e4-8c74-438f-80c7-b497484a8776 | checkpoint | Ductwork straight/level and well supported incl any seismic restraints
36d08792-4124-4d68-a431-c87acbfe2e9a | checkpoint | Duct fittings/joins sealed and mechanically fixed to duct. SAB joins sealed
995dd46d-d279-4448-99f7-32a9167d8ddb | checkpoint | Balancing Dampers locked open and accessible
962514d8-16ef-4855-8a54-031eac344249 | checkpoint | Flexible ducts taped then cable tied
837d097f-89cb-4109-980f-19fad9dee69b | checkpoint | Second fix grille and access panel locations recorded
48139e53-49e7-4be4-bf75-234241833555 | checkpoint | All open ducts sealed off with plastic film or similar
0a9e9189-0b33-4d07-876f-a8bb9ad8684b | checkpoint | Plans marked up for As Builts
d79312b2-cb7c-4780-b901-8237855ffec1 | section | Second Fix
81d86176-ee84-4ffd-9199-b74b030d9ac2 | checkpoint | Grilles installed flush and square
a5335192-530d-4b8e-b09e-f727fdb2be38 | checkpoint | Access for future maintenance all clear. Filter can be easily removed
41997a96-f4de-4745-879e-8b89549a2cf4 | checkpoint | Area left clean and tidy, finger prints removed
c68196ff-1ccf-4570-82e3-c52edfef3e01 | checkpoint | Controller fitted off
8d2341f9-f198-4db8-8805-54675a938800 | checkpoint | Plant and controller labelled
7469307b-bdea-40c6-ac38-ab35fd5c0d85 | checklist | VRV HW |  | VRV HW
06c5b6f6-7fe9-4647-996b-4079f41e2b65 | section | Pre-Start
e8aaa16d-e0e2-469e-a1ff-d9c0edbc6a6c | checkpoint | Area clear, access good, enough space for install
d64de2bc-7fa4-4135-984a-7718b3e4ddd9 | checkpoint | Pipework route from BS to Indoor unit all clear, penetrations complete
5efdcf15-c63c-41bd-856a-74666e8ca8dd | section | First Fix
259ba956-df59-4167-ac7c-1fd01968d283 | checkpoint | Pipework connected to BS Box and run to Indoor unit location
5340f84b-ce6d-43db-93e3-002afcc4c1bc | checkpoint | Pipework Insulated, glued and taped complete length
af081337-07fe-41b5-a186-93fc81a152f8 | checkpoint | Pipework supported incl any seismic restraints
2c98a22e-88a2-4c14-a602-b67adec954af | checkpoint | Drain installed and insulated
034bc777-eb6f-47c0-9684-f1d3e4bef601 | checkpoint | Pipe lengths are recorded accuratley. INSERT PIPE LENGTH (IN NOTES):
ecee64ae-c986-44b6-8162-d0d4c3a7284b | checkpoint | Control cables installed
b4d61813-bada-4775-a401-83d45d1997ad | checkpoint | Power Cables installed
4a2750f8-8327-4bf2-98d4-687c438e3c8f | checkpoint | Plans marked up for As Builts
0425fa74-943d-4630-abeb-a3b504ceb3e2 | section | Second Fix
f044dfb2-b527-48fa-b082-b0713317b5bd | checkpoint | Unit installed flush and square
5431e7f1-16c3-41e8-966b-bb12d986a518 | checkpoint | Correct Unit installed (Insert Photo)
f11074cf-5e3f-44a5-8bc9-26c945081873 | checkpoint | Area left clean and tidy, finger prints removed
5bb8fbe8-2744-4dde-b2ea-413485d6308c | checkpoint | Controller fitted off
c24aeece-104d-4572-bb11-d42451596568 | checkpoint | Plant and controller labelled
092542e9-8a55-4aa8-b822-86520f4b59f0 | checklist | VRV OU |  | VRV OU
06f0d922-0fcf-43f1-8718-6fe29f7abb0c | section | Pre-Start
7a79f995-9c3e-4860-9eff-e79abfe81889 | checkpoint | Area/base ready for outdoor unit
57548678-1c8f-457e-b50a-a29c51f52fee | checkpoint | Any required drains in place
b36d5e36-2a50-463c-a93f-b56a01cd5393 | checkpoint | Outdoor unit area accessible
50c099b0-81f1-4684-9f5f-5c9b7e3f0569 | checkpoint | Pipework route from OU to BS box all clear, penetrations complete
9bb74ed2-f2a0-4d1e-849a-af8d2462f5bf | checkpoint | Area clear for BS Box installation
e247ac8b-3cd1-4330-b92f-2f811cc5460a | section | First Fix
10a046b6-4981-4b02-9e49-13b516d7780e | checkpoint | Outdoor unit brackets/feet/strut in place
67d849f6-e08e-49ba-aec3-d381bd018c40 | checkpoint | Unit level, secure, bolted down, seismically restrained
44b9821c-123a-442b-b2cd-99941b1c6570 | checkpoint | Correct VRV unit installed. (INSERT PHOTO)
2aa347f0-6628-4ff8-bc99-662d0269fabd | checkpoint | Pipework connected from OU unit to BS box
94e66c1d-2135-4d65-bd27-33a2adf0d811 | checkpoint | Pipework Insulated, glued and taped
d53e8e8a-c6c3-45f8-9e1e-9f2c1dcd89ae | checkpoint | Pipework supported incl any seismic restraints
459aac61-f096-427d-9ccf-deed1ba9bdb7 | checkpoint | Pipework supported up off the ground
2bae332c-1f74-4817-92d5-420eb084e066 | checkpoint | Refnets installed as per Manufacturers Instructions
435532fb-b74a-4f13-80a9-5aee0d02cda5 | checkpoint | BS Box level, secure and seismically retsrained
ce15af24-7b6b-4ac9-85ae-7ecd9d26ab8a | checkpoint | Correct BS unit installed. (INSERT PHOTO)
28b2886c-2d6a-42cc-9455-4eb47dbc8fcc | checkpoint | Drain installed and insulated
e01b12e4-7aad-4208-ad98-da753c2316b5 | checkpoint | Pipe lengths are recorded accuratley. INSERT PIPE LENGTH (IN NOTES):
f5d57617-9526-4cb3-af5b-43c5315d7264 | checkpoint | Access Panel requirements are marked and given to builders
805234b4-697a-46cc-82c7-0f13ffe40d36 | checkpoint | Plans marked up for As Builts
7db2d627-468f-450c-91bd-62cdfaf66386 | section | Commissioning
fcde9456-6a0e-4009-8eff-89fc63faec45 | checkpoint | Access to OU unit is good
441bca6f-cf39-4940-93f8-9daebfac5f2d | checkpoint | Access to BS Box is good
ba9db7ae-b9fe-4ecf-8a0a-0329428ca0fe | checkpoint | Access to Indoor units is good
0ffb4a4d-8edd-4ad5-b8c1-6c8c21ae48be | checkpoint | Pre-commissioning paperwork completed and sent to TSL PM
25c82333-50ca-4a78-ac95-8b09c080ec8b | checkpoint | Power on to compressor for 24 hours (impt: only once evac completed)
9e8071ac-5c05-4ec5-9dd3-b852a5ce0578 | checkpoint | Commissioned by Supplier
acc19965-f04a-4263-9425-dae2459b98ba | checkpoint | All plant labelled incl OU/BS/Indoors/Controllers/Pipework