## Fire Dampers
Pre-Start Fire Damper
Area clear, access good, enough space for install
Duct Route clear, Penetrations complete
First Fix Fire Damper
Correct Fire Damper installed. (Insert Photo)
Fire Damper installed straight and level with correct orientation.
Breakaway joints either side of fire dampers, taped then cable tied.
Fire Dampers installed to manufacturers specifications. Drop tested where applicable
Access Panels in duct for fire dampers.
Building Access Panel requirements are marked and given to builders
Plans marked up for As Builts with Access Panel locations
Second Fix Fire Damper
Fire Damper Label affixed, Asset Number applied.
Fire Dampers Access Panels still accessible for maintenance
Area left clean and tidy, finger prints removed
Fire Damper sealed to structure both sides.
Commission Fire Damper
Drop Tested as applicable
Drop Test Motorised Fire Dampers with Fire Engineer.
Fire Damper Label filled out, photo uploaded.
Form TSL05.8A, Fire/Smoke Damper Test Sheet, updated for Project Completion
Commissioning paperwork reviewed and accepted by Project Manager