## Table 1
WORK AREA: Rawhiti St Morningside |  |  | CONTRACT NAME: Morningside Flood Mitigation Pump Station |  |  | DESCRIPTION OF ACTIVITY: SP1 Construction Works |  | Rev |  | Originator | Date |  | Approved | Date
[8 empty] | 0 |  | Casey Aubrey | 2025-01-22 |  | Grant Little | 2025-02-13
ITP No: 01
Item No. | ITEM | ACTIVITY TASK |  | ACCEPTANCE CRITERIA | FREQUENCY |  | Hold Point |  | CERTIFYING DOCUMENTATION, RECORD OR CHECKSHEET |  |  | VERIFICATION SIGN OFFS
[12 empty] | INTERNAL VERIFICATION AUTHORITY OR RESPONSIBILITY *Project Manager* |  | CRITICAL HOLD POINT AUTHORITY
1 | Earthworks (Confluence upstream of Pump Station) | Stripped Surface |  | Visual Inspection | At the completion of surface stripping prior to further construction |  | W |  | N/A |  |  |  |  | Not Required
2 | Earthworks (Confluence upstream of Pump Station) | Install Bunds |  | Visual Inspection | At the completion of bund construction |  | W |  | As per approved EMP |  |  |  |  | Not Required
3 | Earthworks (Confluence upstream of Pump Station) | Install Silt Control |  | Visual Inspection | At the completion of silt control install |  | W |  | As per approved EMP |  |  |  |  | Not Required
4 | Downstream Stilling Station | Stripped Surface |  | Visual Inspection | At the completion of surface stripping prior to further construction |  | W |  | N/A |  |  |  |  | Not Required
5 | Downstream Stilling Station | Supply and place Geotextile and Reno Mattress |  | Visual Inspection | At the completion of placement of Geotextile and Reno Mattress |  | W |  | As per approved EMP |  |  |  |  | Not Required
6 | Pump Station | Stripped Surface |  | Visual Inspection | At the completion of surface stripping prior to further construction |  | W |  | N/A |  |  |  |  | Not Required
7 | Pump Station | Hardfill against Walls |  | 95% compaction required | Each layer, Max layer thickness 200mm |  | H |  | Test Certificates required |  |  |  |  | Not Required
8 | Pump Station | Outlet and Discharge |  | As per IFC drawings or Engineers instruction | Prior to construction |  | H |  | Check against IFC drawings specification |  |  |  |  | Not Required
9 | Pile driving | Delivery inspection of piles |  | 10M 300 SED H5 | Prior to pile driving |  | H |  | Check pile tags |  |  |  |  | Not Required
10 | Pile driving | Driving of timber piles |  | As per IFC drawings | Prior to backfill |  | H |  | Piles driven to 10M depth top of pile RL -2800 |  |  |  |  | Not Required
11 | Pile driving | Piling card |  | As per IFC drawings | Prior to Backfill |  | H |  | Subcontractor QA |  |  |  |  | Not Required
12 | Excavation | Excavate to RL - 1.2 |  | Surveyed as built | Upon completion of Excavation |  | H |  | Survey data |  |  |  |  | Not Required
13 | Installation of retaining wall plates | Install plates |  | 22mm Steel plates | During construction |  | H |  | Visual Inspection |  |  |  |  | Not Required
14 | Excavation | Excavate to RL - 2.8 |  | Surveyed as built | Upon completion of Excavation |  | H |  | Survey data |  |  |  |  | Not Required
INSPECTION & TEST PLAN
INSPECTION & TEST PLAN (ITP)
The ITP defines the required inspections during various stages of fabrication, construction and installation work. It is also a method of communicating these requirements to those doing the work and a verifying record that they have been carried out.
The ITP defines 2 different levels of inspection according to the following criteria:  Internal Verification: This inspection or verification activity is required internally by United Civil. A Designated Internal Authority- Project Manager, Supervisor, Foreman or other authorised person is determined for the given inspection point or verification activity. Where a signature required verification is notified by signing the designated check sheet.  Critical Hold Points: These are ONLY inspections required by the contract. It requires the Foreman/ Supervisor or Subcontractors Representative to notify the United Civil Project Manager that the hold point stage of inspection has been reached. Fabrication shall not proceed past this point unless the inspection has been carried out or approval to proceed is given in writing & signed by the Engineer’s Representative. The Engineer’s Representative shall sign the Check sheet. A Contract Hold Point is a contractual requirement. Where the Engineer’s Rep has not signed or for whatever reason cannot sign the Hold Point off the Project Manager must signify verification by the Engineer by other means such email sign off or other formal correspondence and note as such on the ITP.