## Network Drainage
|  |  |  | Inspection Test Plan |  |  | Approver / Signatures |  | Project Site reps.
|  |  |  | Contract Name: | G1202A - Waikaretaheke Riverbend Recovery |  | CPS Approver | Quality Approver | CPS Eng.
|  |  |  | Procedure: | Network Drainage |  | Name / Signature | Name / Signature | Site Engineer
Inspection & Test Plan / Checklist | [6 empty] | Robert Loomes |  | Quality Eng.
Lot No: G1202A |  |  |  | Corresponding Work Instruction: |  | G1202A - Waikare Riverbend Recovery RP7 - TREC Quick Wins.docx |  | Compliance with Work Instructions and Specifications
Detailed Location: SH38 at RS 161 RP 7.171
Chainage:
No: | Inspection / Test Point | ACTION (Hold, Monitor, Witness) | Detail | Frequency | Inspection / Test Method submission, visual inspection, testing, measure, review | Conformance Criteria | Records | Initials | CPS Engineer Initials (Grey if not required) | Date(s)
1 | Survey Setout | W | Setout inlet & outlet points with inverts as required by Contractor to construct to design | Prior to commencement | Survey |  | Survey receipt | Site Engineer
2 | Locate existing services by hand digging/hydro excavation | W | Ensure all services conflicting with the line of trench has been exposed by hand digging/ hydro excavation | Prior to commencement | Potholing | All conflicts have been located. New services and/or conflicts to be advised to Project Engineer. As-built all services | As-built Drawings Doc. Review | Site Engineer
3 | Trenching and Excavation | W | Inspect trench profile and ensure it is correct to minimum drainage standards | Daily | Visual/Inspection | Line and level is correct | CS-4025 Drainage Line Record Check Sheet (or equivalent) | Site Engineer
4 | Trenching and Excavation | W | Ensure trench width is sufficient to provide enough space on either side of the pipe | Daily | Visual/Inspection | D/6 or 150mm whichever is greater on either side of the pipe | CS-4025 Drainage Line Record Check Sheet (or equivalent) | Site Engineer
5 | Foundation Compliance | H | Test formation level on completion of excavation to check if undercut required | One test per 20 linear metres | Scala Penetrometer | If CBR is less than 50kPa , advise Engineer | Lab Test Report | Site Engineer | CPS Engineer
6 | Pipe Bedding Material Compliance | W | Material to meet specifications dependant on material type selected | Each material used | Document Review | Reject chip 10-20mm | Supplier Documentation / Lab Test Report | Site Engineer
7 | Bedding | W | Bedding - Ensure correct thickness of bedding is placed and compacted | Daily | Visual/Inspection | 100 mm thick bedding for all mm dia pipe | CS-4025 Drainage Line Record Check Sheet (or equivalent) | Site Engineer
8 | Pipes and Precast Units | W | Confirm pipes diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition. | Each delivery to site | Certification | Pipe - Diameter & Class, Wingwalls, Manholes, Cesspits etc. | Delivery Dockets | Site Engineer
9 | Pipe Laying | W | Pipe Laying -Variation between design invert level to as-laid invert level must be less than 5mm. Variation of grade of one pipe to the next shall be less than 3mm | Daily | Visual/Inspection | Invert level <= 5mm and grade <= 3mm from design levels | CS-4025 Drainage Line Record Check Sheet (or equivalent) | Site Engineer
10 | Pipe Laying | W | Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness | Prior to backfilling | Visual/Inspection | No defects/ gaps / pipes are aligned correctly | Photos | Site Engineer
11 | Pipe Laying | W | As-built survey of pipes installed | Once line is completed between 2 structures | Survey | Invert level <= 5mm and grade <= 3mm from design levels | Survey Receipt | Site Engineer
12 | CPS Engineer Pre backfill Inspection | H | Inspection of pipes prior to backfilling to ensure they have been installed correctly and that the joints are sealed. Check for any gaps. | Daily | Visual Inspection | Compliance with the Specification | CS-4025 Drainage Line Record Check Sheet (or equivalent) | Site Engineer | CPS Engineer
13 | CPS Engineer Pre backfill Inspection | W | The pipes shall be laid with the variation between the specified invert level and invert level laid shall not exceed 5mm | Prior to backfilling | Survey | Vertical tolerance +/- 5mm | CS-4025 Drainage Line Record Check Sheet (or equivalent) | Site Engineer
14 | CPS Engineer Pre backfill Inspection | W | Pipe invert checks shall be carried out at least once per day with a maximum of 20m between checks. | Prior to backfilling | Survey | Vertical tolerance +/- 5mm | CS-4025 Drainage Line Record Check Sheet (or equivalent) | Site Engineer
15 | Pipe Backfill Compliance | H | Material to meet specifications dependant on material type selected | Each material used | Document Review | Compliance with requirements from Specifications | CS-4025 Drainage Line Record Check Sheet (or equivalent) | Site Engineer
16 | Pipe Backfill Compliance | H | Backfill Construction Material | 1 test per 50m, or per 500m3 of source. | Lab Testing - OMC Standard Compaction Curve; Grading Curve (wet or dry sieve) | CLEAN GRADED GRANULAR AGGREGATE AND HAVE BROKEN FACES AP65 | Lab Test Report | Site Engineer
17 | Backfilling | W | Backfill 150mm lifts with (material) and test every 300mm lift to underside of Subgrade alternatively, to 300mm above crown of pipe in berms. Remainder of backfill to be done with excavated material. | 1 test per 20 m length of trench per 300mm lift | Testing | 97% (under carriageway) or 95% (under berm) of MDD or Clegg equivalent | Lab test results | Site Engineer
18 | Structure installation (Manhole, Catchpit, Wingwall) | H | Structures to be installed to the design survey location and level | During structure construction | Visual/Inspection | As Built Survey | ACE-CS-4006 Manhole Catchpit Board Check Sheet and Survey receipt (or equivalent) | Site Engineer | CPS Engineer
19 | Structure installation (Manhole, Catchpit, Wingwall) | W | All joints are to be sealed including rungs and lids | During structure construction | Visual/Inspection | Pipe joint to structure shall be encased in 200mm (min.) thick 20MPa concrete | CS-4006 Manhole Catchpit Board Check Sheet (or equivalent) | Site Engineer
20 | Structure installation (Manhole, Catchpit, Wingwall) | W | Arrange as-built survey of the structure and all invert levels | Once installed | Survey | As Built Survey | Survey Receipt | Site Engineer
21 | Survey As Built | H | Ensure all drainage lines comply with design prior to carrying on with next construction process | At completion of drainage line | Measurement |  | Survey receipt | Site Engineer
22 | Lot Number QA File | W | Ensure all NCRs are closed and included within QA file, Delivery Dockets and Lab Testing Spreadsheet and Test Reports to be included in QA File | At completion of Lot | Document Review | 65 | Delivery Dockets, Test Reports, Lab Testing Register | Site Engineer
23 | As-builts | H | Red pen mark up drawings to be included in QA file | At the completion of the Lot of work | Drawings |  | As-built Drawing | Site Engineer
24 | Quality Assurance deliverables | W | Red line mark up drawings to be reviewed and accepted. All NCRs and RFIs are closed and included with Handover QA file. Red line mark up drawings to be included in QA file | At completion of Lot | Document Review | Ensure all QA is uploaded into ConQA / Procore | As-builts, NCR's and RFI's | Site Engineer
25 | Completion Sign Off From Fields Below | [5 empty] | Signatures | PM | CPS | QM
Comments:
IFC Drawings used for Construction incl. Rev numbers:
Reference Documentation (Notices/NCRs etc.):
QA Compiled By : |  |  |  |  | Signature: |  |  | Date:
QA checked By Construction Manager: |  |  |  |  | Signature: |  |  | Date:
QA checked By Quality Manager: |  |  |  |  | Signature: |  |  | Date:
Accepted By CPS Manager: |  |  |  |  | Signature: |  |  | Date:
Note on F14: Insert Frequency here
Note on H15: List Tests required from Spec & PRs here with criteria for a passing test - use multiple rows if required
Note on F25: Insert Frequency here
Note on H25: List Tests required from Spec & PRs here with criteria for a passing test - use multiple rows if required