## Foundation
INSPECTION & TEST PLAN
|  | Contract Name: | [6 empty] | Rev: | Originator | Date | Approved | Date
|  | Tauhara Field facilities |  |  | Hold Point (H) | Verify (V) |  |  | 0 | Sid Rudani | 2021-11-17
TAB006C ITP No: 002 Foundations |  |  |  |  | Submit (S) | Review (R)
Approve(A)
TASK | SPECIFICATION REFERENCE | TEST REQUIRED | INSPECTION BY | TASK TIMING OR TASK FREQUENCY | ACCEPTANCE CRITERIA | UCCL Signature | Client Signature | UCCL | Client | DATE | COMMENTS
Preliminary
Concrete Mix Design Approved | TABG-JEC-0-000-STR-SPC-7500-B Structural Specification | Jacbos | Engineer | Formal request/RFI | Approved by Engineer |  |  | H | R/A
Concrete Mix Design Trails | TABG-JEC-0-000-STR-SPC-7500-B Structural Specification | Temperture, slump and strength | Engineer | Per Mix Design | Approved by Engineer |  |  | H
Concrete | TABG-JEC-0-000-STR-SPC-7500-B Structural Specification | Compressive Strength | Supplier | 1 Set of 3 tests for every 50m³ testing at the plant and 100m³ on site. Slump test on first 2 trucks from each plant. Then visual slump test for the pours over 20m³ and intermitted/random testing every 100m³. | Slump Test, Air Content Test, Compressive strength test results, shrinkage strain Accreditation/ Registration certificate from Laboratory |  |  | H | R
|  | Slump Test | Supplier | As Per above | As per Above |  |  | H
|  | Air Content Test | Supplier | As Per above | As per Above |  |  | H
|  | Shrinkage strain at 56 days | Supplier | As Per above | As per Above |  |  | H
Shop Drawings | TABG-JEC-0-000-STR-SPC-7500-B Structural Specification - 12.1.4 | Approved shop drawings prior to fabrication | Engineer | 10 Days before commencing fabrication | Approved by Engineer |  |  | H |  |  | Applicable to embedded items. Structural Steel ITP will cover material conformance
Supply of Reinforcement - Steel reinforcement compliance records | TABG-JEC-0-000-STR-SPC-7500-B Structural Specification - STEEL REINFORCEMENT COMPLIANCE 6.1.7 | Schedules shall be prepared by the supplier and reviewed/ accepted by CEL prior to fabrication. | Engineer | Prior to manufacturing any reinforcement | Manufacturer´s Mill Certificate/Rebar schedule/Rebar summary sheet |  |  | H | R
Pre-construction site works
Ground Condition/Subgrade | TABG-JEC-0-ULG-STR-DET-3104(1) Note 4 | Geotechnical testing | Contact | Before placement of any site concrete, Scala penetrometer testing, proof roll. | SITE TO BE INSPECTED BY AN EXPERIENCED GEOTECHNICAL ENGINEER AND CONFIRM SUITABILITY FOR MINIMUM 100 kPa ULTIMATE BEARING CAPACITY. |  |  | H | R
Trim Sub grade | As per IFC Drawings and approved CAD files | Survery plan | UCCL/Engineer | Before placement of any site concrete check sub grade profile | Finished height for sub grade + 10/-50mm. Minimum thickness to be 50mm as per IFC Drawing. Target RL as per IFC Drawings. |  |  | H | S
Site Concrete/binding | As per IFC Drawings and approved CAD files | Visual Inspection | UCCL/Engineer | Thickness, minimum 50mm, consider 75mm depending on subgrade. | Finished height for site concrete to be within +/- 10mm.Thickness, minimum 50mm, consider 75mm depending on subgrade. |  |  | H | S
Foundation
Setout | As per IFC Drawings and approved CAD files | Surveying as built/Visual Check | UCCL/Engineer | For set out of each Foundation. After placement of Formwork. Top of Foundations to be sloped 1:200 to avoid ponding | Finished height of embebded items +/- 10mm vertically and +/-20mm laterally |  |  | H | S
Pre-pour Insepction | Design / IFC Drawings | Visual Inspection | Engineer | Pre pour inspection for each Pour or Foundation | Pre pour inspection check sheet |  |  | H | W
Embeded Items | TABG-JEC-0-000-STR-SPC-7500-B Structural Specification | QA Documents and PS4, visual inspection | Engineer | For each Foundation Embeded items | As per specifications. Confirmation from Engineer. Deviation of Centerlins of the plate relative to the specified positions of the cenre-lines to be +/- 10mm vertically and Laterally |  |  | H | R
Backfill | Design / IFC Drawings | Visual Inspection | Enginner |  | Backfilling with site won material with small plate compactor in confined space and static roll with 4T Roller where applicable with max. of 300mm lift |  |  | W | R
Post Construction
As Built & Final Design Documentation |  | Surveying | UCCL | For each Pour | Confirmation From Engineer on as built records & redline mark ups |  |  | H | R
Completion Inspection inc. Construction Defects Report |  | Completion inspection on the structure by CEL | CEL/ UCCL | For each structure | Provided a completed construction defect report that that details any remedial measure taken, snag lists closed out |  |  | H
Note on B25: Siddharth Rudani: To be Referenced

## Piling
INSPECTION & TEST PLAN
|  | Contract Name: | [6 empty] | Rev: | Originator | Date | Approved | Date
|  | Tauhara Field facilities |  |  | Hold Point (H) | Verify (V) |  |  | 0 | Sid Rudani | 2021-11-17
TAB006C ITP No: 002 Foundations |  |  |  |  | Submit (S) | Review (R)
Approve(A)
TASK | SPECIFICATION REFERENCE | TEST REQUIRED | INSPECTION BY | TASK TIMING OR TASK FREQUENCY | ACCEPTANCE CRITERIA |  | CLL | UCCL | Client | DATE | COMMENTS
Preliminary
Acceptable Method Statement |  |  |  | Once Prior to commencement of piling | Approved Method statement document
Concrete Design Mix Verification | TABG-JEC-0-000-STR-SPC-0004(B) Bored Pile Specification |  |  | Once Prior to commencement of piling | Approved by Engineer
Supply of Reinforcement - Steel reinforcement compliance records | TABG-JEC-0-000-STR-SPC-0004(B) Bored Pile Specification | Schedules shall be prepared by the supplier and reviewed | Engineer | Prior to manufacturing any reinforcement | Manufacturer´s Mill Certificate/Rebar schedule/Rebar summary sheet |  |  | H | R
Pile Boring
Pile Location | Jacobs Technical requirements: For Bored Piles | Survey record | Surveyor | Every Pile | Hz +/-75mm Vt +/- 25mm |  | H
Drill Tool Diameter | Visual | QAC Pile Card | CLL | Start of project | Design |  | H
Verticality | Jacobs Technical requirements: For Bored Piles | QAC Pile Card | CLL | As per QAC requirements | Vertical alignment <1:75 from design |  | R
Casing Inspection |  | QAC Pile Card | CLL | Start of project | Visual |  | H
Bore size | Jacobs Technical requirements: For Bored Piles | QAC Pile Card | CLL |  | ≥ specified diameter |  | H
Pre pour Inspection Check
Required depth reached | Jacobs Technical requirements: For Bored Piles | Visual Inspection | CLL/UCCL | Every Pile | Weighted tape |  | H | H | W
Clean with no unsuitable material | Jacobs Technical requirements: For Bored Piles | QA Documents and PS4, visual inspection | CLL/UCCL/CEL | Every Pile | Weighted tape |  | H | W | H
Reinforcement Cage inspection | Jacobs Structural Specification | Visual/ Delivery Docket | CLL/UCCL | Every pile | Documentation matches Design |  | H | R | W
| Jacobs Technical requirements: For Bored Piles Jacobs Structural Specification |  |  | Every Pile | Complies with IFC Drawings for Alignment, Height and Type |  | H | R | R
Concrete Placement
Verify Concrete Mix | Jacobs Structural Specification | Concrete Ticket | CLL | Each delivery | Approved Mix Design |  | H | W | W
Concrete level | Jacobs Structural Specification | QAC Pile Card | CLL | Every Pile, United Civil at commencement of project on the first pile/piles | Design +50mm |  | H | W | W
Concrete pouring | Jacobs Technical requirements: For Bored Piles Jacobs Structural Specification | QAC Pile Card | CLL | Every Pile, United Civil at commencement of project on the first pile/piles | Tremie as required |  |  | R | R
Compressive Strength Sampling | OTR | Lab.Test Record | IANZ Accredited Lab | As per NZS 3104 | 28 day - 30MPa |  | R | R | R
| NZS 3104 Jacobs Structural Specification | Lab. Test Record | IANZ Accredited Lab | Daily on-site testing for each concrete pour for each 50 m3 or pt. thereof | 28 Day - 30MPa |  | H | R | R
Slump/spread test | Jacobs Structural Specification NZS 3109 | QAC Pile Card | IANZ Accredited Lab | At same time as on-site compressive test sampling | TBC |  | H | R | R
Post-Construction Testing
Pile Dynamic Analysis
Pile Integrity Testing
Post Construction
As Built & Final Design Documentation |  | Surveying | UCCL | For each Pour | Confirmation From Engineer on as built records & redline mark ups |  |  | H | R
Completion Inspection inc. Construction Defects Report |  | Completion inspection on the structure by CEL | CEL/ UCCL | For each structure | Provided a completed construction defect report that that details any remedial measure taken, snag lists closed out |  |  | H
Note on B23: Siddharth Rudani: To be Referenced