## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | ITP - Precast Installation | itp |  |  |  | Yes | ITP - Precast Installation | 260c9038-5e6f-409d-8a5a-cab4d4809131
checkpoint-group |  |  | section | Precast Installation
checkpoint-status |  |  | checkpoint | Preplanning
label | 2e281406-7891-598c-9155-6c0694c046d9 |  | note | Specification Reference: UC Temp works procedure
label | fbfe6d95-e1f4-5e96-b6b3-f8031cf24b0d |  | note | Test Required: Construction sequence, Precast propping temporary works design, Lifting inserts required, Site Access Plan, Storage Plan, Lift Plan.
label | 7471ff79-c158-52e9-8a57-9eef7e0d60a5 |  | note | Inspection By: UCCL
label | 4b820a49-2e57-5b70-9d2d-3493cd944525 |  | note | Task Timing or Task Frequency: Prior to installation
label | 26604571-67de-567a-842f-73ae41174325 |  | note | Acceptance Criteria: Certified TW's design, Method statement
checkpoint-status |  |  | checkpoint | Survey setout
label | dbc6ab67-7b56-5271-afdb-77e378cb304c |  | note | Specification Reference: IFC drawings, Shop drawings
label | 2a88bd8c-4769-5ea3-a65e-ba79302cd917 |  | note | Test Required: Setout pins to determine line and level of precast elements
label | 8c0a44e4-9e70-5c91-81f8-a5075656b186 |  | note | Inspection By: UCCL
label | a32ef768-4653-55a0-878d-f500e770420e |  | note | Task Timing or Task Frequency: Prior to installation
label | 93b7f4e5-1aac-5478-97ba-857dd5b734d6 |  | note | Acceptance Criteria: Survey Data / Report
checkpoint-status |  |  | checkpoint | Verticality and positional alignment
label | e4d6887e-91e7-5240-b269-e4282007c760 |  | note | Specification Reference: Locate precast items to the following tolerances:
label | c8685268-867d-5157-8437-b08f7a62be90 |  | note | Plan: ± 10mm
label | f4a0a3b3-4609-5376-93ee-fa7993b2863f |  | note | Vertical: ± 1mm/metre
label | 6be7c293-defb-55e6-8872-962a010c19e3 |  | note | Panel Joint width: ± 1mm/metre; but no panel joint shall be less than 10mm, or more than 20mm (unless indicated otherwise on drawings)
label | 7a0c70fc-0d6c-5caa-8a11-978007357e50 |  | note | Above tolerance can be increased but should not be more than the values mentioned in NZS3109.
label | 67957dc9-7f49-53b1-8961-c2d40b6b4565 |  | note | Test Required: Check verticality of the precast elements are within spec tolerance
label | 6fa1ba57-6b92-5cb3-bc6e-c25336587eda |  | note | Inspection By: UCCL
label | b7c8e706-3d3b-5feb-854d-41cd1652080b |  | note | Task Timing or Task Frequency: During installation
label | d51903ae-9acd-5c48-8356-86076c5a9086 |  | note | Acceptance Criteria: Signoff the ITP
checkpoint-status |  |  | checkpoint | Propping precast units
label | 2bbdfe9a-c616-59bb-b34a-c8069b535a63 |  | note | Specification Reference: Certified TW's design, Precast to be installed per Approved Code of Practice for the Safe Handling, Transportation and Erection of Pre-Cast Concrete
label | 75197492-f9b4-5cbb-8164-b61995b43e7f |  | note | Test Required: Check props have been installed per temporary works design.
label | fc8b50f2-6ad7-5196-b848-d87b944492ed |  | note | Inspection By: UCCL
label | 8ab3e331-41a0-5453-a776-274257de473f |  | note | Task Timing or Task Frequency: Before releasing crane
label | d3eaa08d-7ebb-5bf3-a4b9-e32806db842f |  | note | Acceptance Criteria: Permit to load
checkpoint-status |  |  | checkpoint | Grouting / waterproofing / joint sealing /
label | 5e21600b-becf-5b35-b780-243cf19b8474 |  | note | Specification Reference: IFC drawings
label | aa3b71ec-d5fd-584f-986a-63f9189582b3 |  | note | Test Required: Drossbach ducts to be filled with concrete of the element they are to be incorporated within.
label | 8834a84f-1e0d-5c49-9c4f-ed88a587124f |  | note | Inspection By: UCCL
label | a31e5526-0395-5acd-a684-1d26219249a6 |  | note | Task Timing or Task Frequency: During installation
label | 4a6dcb19-6f7f-5bcc-b6da-53eb67b2b7b1 |  | note | Acceptance Criteria: Signoff the ITP
checkpoint-group |  |  | section | Post-Construction
checkpoint-status |  |  | checkpoint | As Built Survey
label | d225d7ca-3785-56d8-b5b8-bcabefde3a0c |  | note | Specification Reference: Compliance to IFC Drawings / Shop Drawings.
label | 720251dd-6ae8-5358-89e5-ee15af8c2d45 |  | note | Test Required: Survey As-Built Drawings
label | 6331cb25-75cc-5655-9f2f-ce916141e9d7 |  | note | Inspection By: UCCL
label | 83c2b8a2-91c2-5f0d-9d38-76d773d3da19 |  | note | Task Timing or Task Frequency: Completion
label | e49cc528-3b4a-5013-a810-2f101b48d9af |  | note | Acceptance Criteria: As built drawing/ report
checkpoint-status |  |  | checkpoint | Completion Inspection
label | 36548b15-c7ce-531a-924f-9f12cab2a1a8 |  | note | Specification Reference: The construction defects completed (excluding only Snagging Defects have been rectified).
label | b573e4be-65e7-5e0a-b027-8c4a69927210 |  | note | Test Required: Completion inspection on the structure by Constructors and Designers
label | 703346d0-5c86-5ce6-b90a-ffb2d4b6a8ff |  | note | Inspection By: UCCL
label | 06cabfae-6716-5a98-98f4-13de2311b7a0 |  | note | Task Timing or Task Frequency: At the completion of the construction of each element
label | 14553abe-f717-5e37-bb7e-138b485b8b94 |  | note | Acceptance Criteria: Project requirements and relevant specification / Records.
checklist-sectioned |  |  | checklist | ITP 001 Separation Slab Foundation |  |  |  |  | Yes | ITP 001 Separation Slab Foundation | 2a10233f-7009-44bc-9040-3f503a489fb1
checkpoint-group |  |  | section | Preliminary
checkpoint-status |  |  | checkpoint | Concrete Mix Design Approved
label | 78b6a694-f0f9-5c61-a462-22ecbbeadf57 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | c5994bca-3ecf-596e-8666-cbf6350363af |  | note | Test Required: Jacbos
label | 37cbf796-e379-5726-a365-9d43f7f4da4f |  | note | Inspection By:: Engineer
label | 873a6c45-36c7-5611-9948-6f9964e55da7 |  | note | Task Timing or Task Frequency: Formal request/RFI
label | e681dcad-d809-53a1-8734-3c18e491ba3b |  | note | Acceptance Criteria: Approved by Engineer
label | de5de122-4341-58f0-a961-21768daa287e |  | note | UCCL - H
label | 9fe26852-52ca-5da3-9eab-126d471480ba |  | note | Client - R
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Mix Design Trails
label | 86d44c81-826f-5f8c-8ab5-091f4cf25d59 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | c0ba497a-ff6a-5528-a539-ede13c0e176d |  | note | Test Required: Temperature, slump and strength
label | 1cfae95b-6b12-5a9f-9a6e-0a296324f845 |  | note | Inspection By:: Engineer
label | 67608a1c-4468-5a70-b71e-37cf0ee909f9 |  | note | Task Timing or Task Frequency: Per Mix Design
label | 1fe7ba87-172e-5545-ac2d-965fabb4b5e1 |  | note | Acceptance Criteria: Approved by Engineer
label | 92fa755f-b5f9-5a67-a1d6-42b5d574eead |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Tests Pour-1
label | 4c6abcdc-fb7f-5da4-9826-4d8e34673531 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | b87a9303-d4a3-57fb-85ab-fd01d223ec27 |  | note | Test Required: Compressive strength, Slump Test, Air Content Test, Shrinkage Strain at 56 Days
label | 410cc060-bc38-5ddc-9cef-8b9a48fa1e9e |  | note | Inspection By:: Supplier
label | 1675c8aa-d6be-5199-8c71-1b4b022d7c3a |  | note | Task Timing or Task Frequency: 1 Set of 3 tests for every 50m³ testing at the plant and 100m³ on site. Slump test on first 2 trucks from each plant. Then visual slump test for the pours over 20m³ and intermitted/random testing every 100m³.
label | 2979be29-9b67-590b-be89-aa9ad04db269 |  | note | Acceptance Criteria: Slump Test, Air Content Test, Compressive strength test results, shrinkage strain. Accreditation/ Registration certificate from Laboratory
label | 0abb3e41-5aad-5fee-b305-fa9178361f1e |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Tests Pour-2
label | f7893774-70c4-5b9d-bca1-432bc5211fb4 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 42f796cf-9732-5ddc-b7cf-c9113687c0ab |  | note | Test Required: Compressive strength, Slump Test, Air Content Test, Shrinkage Strain at 56 Days
label | 1660384e-d022-5377-81dc-0de9dae0b32b |  | note | Inspection By:: Supplier
label | 53290b1d-be1d-5e3f-b796-5d96b5b4118e |  | note | Task Timing or Task Frequency: As Per above
label | 4ac51f17-a022-59d4-88ff-b8202cbee2cb |  | note | Acceptance Criteria: As per Above
label | 0215f0d4-35af-56ed-8df1-b544bc24d830 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Tests Pour-3
label | e48b65c8-bd64-5b61-a877-da679e088878 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | d1dc51dc-1f57-5b5c-8d28-6a5584885edc |  | note | Test Required: Compressive strength, Slump Test, Air Content Test, Shrinkage Strain at 56 Days
label | c13f5e3b-25a5-57d4-8250-6d78138ce26d |  | note | Inspection By:: Supplier
label | d7e39824-9474-5cee-ab0e-dacdf0660292 |  | note | Task Timing or Task Frequency: As Per above
label | fcfcd74e-0d21-5c9d-87ab-adc33f6ffab7 |  | note | Acceptance Criteria: As per Above
label | f87c45e6-f53c-50eb-baa7-ef3bcdecca1b |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Tests Pour-4
label | c995c995-3fbe-5881-afc7-f2fbe394e5f2 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | d3a42b20-3178-5aad-bb5f-03340bae026e |  | note | Test Required: Compressive strength, Slump Test, Air Content Test, Shrinkage Strain at 56 Days
label | edff078c-1374-5ed4-b391-b732cbb24864 |  | note | Inspection By:: Supplier
label | 185c6af0-c0a6-5111-913d-366344045c0f |  | note | Task Timing or Task Frequency: As Per above
label | 01ee1d0e-9faa-56dd-918a-a3734f5ef58e |  | note | Acceptance Criteria: As per Above
label | bcb7d9e3-2485-58d4-a252-18432b614e42 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Tests Pour-5
label | 365d165a-3d19-53bd-8c6d-77486e4a7525 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 3d10a608-0571-5830-846a-ea4d41229d30 |  | note | Test Required: Compressive strength, Slump Test, Air Content Test, Shrinkage Strain at 56 Days
label | ef6fa1ba-1243-546d-aedf-bd86eecaf82d |  | note | Inspection By:: Supplier
label | 30d4998d-5ce2-5e75-aa17-9f3c8387a283 |  | note | Task Timing or Task Frequency: 1 Set of 3 tests for every 50m³ testing at the plant and 100m³ on site. Slump test on first 2 trucks from each plant. Then visual slump test for the pours over 20m³ and intermitted/random testing every 100m³.
label | 238f46e8-7f02-5d08-b554-6d8dcaa414de |  | note | Acceptance Criteria: Slump Test, Air Content Test, Compressive strength test results, shrinkage strain. Accreditation/ Registration certificate from Laboratory
label | 1ceed24b-05fc-5854-9dd7-ef6c2a20351b |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Tests Pour-6
label | 3683e736-adf9-5463-82ef-c1b429279f82 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 9fcaa5ff-b701-5932-a542-90eb67a2bb20 |  | note | Test Required: Compressive strength, Slump Test, Air Content Test, Shrinkage Strain at 56 Days
label | ea6fd300-dd73-5aea-935e-0be57f93081f |  | note | Inspection By:: Supplier
label | 7555300b-b6d9-5e7a-8e06-61f167724aa7 |  | note | Task Timing or Task Frequency: As Per above
label | 745aa629-85fc-5e8c-9a53-d7b84e8cdd49 |  | note | Acceptance Criteria: As per Above
label | 28e9a525-cf38-5b97-8e0a-5ff63582da0f |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Tests Pour-7
label | 15ef15bc-5e25-5c79-bb03-99b36077f656 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | afd8de75-f80f-546c-b0e8-521ec5ab9163 |  | note | Test Required: Compressive strength, Slump Test, Air Content Test, Shrinkage Strain at 56 Days
label | 2ec83ef5-b54b-5fce-acf2-b4291ceb2e01 |  | note | Inspection By:: Supplier
label | 645061ff-c634-5bfd-9fa8-790894675db8 |  | note | Task Timing or Task Frequency: As Per above
label | 4f417ece-9fa7-562e-a804-3a2cbf2c2584 |  | note | Acceptance Criteria: As per Above
label | 6980ec2f-7ad1-5152-a237-7d1f7512cfee |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Tests Pour-8
label | f9627d47-78f4-5557-ad72-a28e130cdb56 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 004481c3-8b0c-53f0-9490-d816cf8f1010 |  | note | Test Required: Compressive strength, Slump Test, Air Content Test, Shrinkage Strain at 56 Days
label | 1368d103-e3a2-50ae-8e9e-4b3de40fe0d3 |  | note | Inspection By:: Supplier
label | edb0c431-7647-52d9-9e17-4a00137b11c4 |  | note | Task Timing or Task Frequency: As Per above
label | a38b1952-7c51-5158-be19-d18b7124185e |  | note | Acceptance Criteria: As per Above
label | cfc659d2-77b2-58a9-b0d4-65f9f6e9fdf8 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-group |  |  | section | Pre-construction site works
checkpoint-status |  |  | checkpoint | Ground Condition/Subgrade
label | 94b058d1-4841-5578-a9ee-75579c5aba11 |  | note | Specification Reference: TABG-JEC-0-ULJ-STR-AGT-1201-1 Note 4
label | f3f3196a-bd89-5a82-8917-dd55f3d690d3 |  | note | Test Required: Geotechnical testing
label | 6de68e76-53fe-5c4e-9cf1-6cb53dbaa92b |  | note | Inspection By:: Contact
label | 5acd808c-c5d7-52d3-8bc7-4a44d8ddc01f |  | note | Task Timing or Task Frequency: Before placement of any site concrete, Scala penetrometer testing, proof roll.
label | 750b3327-0a89-54f5-adaf-dcbaa6744978 |  | note | Acceptance Criteria: Geotech Report by Client with confirmation that Foundation is suitable (minimum 200 kPa allowable bearing capacity).
label | e249ac11-9723-5102-9f95-163a8d6dbe75 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Trim Sub grade
label | 67a173f7-bf90-5649-866d-3c6aff59cd95 |  | note | Specification Reference: TABG-JEC-0-ULJ-STR-DET-1206
label | 40ef90b9-f27b-519b-8866-5d4680300508 |  | note | Test Required: Survey plan
label | daf47334-398c-5bf7-ac4f-685086e6c21c |  | note | Inspection By:: UCCL/Engineer
label | 48107894-1dc4-5a62-8da7-669fc3701319 |  | note | Task Timing or Task Frequency: Before placement of any site concrete check sub grade profile
label | 652e2a09-fd58-5a10-ac6d-7b76878ae700 |  | note | Acceptance Criteria: Finished height for sub grade + 10/-50mm. Minimum thickness to be 50mm as per IFC Drawing. Target RL 468.950*
label | 001c9c84-3135-5f6c-bfbc-68a8dc8338e0 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Site Concrete/binding
label | 4ded037b-8de4-5547-a90c-dc4f402bc0ee |  | note | Specification Reference: TABG-JEC-0-ULJ-STR-AGT-1201-1
label | 581ce84d-e750-53de-b809-10a2b04fb473 |  | note | Test Required: Visual Inspection
label | 420fd216-fb2d-5aa6-b64f-25c3ae018c1e |  | note | Inspection By:: UCCL/Engineer
label | 1f2a766a-6f33-5eee-95b6-858cbca92921 |  | note | Task Timing or Task Frequency: Thickness, minimum 50mm, consider 75mm depending on subgrade.
label | 3459ccb0-7b5e-5e8e-8d0f-6dbc3a1dc649 |  | note | Acceptance Criteria: Finished height for site concrete to be within +/- 10mm.Thickness, minimum 50mm, consider 75mm depending on subgrade. Target finish RL 469.000
label | 8f1e1a72-fc3f-55fd-9e6d-c13ef9237874 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Setout
label | 664bbc75-b790-505e-a8f3-995861c776f9 |  | note | Specification Reference: TABG-JEC-0-ULJ-STR-AGT-1201-1 Note 3
label | 1739c238-5240-5aeb-9ead-601c2c19c487 |  | note | Test Required: Surveying as built/Visual Check
label | 89356f0d-f43d-542c-947d-e84ffdf63efd |  | note | Inspection By:: UCCL/Engineer
label | 2c3130dd-bfdc-586e-a854-5b61713bd4c6 |  | note | Task Timing or Task Frequency: For set out of each Foundation. After placement of Formwork
label | 67e935ed-8084-5ae7-bb16-52d09771fd99 |  | note | Acceptance Criteria: Finished height of embedded items +/- 10mm vertically and +/-20mm laterally
label | 7be159c9-f64b-5d9a-af97-fdf5c36406c4 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-group |  |  | section | Foundation Set Out
checkpoint-status |  |  | checkpoint | Setout Pour - 1
label | d424ae44-d8d2-5dcf-89f3-36254ee8943a |  | note | Specification Reference: Design / IFC Drawings
label | da2d296c-6726-5ca3-a7cc-d87e00541b60 |  | note | Test Required: Surveying/Visual Check
label | 964799ae-a183-5085-b0a3-56271b91f172 |  | note | Inspection By:: UCCL
label | dd9172fb-290f-5f7e-bedc-ec694ee21a9a |  | note | Task Timing or Task Frequency: For set out of each Pour
label | 40b7e58e-485a-5719-be2a-59c42e4cf300 |  | note | Acceptance Criteria: As per IFC Drawings & site issue Drawing.
label | 1a08f54a-4595-538a-a7c5-3cc5da8e99a2 |  | note | W
checkpoint-status |  |  | checkpoint | Setout Pour - 2
label | 2cc30582-ae19-518d-9099-2496b4664836 |  | note | Specification Reference: Design / IFC Drawings
label | 5f88425b-3878-5d6f-b66f-26a52d5f2583 |  | note | Test Required: Surveying/Visual Check
label | a5762769-8f02-5fdf-8b0a-76775d948de5 |  | note | Inspection By:: UCCL
label | 64a67c40-1714-5d19-94c1-982df54270f6 |  | note | Task Timing or Task Frequency: Pour -1
label | 51c6c5ac-887d-5d23-afbd-b1f6bd2dcadb |  | note | W
checkpoint-status |  |  | checkpoint | Setout Pour - 3
label | b7e7aab3-3b88-558b-b753-ecb0204c96eb |  | note | Specification Reference: Design / IFC Drawings
label | 994b71f2-8b25-53ac-b91a-9f23c06b3e13 |  | note | Test Required: Surveying/Visual Check
label | 974b64ac-e7e7-5457-807c-d29e1406aef5 |  | note | Inspection By:: UCCL
label | a28b41f8-9d0c-5cd2-8585-4ad293ba1a4d |  | note | Task Timing or Task Frequency: Pour -2
label | 5cfdd9c4-722d-5d96-bdf0-df8896710cdb |  | note | W
checkpoint-status |  |  | checkpoint | Setout Pour - 4
label | d2488eb2-2f22-5be8-ba37-808a1c8bb8c3 |  | note | Specification Reference: Design / IFC Drawings
label | 7f047b9d-78f1-5a46-8d58-58eef4d92ad0 |  | note | Test Required: Surveying/Visual Check
label | c37b9089-79a7-50a9-8f57-c239554bb675 |  | note | Inspection By:: UCCL
label | 993664f0-0c37-5371-80ef-722b908e7d04 |  | note | Task Timing or Task Frequency: Pour -3
label | c98dee54-04e7-521f-9840-80cef9c90646 |  | note | W
checkpoint-status |  |  | checkpoint | Setout Pour - 5
label | 5b09da37-7a28-568f-af37-b631c040eee5 |  | note | Specification Reference: Design / IFC Drawings
label | 3555a8f9-a91d-5ca4-a99d-631337ecef65 |  | note | Test Required: Surveying/Visual Check
label | 2db7bbb1-bbf3-568a-a108-789ed67439f5 |  | note | Inspection By:: UCCL
label | 25b143de-b406-5a93-ad41-8de264f1e4f2 |  | note | Task Timing or Task Frequency: Pour -4
label | 4a2aebab-b167-5333-be2d-3e2f8b4462b0 |  | note | W
checkpoint-status |  |  | checkpoint | Setout Pour - 6
label | c3c4b6f2-6297-5653-89bf-bca524ac2090 |  | note | Specification Reference: Design / IFC Drawings
label | 3d132347-35ef-5a53-831a-62234a0cd0c1 |  | note | Test Required: Surveying/Visual Check
label | b1cc94a7-da5d-5d7f-bb24-99d24713c009 |  | note | Inspection By:: UCCL
label | 7cc1128c-c7ac-5902-8ffb-21f76a576ffd |  | note | Task Timing or Task Frequency: Pour -5
label | 45807421-502b-5c39-be19-793c36a85b66 |  | note | W
checkpoint-status |  |  | checkpoint | Setout Pour - 7
label | fdc9e661-a5a3-5559-b5bb-671b8e06c4a3 |  | note | Specification Reference: Design / IFC Drawings
label | e1a81341-25e8-5958-8578-d9f84a43f747 |  | note | Test Required: Surveying/Visual Check
label | 21f7e9f7-bb4f-56fc-bd14-ede8fcd9b1d7 |  | note | Inspection By:: UCCL
label | c0f16d41-f0fb-5039-9fa4-0c78f8d3a7a5 |  | note | Task Timing or Task Frequency: Pour -6
label | 7482c21f-e7a5-593b-b6a0-e46b672f6580 |  | note | W
checkpoint-status |  |  | checkpoint | Setout Pour - 8
label | edca7fd5-4c3e-5c63-a297-63e98a70124b |  | note | Specification Reference: Design / IFC Drawings
label | 8f7164d0-90df-543b-aa93-4063ee036850 |  | note | Test Required: Surveying/Visual Check
label | ed1f48e9-0c2e-5e67-8b69-4c516146d51f |  | note | Inspection By:: UCCL
label | 77f35cbe-887c-5db5-bf52-d84f1d4c6735 |  | note | Task Timing or Task Frequency: Pour -7
label | 339ae7a7-3173-581f-a3a4-6692c77b6523 |  | note | W
checkpoint-status |  |  | checkpoint | Setout Pour - 9
label | 52820a25-c8dc-5905-9bec-804c9113596d |  | note | Specification Reference: Design / IFC Drawings
label | 79ba223e-eaa4-52c8-b20e-94ff42ee95ec |  | note | Test Required: Surveying/Visual Check
label | cb5252d4-04e2-541b-95e0-b550f7157167 |  | note | Inspection By:: UCCL
label | 1eb8b5d0-e6e0-5e71-b3b9-87def1b61e30 |  | note | Task Timing or Task Frequency: Pour -8
label | d01cb704-8b0b-59c8-a6ba-1569de3af6ea |  | note | W
checkpoint-group |  |  | section | Pre-Pour Inspection
checkpoint-status |  |  | checkpoint | Concrete Pour 1
label | fe43e104-9063-543b-a0f5-b22c813d6ac1 |  | note | Test Required: Visual Inspection
label | 3f8b3154-6b47-5f92-9e3a-9b2757c36049 |  | note | Inspection By:: Engineer
label | 24506565-b8bb-52a9-8279-5248ec9580b7 |  | note | Task Timing or Task Frequency: Pour - 1
label | 48e94498-1350-53e1-9ecc-0c12321bce61 |  | note | Acceptance Criteria: Pre pour inspection check sheet
label | 24747535-3578-5acb-868a-7f2b65b1dd0d |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Pour 2
label | 7edf8688-66bf-5ca3-a7d3-635253a41d9b |  | note | Test Required: Visual Inspection
label | 3e1a67db-25b5-5643-8d93-dd6d281ef846 |  | note | Inspection By:: Engineer
label | d46c7eef-f453-54a4-93c1-623a73deb7f4 |  | note | Task Timing or Task Frequency: Pour - 2
label | 47bf5f55-e51f-51b8-90a5-6b205079df9e |  | note | Acceptance Criteria: Pre pour inspection check sheet
label | 162be1e0-1a27-5799-8db1-1272b717b8a7 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Pour 3
label | efe0d96f-90df-507d-83f6-29c9e258fa96 |  | note | Test Required: Visual Inspection
label | d65de09a-645e-512a-afbc-3ad0ddc4e402 |  | note | Inspection By:: Engineer
label | 5d867287-574d-5abc-bfe9-c313c49a806f |  | note | Task Timing or Task Frequency: Pour - 3
label | f8103ddb-f15e-51af-a24c-6b8f7562bb50 |  | note | Acceptance Criteria: Pre pour inspection check sheet
label | e220954c-c0e7-50cc-afaf-77544b874add |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Pour 4
label | b479bc13-ca18-5d0f-b75f-be34b55b9ed3 |  | note | Test Required: Visual Inspection
label | 5e66ddef-06f6-50f4-95ec-da325190954e |  | note | Inspection By:: Engineer
label | 9cc14f0e-1741-58f9-b74c-85a857adb61c |  | note | Task Timing or Task Frequency: Pour - 4
label | 811ece45-4c6d-5ac6-a6d3-bf33fa187f25 |  | note | Acceptance Criteria: Pre pour inspection check sheet
label | 3fb47e79-2a61-519a-a48c-349dd72503a3 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Pour 5
label | 9a31959b-5d5c-5d7b-9294-d8ca98576561 |  | note | Test Required: Visual Inspection
label | f194e1cd-ea99-5d6d-bd30-64d2489c5e99 |  | note | Inspection By:: Engineer
label | 91039ca1-4869-581b-a5f4-089efe799568 |  | note | Task Timing or Task Frequency: Pour - 5
label | 18e468da-85f4-54e3-b5eb-a989f7a53c02 |  | note | Acceptance Criteria: Pre pour inspection check sheet
label | 938509db-981b-5be9-8539-eaeaf708c587 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Pour 6
label | 25c93e3a-24a5-5337-b733-1adb5e8aa6e3 |  | note | Test Required: Visual Inspection
label | bae38c47-6d93-5323-84bc-920ae1654222 |  | note | Inspection By:: Engineer
label | e16c464d-4a63-5444-ae83-1ffa14bbdf9d |  | note | Task Timing or Task Frequency: Pour - 6
label | c85b46d3-2303-51cd-9193-ed226b3cf4c5 |  | note | Acceptance Criteria: Pre pour inspection check sheet
label | ce2ee784-0904-5b64-a938-5ec2ccea0e0e |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Pour 7
label | 59938407-0c12-5c18-8ed3-c83cbef100d7 |  | note | Test Required: Visual Inspection
label | d56c822d-e1a0-5b58-853e-cb6eff54289d |  | note | Inspection By:: Engineer
label | d35ab4ba-351d-565a-b8e2-abcb43a0427f |  | note | Task Timing or Task Frequency: Pour - 7
label | 57353c77-a588-5c8f-9f1f-62befeaf9a6a |  | note | Acceptance Criteria: Pre pour inspection check sheet
label | 20bbb907-1a88-5d10-9614-3de844819218 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Pour 8
label | e127aa04-ebe2-5284-939b-8c121df7ea8f |  | note | Test Required: Visual Inspection
label | db83d85e-1477-538c-bc73-3503b3c2fb97 |  | note | Inspection By:: Engineer
label | 3267a853-e26a-5a90-b7d1-2a75e3f30a85 |  | note | Task Timing or Task Frequency: Pour - 8
label | 6260a122-cdee-58ba-933c-d65800ffa42d |  | note | Acceptance Criteria: Pre pour inspection check sheet
label | e5a54729-d7c3-52ce-9067-166b9d55b262 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Embedded Items for Concrete Pour 1
label | 41b1f3d6-403f-5433-82d5-9ef08ebc76e5 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 29cca701-b7d4-5bab-a311-ef26cb9863bc |  | note | Test Required: Visual Inspection
label | 41a3cc9e-d2be-5bb4-ad14-2c50a7e630ea |  | note | Inspection By:: Engineer
label | 13b82762-29ce-5312-b2aa-d21fd775308b |  | note | Task Timing or Task Frequency: Pour-2
label | 9f031e4a-c398-5323-89ff-2c6c1c867c4b |  | note | Acceptance Criteria: Position in Plan +/-10mm, Level Tolerance +/-20mm
label | b4a1390c-7ee9-5ae0-81ca-cac742af1dc7 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Embedded Items for Concrete Pour 2
label | aeea6615-6812-52aa-9724-f742a169cebf |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 796f3f09-351c-578a-9d12-c7ccb35126e1 |  | note | Test Required: Visual Inspection
label | 480818e5-8ca3-54f6-8523-5cc1d6837c62 |  | note | Inspection By:: Engineer
label | 1a9e390d-0439-5a0d-a0cf-5fb9a37e945d |  | note | Task Timing or Task Frequency: Pour-3
label | e81eb7d6-628d-55d5-928f-a26d2422c22d |  | note | Acceptance Criteria: Position in Plan +/-10mm, Level Tolerance +/-20mm
label | a9dbc01c-39cf-58ee-a20e-1854e41871eb |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Embedded Items for Concrete Pour 3
label | 0527c01c-e01e-5098-ae0b-808972ff9104 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 383e08fc-1f19-5ef1-a4e6-ce39c92698d7 |  | note | Test Required: Visual Inspection
label | 9473eb9e-b309-5f5f-9ad6-2a244adedd0e |  | note | Inspection By:: Engineer
label | 436c5971-1160-5561-a709-d382335ccebd |  | note | Task Timing or Task Frequency: Pour-4
label | a852e557-cbae-5024-9dcb-e5a7bafa2031 |  | note | Acceptance Criteria: Position in Plan +/-10mm, Level Tolerance +/-20mm
label | 6dd402f6-f146-55d1-bcc5-d006d31b84f1 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Embedded Items for Concrete Pour 4
label | 7ec5f954-a8b3-598c-8915-48b6048e6918 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | ae662df7-7e4a-587a-aeea-157528f522d3 |  | note | Test Required: Visual Inspection
label | bf80f9a8-e48e-5345-9ecf-7d0225f5be52 |  | note | Inspection By:: Engineer
label | f6344433-1518-5136-a7e8-3dfd4a238dce |  | note | Task Timing or Task Frequency: Pour-5
label | 6ca98129-1cda-50bc-91c6-a0f1308d559e |  | note | Acceptance Criteria: Position in Plan +/-10mm, Level Tolerance +/-20mm
label | 832c67e6-d3fd-5d1e-865e-be0e1d8587d1 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Embedded Items for Concrete Pour 5
label | 07799cd7-11af-5ba6-93fb-1339cef69b59 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 19a70474-4537-5620-ad0e-28fed106f025 |  | note | Test Required: Visual Inspection
label | 071734f0-dbb1-5c95-a96a-2748daa37e1c |  | note | Inspection By:: Engineer
label | f61a24d6-5ddc-57e5-ae13-9e9555fb6bee |  | note | Task Timing or Task Frequency: Pour-6
label | c3b9c64e-2ce6-54d4-a930-3434675be10f |  | note | Acceptance Criteria: Position in Plan +/-10mm, Level Tolerance +/-20mm
label | 006a0865-f311-5bda-a7ea-0018f263bd3a |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Embedded Items for Concrete Pour 6
label | 046aa09c-9aa0-5cad-b82d-055c94e19042 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 8b15f8f8-8700-5666-b266-282ed2e0e9da |  | note | Test Required: Visual Inspection
label | aad40205-c708-526c-a19b-6f5ea03eb790 |  | note | Inspection By:: Engineer
label | 685d021e-8641-5f58-af1a-4d7e942653cc |  | note | Task Timing or Task Frequency: Pour-7
label | 7b1c025f-4f19-57bf-ab27-c5acce0f74e8 |  | note | Acceptance Criteria: Position in Plan +/-10mm, Level Tolerance +/-20mm
label | 1d126ea4-29b0-5550-a6fe-8f5931757681 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Embedded Items for Concrete Pour 7
label | 5a116400-639e-5d37-9908-e725342d624c |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | acafaf5b-0566-5a86-b3dc-bc42c8f15650 |  | note | Test Required: Visual Inspection
label | f1f0fa1d-1922-5851-be23-c38000ba24ce |  | note | Inspection By:: Engineer
label | 857c2de0-a6b0-572a-a943-27f1e98f8f6c |  | note | Task Timing or Task Frequency: Pour-8
label | 776ba512-034e-5ea1-868e-a199996c5fc0 |  | note | Acceptance Criteria: Position in Plan +/-10mm, Level Tolerance +/-20mm
label | 6882b7ec-1425-51b9-9cc7-00a6490e9151 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-group |  |  | section | Post pour Inspection/Curing
checkpoint-status |  |  | checkpoint | Concrete Pour 1
label | ff7b86be-2828-51f6-9071-4d935ce2471f |  | note | Test Required: Surveying/Visual Check
label | 4989430e-2e80-5746-8964-9d4bb1bd0dad |  | note | Inspection By:: UCCL
label | 9dbe74d3-28d3-5d84-90aa-84523a277cf0 |  | note | Task Timing or Task Frequency: Pour - 1
label | 0617389d-d457-550c-83c1-c7163626de4e |  | note | Acceptance Criteria: Post Pour Inspection Check sheet
label | 88f0cec2-9f91-5c54-909d-69a53f38aa3e |  | note | W
checkpoint-status |  |  | checkpoint | Concrete Pour 2
label | e4dd88be-c625-5f51-abf3-ca0e902c796f |  | note | Test Required: Surveying/Visual Check
label | 5ce1ad6e-86b5-51cd-9720-e91733811414 |  | note | Inspection By:: UCCL
label | 0d72ceb6-82da-5b99-91fb-e076d338928c |  | note | Task Timing or Task Frequency: Pour - 2
label | bf7aa85e-5a47-52d8-bdb2-891d7b87c973 |  | note | Acceptance Criteria: Post Pour Inspection Check sheet
label | 4908e2e4-c722-5aa7-87bd-a998729e17a7 |  | note | W
checkpoint-status |  |  | checkpoint | Concrete Pour 3
label | 1d1ff6d0-4af8-52d9-9cd6-54368d1ba458 |  | note | Test Required: Surveying/Visual Check
label | 84daf302-6544-51e1-a976-4e3779db70c4 |  | note | Inspection By:: UCCL
label | 4e7ee84f-cefd-5286-ac05-032488327fcb |  | note | Task Timing or Task Frequency: Pour - 3
label | 0654d196-2620-5a11-80fe-a55a07d5b4c4 |  | note | Acceptance Criteria: Post Pour Inspection Check sheet
label | a2f88dfb-03ec-588e-b2c8-f0453307cb6a |  | note | W
checkpoint-status |  |  | checkpoint | Concrete Pour 4
label | e5718c20-42d2-5ee5-80e1-67f2fd417952 |  | note | Test Required: Surveying/Visual Check
label | 31108616-503a-542f-a2e6-0171e1f37d63 |  | note | Inspection By:: UCCL
label | f3321038-2c5d-56d7-bd39-3c0b7a522b66 |  | note | Task Timing or Task Frequency: Pour - 4
label | 8fa0e888-8b22-5a8f-89d4-df311928f5ff |  | note | Acceptance Criteria: Post Pour Inspection Check sheet
label | 93a79f66-fbdd-5e04-b014-8aba5746bfba |  | note | W
checkpoint-status |  |  | checkpoint | Concrete Pour 5
label | d08d482c-5279-5898-9396-8024a454515a |  | note | Test Required: Surveying/Visual Check
label | d9662caf-ac15-5708-8a01-72fefeed6f2f |  | note | Inspection By:: UCCL
label | 4d5353e4-450c-5800-8680-aa838c802f78 |  | note | Task Timing or Task Frequency: Pour - 5
label | bfab3336-92c3-51ec-9e5e-d4b02db3b397 |  | note | Acceptance Criteria: Post Pour Inspection Check sheet
label | 2f539e48-cf7a-50e6-be5f-7a1a6ec79734 |  | note | W
checkpoint-status |  |  | checkpoint | Concrete Pour 6
label | bb1e79c4-8177-5106-b0b3-e7f15c8cc407 |  | note | Test Required: Surveying/Visual Check
label | 95068276-4513-52d6-828c-1143e9d7e357 |  | note | Inspection By:: UCCL
label | 14e2e778-892a-591f-8671-df5e95315d84 |  | note | Task Timing or Task Frequency: Pour - 6
label | 99179335-4d73-5025-a440-b87585a133ec |  | note | Acceptance Criteria: Post Pour Inspection Check sheet
label | c3080297-b25a-5a0e-afa5-b47a28157b34 |  | note | W
checkpoint-status |  |  | checkpoint | Concrete Pour 7
label | c6be7478-d66e-528a-94d7-07d3855baffb |  | note | Test Required: Surveying/Visual Check
label | d901d15b-a2c8-5b57-a09a-e908099227c6 |  | note | Inspection By:: UCCL
label | 946fd248-7232-5c72-bad4-550d87d4203d |  | note | Task Timing or Task Frequency: Pour - 7
label | 67a1774d-38ed-5517-8446-af4f7ac58800 |  | note | Acceptance Criteria: Post Pour Inspection Check sheet
label | 66afe579-6479-5db1-86bb-b4f01906ed98 |  | note | W
checkpoint-status |  |  | checkpoint | Concrete Pour 8
label | 81fa3cca-6bda-59d0-9b3b-c840e5bcbf2c |  | note | Test Required: Surveying/Visual Check
label | ce12bdc5-6ce6-57b3-b50e-2c082651a6f2 |  | note | Inspection By:: UCCL
label | 43d0b499-a618-5f3c-a00f-c9156b0b1a86 |  | note | Task Timing or Task Frequency: Pour - 8
label | 459cecea-c407-56f6-8b07-413d228f5b21 |  | note | Acceptance Criteria: Post Pour Inspection Check sheet
label | f5796eb3-2cfd-5bf1-8cda-dbf9a1f780d7 |  | note | W
checkpoint-group |  |  | section | As Built
checkpoint-status |  |  | checkpoint | As Built Pour 1
label | 03a27ea0-c89f-5e24-baca-018aff12481c |  | note | Test Required: Surveying
label | 3d9e63a7-48de-5192-ac34-ba0a69819ea6 |  | note | Inspection By:: UCCL
label | 5a861b6d-e32e-5920-927f-623537736ea4 |  | note | Task Timing or Task Frequency: For each Pour
label | 7ca2cdcf-1f4a-575b-b1f9-982d1420fb0c |  | note | Acceptance Criteria: Confirmation From Engineer on as built records
label | e4939343-9d65-5bae-aaf2-6fa04f8fbd3d |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | As Built Pour 2
label | 74787d10-81ab-59db-9478-e27f0de98ea5 |  | note | Test Required: Surveying
label | ffb4234c-61d9-5c46-b491-f7c6a660bc55 |  | note | Inspection By:: UCCL
label | 21ccef1f-2d74-5da2-b83b-8a31cb886243 |  | note | Task Timing or Task Frequency: For each Pour
label | c7f00624-5d22-509d-a82d-11b2cc0f1d6a |  | note | Acceptance Criteria: Confirmation From Engineer on as built records
label | 99ea097a-9912-5287-b120-7149377dc071 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | As Built Pour 3
label | 717dceac-15a2-5edf-8db6-f8c001a695b3 |  | note | Test Required: Surveying
label | acd7b18f-f773-5dee-91e1-77e50d7b58e1 |  | note | Inspection By:: UCCL
label | 9d93b74a-ce26-5385-9c81-f6f78c698be4 |  | note | Task Timing or Task Frequency: For each Pour
label | 8af86829-f856-5d58-a844-507dc96b7358 |  | note | Acceptance Criteria: Confirmation From Engineer on as built records
label | 8fd2966e-0c3e-599b-99ad-566cf14d3070 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | As Built Pour 4
label | 49addfdd-bc19-5f68-95f7-f69390911ab7 |  | note | Test Required: Surveying
label | febeefe7-3674-5c97-ba3e-0c6be8e3bef8 |  | note | Inspection By:: UCCL
label | 0c1c7ef3-2113-575c-b3a1-da3aaa642551 |  | note | Task Timing or Task Frequency: For each Pour
label | 2bf99750-03e9-513a-9914-1d930fffe7ce |  | note | Acceptance Criteria: Confirmation From Engineer on as built records
label | 182198b3-a4b6-5af5-b633-774670d6c972 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | As Built Pour 5
label | f514f427-940f-5e48-b63b-d76a6f4afeab |  | note | Test Required: Surveying
label | a2d06f41-11eb-58b3-9f7f-f723090956ae |  | note | Inspection By:: UCCL
label | 3646cb92-ea90-5081-93e8-36c76562b72d |  | note | Task Timing or Task Frequency: For each Pour
label | 472b1d11-b22f-5860-816c-13b03b513978 |  | note | Acceptance Criteria: Confirmation From Engineer on as built records
label | bf1c1fda-7ce8-5c55-b87c-02920b059a20 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | As Built Pour 6
label | 1c5a9360-8d02-5d79-8a88-9ad0559def0b |  | note | Test Required: Surveying
label | 94df2d65-c9b1-557e-a0bf-785b09e06350 |  | note | Inspection By:: UCCL
label | edbecfdb-bd37-5696-acbc-1a9ddec9f1f0 |  | note | Task Timing or Task Frequency: For each Pour
label | 6bd4e9f6-41c0-5c0a-ad2b-18ab81e9b52b |  | note | Acceptance Criteria: Confirmation From Engineer on as built records
label | 8135448b-9057-51e5-ba33-66088a4fdc02 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | As Built Pour 7
label | 88600f86-73f0-52bf-b49c-a2da59a2c3c6 |  | note | Test Required: Surveying
label | f6260e29-8f2f-5eec-ba03-737c613dc07a |  | note | Inspection By:: UCCL
label | 78cad8ad-c67c-5bd3-95bb-650f809ef4ac |  | note | Task Timing or Task Frequency: For each Pour
label | fb4b7a58-9d29-57f2-8ccf-3a095f07fbfd |  | note | Acceptance Criteria: Confirmation From Engineer on as built records
label | 40e4baa4-be6c-5896-aaf7-4a54e22b1e4d |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | As Built Pour 8
label | ca556ed5-625f-5971-b705-f115a7d8dc7f |  | note | Test Required: Surveying
label | b7b9449f-baaf-59e7-ae12-0c93ea7ed52c |  | note | Inspection By:: UCCL
label | 96e23374-5281-5836-9e6d-d6984635c5fb |  | note | Task Timing or Task Frequency: For each Pour
label | 723c8965-859a-55e3-bcc4-97eeafe9722e |  | note | Acceptance Criteria: Confirmation From Engineer on as built records
label | c0aafe66-b9f2-5d8f-93b9-ac61598f7828 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checklist-sectioned |  |  | checklist | ITP - Precast Fabrication | itp |  |  |  | Yes | ITP - Precast Fabrication | 514e61de-1d0d-47a0-a4df-060d9b62f11a
checkpoint-group |  |  | section | Pre Construction
checkpoint-status |  |  | checkpoint | IFC Drawing and IFC Project Specifications Review
label | 8492d124-d793-59ba-9422-fb40e8a020fa |  | note | Specification Reference: Confirmation all inspection and test requirements from the IFC drawings and IFC project specifications are captured
label | 4717324b-3e34-547a-af60-bf937c2663ce |  | note | Test Required: General review of the IFC drawing and IFC project specifications
label | 3fb45a17-1781-587f-9f94-b8554263d3c0 |  | note | Inspection By: UCCL/ CEL
label | bbaa861a-0f3b-55a4-83fb-484f418e036c |  | note | Task Timing or Task Frequency: Commencement / Completion
label | 54959f82-b7d9-556a-a1c5-4931b783daa7 |  | note | Acceptance Criteria: IFC Drawing and IFC project specifications; Work Pack Checklist (if applicable)
checkpoint-status |  |  | checkpoint | Shop Drawings
label | 831de4b6-7066-50d7-8fb7-baccfb7b0283 |  | note | Specification Reference: Reviewed and approved prior to commencement
label | cf2b8681-12b1-55e9-909f-7a706c9028cb |  | note | Test Required: Designer general review of the shop drawings
label | 720ad202-62c3-5862-ad19-30058ed71f9f |  | note | Inspection By: UCCL/ CEL
label | 4d5d91d4-e7ef-500d-83ef-fb63a0675a20 |  | note | Task Timing or Task Frequency: 10 days prior to fabrication
label | 8ef3ce2e-9eb3-5f72-a467-83fb4d4198d2 |  | note | Acceptance Criteria: Shop drawing approval
checkpoint-status |  |  | checkpoint | Lifting Design
label | 8ffaff0c-5921-5978-8e9a-d96bc98d9680 |  | note | Specification Reference: Approved Code of Practice for the Safe Handling, Transportation and Erection of Pre-Cast Concrete.
label | 41bfaa15-178a-54b6-bdd7-fdb7121b9769 |  | note | Test Required: Lift design produced for demoulding, storage, transportation and installation of precast items
label | 2ebbefa4-7c6f-55ff-8ed4-039c686e77d4 |  | note | Inspection By: UCCL
label | 4e1f259a-6dc0-5e07-b45c-46777a3f6904 |  | note | Task Timing or Task Frequency: Prior to Casting
label | b731b596-7374-5882-9296-d8574781f399 |  | note | Acceptance Criteria: Lift Designs for each precast element
checkpoint-group |  |  | section | Material
checkpoint-status |  |  | checkpoint | Concrete Mix Design
label | 5eeb626f-52bd-51c4-b6a3-18f1fc1a605a |  | note | Specification Reference: NZS 3101, NZS 3109, NZS 3104, Project Specification Tauhara Steamfields – Structural Specifications
label | 447add7b-e28a-5d3f-8f77-80ce76849bfc |  | note | Test Required: Mix designs shall be supplied to Designer's for review and acceptance.
label | 91e9366b-4c99-50bd-b27a-e49afb961cad |  | note | Inspection By: UCCL/ CEL
label | f5a0d022-8a39-5fae-b44c-be8bfd4d6b94 |  | note | Task Timing or Task Frequency: Submission 4 weeks prior to pouring any concrete (intended for new concrete mix design)
label | f0cf006d-9fb2-5b32-a300-5c395ab40b5e |  | note | Acceptance Criteria: Approved Mix Design
checkpoint-status |  |  | checkpoint | Supply of Reinforcement Steel reinforcement compliance records
label | 21202f1f-7eeb-5e22-a3c2-1f99ac572242 |  | note | Specification Reference: In accordance with AS/NZS4671. Steel shall be grade 300 or 500 Compliance with Project Specification Tauhara Steamfields – Structural Specifications
label | bbd87f6d-8a43-5895-854c-a289a30cbf9f |  | note | Test Required: Schedules shall be prepared by the supplier and to be reviewed and accepted prior to fabrication.
label | 4061027b-5553-52ed-a65d-44c61420b613 |  | note | Inspection By: UCCL
label | 5364a65f-66f1-5286-86d6-6d0851e29be9 |  | note | Task Timing or Task Frequency: Per Delivery
label | a8557f4f-982f-592c-b61e-b438205b9639 |  | note | Acceptance Criteria: Manufacturer´s Mill Certificate/Rebar schedule/Rebar summary sheet
checkpoint-status |  |  | checkpoint | Embedded / inserts product data
label | 781ac1b1-7d0e-5cd7-8c45-49e560dac24a |  | note | Specification Reference: Compliance with Project Specification Tauhara Steamfields – Structural Specifications, and are in accordance with the Approved Code of Practice for the Safe Handling, Transportation and Erection of Pre-Cast Concrete.
label | fc45439a-a174-5b61-9df0-9e6e4d4a7225 |  | note | Test Required: Product data review
label | fd0a5366-4ada-57a4-9d66-0b7dece8f729 |  | note | Inspection By: UCCL
label | 349be3c4-d4e8-5199-b8cc-b2f9ed4c109f |  | note | Task Timing or Task Frequency: prior to casting
label | 340c14a1-bf28-55a7-a12d-2ad6c35969ba |  | note | Acceptance Criteria: Product testing conformance
checkpoint-group |  |  | section | Precast Fabrication (Pre-pour inspections & concrete testing)
checkpoint-status |  |  | checkpoint | Mould bed preparation
label | 10c71eb4-a566-5da8-9c8e-7e1142c46e1d |  | note | Specification Reference: Compliance with Project Specification Tauhara Steamfields – Structural Specifications
label | bf98ae56-4811-5c2d-b6b2-f7c17a837f1b |  | note | Test Required: Conduct inspection on precast mould bed for level and cleanliness.
label | 6ed331db-1987-5204-a50f-89914882898a |  | note | Inspection By: UCCL
label | f1f66e8d-9e04-5a8c-9947-cdae9f3b8a7e |  | note | Task Timing or Task Frequency: Prior to casting
label | 4eb483b5-36ab-5999-b850-1f186a83cddf |  | note | Acceptance Criteria: Concrete placement card
checkpoint-status |  |  | checkpoint | Steel reinforcement installation
label | d6c37439-0824-577b-b134-ea85f4bbfd83 |  | note | Specification Reference: IFC drawings, Approved shop drawings
label | 510bc3fe-6247-54ad-b3c0-61917135ec0b |  | note | Test Required: Check bar size, spacing, lap, location and cover.
label | 6aa117ae-3806-5332-b2e1-b625feff6cae |  | note | Inspection By: UCCL
label | 0610e036-ae53-50c1-b641-9357bd97c865 |  | note | Task Timing or Task Frequency: Prior to casting
label | ecf69709-fc0d-52ae-aea5-4905799bc64b |  | note | Acceptance Criteria: Concrete placement card
checkpoint-status |  |  | checkpoint | Embedded items including anchor bolts and couplers
label | 94c9c339-ffed-5b90-927e-00247b5c598f |  | note | Specification Reference: IFC drawings, Approved shop drawings
label | 27fef478-d1ca-5e1f-b3d7-5c82357c8426 |  | note | Test Required: Check size, type, number, location, alignment, elevation and that firmly supported / protected from damage or movement during the pour.
label | 749fd1bc-64e8-54b9-bb52-5200a7878d83 |  | note | Inspection By: UCCL
label | 74b720c6-52cf-54bb-ad46-fbb2f7976cd8 |  | note | Task Timing or Task Frequency: Prior to casting
label | 73348a48-dfd5-5a40-bcea-9bd4cebf6857 |  | note | Acceptance Criteria: Concrete placement card
checkpoint-status |  |  | checkpoint | Formwork moulds /Reinforcing
label | 67522cf7-6056-56ec-92b0-145a13ddb8a1 |  | note | Specification Reference: IFC drawings
label | c8191216-c3b5-5ecd-9707-0518390d0122 |  | note | Test Required: Dimensional checks against shop drawings, propping, chamfers and form release agent.
label | 4d6cab41-b412-5c41-bd2c-21912c055d34 |  | note | Inspection By: UCCL
label | 1670448d-d6b3-59a9-a906-c99ee8844026 |  | note | Task Timing or Task Frequency: Prior to casting
label | cf9f0452-de5f-50e2-9466-9c5df86755ef |  | note | Acceptance Criteria: Concrete placement card
checkpoint-status |  |  | checkpoint | Designer's Inspection
label | e5bd7b2e-e506-5cd2-92a1-f2302ca93fcb |  | note | Specification Reference: Specification / Project Requirements
label | e6ebdf31-0674-5bfa-8536-9748cbce8c3f |  | note | Test Required: No concrete shall be placed until the Designer's review / inspection.
label | d8d4c2d3-ad0e-54ec-86cf-4ad047072785 |  | note | Inspection By: UCCL
label | a42c2863-6396-571a-8c1a-184937d91ff5 |  | note | Task Timing or Task Frequency: Per individual structural element
label | 30da362c-5ed6-5b5a-a5a4-1fd4c96616d7 |  | note | Acceptance Criteria: Approved Drawings / Hold Point Release signed on Concrete Pour Inspection Sheet (ConQA)
checkpoint-status |  |  | checkpoint | Slump test
label | 3a4bbaa5-7c69-5cd1-bed8-c84d8b686ef6 |  | note | Specification Reference: Compliance with Project Specification Tauhara Steamfields – Structural Specifications
label | 78a3c695-5f5a-56e1-8a56-abfe8d5eadbb |  | note | Test Required: On site pre-pour
label | b2164aa1-bd33-5b53-8f63-61b807092d8f |  | note | Inspection By: UCCL
label | c4dfdf93-07e5-540b-bd01-2e1008d79de6 |  | note | Task Timing or Task Frequency: Each truck prior to placing
label | a7b8e4f7-b91c-51ae-8f1c-8658032b8236 |  | note | Acceptance Criteria: Concrete pour record sheet
checkpoint-status |  |  | checkpoint | Compression tests
label | e65ed6f4-ceb2-5143-9f3b-d13dd0ff56f6 |  | note | Specification Reference: Compliance with Project Specification Tauhara Steamfields – Structural Specifications
label | 38060542-d431-5eaa-9c5e-c8439a8171bc |  | note | Test Required: 1no. for 7 day & 2no. for 28 day
label | c3c031ad-8086-5190-a1f1-3fbeed31df1f |  | note | Inspection By: UCCL/ CEL
label | 00b1f60a-9392-5ac2-943c-a5ccc211cb6c |  | note | Task Timing or Task Frequency: 3no. specimens taken from each 100m3 of concrete placed (or part thereof), each day, of each different mix
label | 3b585652-a545-5438-97ad-07a61b657b2f |  | note | Acceptance Criteria: Concrete pour record sheet, IANZ Accredited Independent test report
checkpoint-status |  |  | checkpoint | Precast concrete curing
label | 5ef267cf-1d21-5692-8024-9d1f2ed2a6b8 |  | note | Specification Reference: Compliance with Project Specification Tauhara Steamfields – Structural Specifications
label | 80eca4ff-a2b2-5e69-bb28-86f9237f2919 |  | note | Test Required: Heat accelerated curing for panels instead of water curing proposed. Curing method to submitted and approved prior to casting.
label | cb1db793-a981-58da-aeb5-9033b199072d |  | note | Inspection By: UCCL/ CEL
label | d02d8be4-a8f7-5b66-927b-27392c5e253f |  | note | Task Timing or Task Frequency: After casting
label | 3e173fee-d01f-5ed9-a003-415ab8778180 |  | note | Acceptance Criteria: Concrete pour record sheet
checkpoint-group |  |  | section | Precast Fabrication (Post Pour Inspection)
checkpoint-status |  |  | checkpoint | Precast pre-delivery check
label | f7df378a-c718-5e58-b548-739fca1782f4 |  | note | Specification Reference: Compliance with Project Specification Tauhara Steamfields – Structural Specifications
label | f6a6e54f-cb41-5c7d-a7b4-635b7db3aa62 |  | note | Test Required: Check completed precast unit for compliance with the specifications, tolerances and drawings
label | 10b769fa-79fd-570a-b146-9dc3c14fb514 |  | note | Inspection By: UCCL
label | 98ac8de7-c21d-5f47-b686-ecfffd336544 |  | note | Task Timing or Task Frequency: Prior to delivery
label | e722f185-ca94-5c7e-ad61-737ce59cf34a |  | note | Acceptance Criteria: Supplier Fabrication ITP, Post Pour Inspection Record
checkpoint-status |  |  | checkpoint | Defective precast concrete or reinforcing
label | c68c66ba-3e26-5bd4-8286-d5ee7c02e3a7 |  | note | Specification Reference: CEL approval
label | 293328b3-2fff-5b6f-a115-6c2706ac122e |  | note | Test Required: Method statement to be prepared and agreed before repair is undertaken
label | 73243535-203e-5157-9301-ace8605efd51 |  | note | Inspection By: UCCL
label | af679819-263b-5a9f-b8a0-9c8d1da95b56 |  | note | Task Timing or Task Frequency: 2 wks prior to repair work
label | c263ea6b-1708-53ce-af06-8b1e2d7e4c42 |  | note | Acceptance Criteria: Method statement approval by RFI
checkpoint-status |  |  | checkpoint | Precast unit handling, transport and delivery
label | c8a80339-c901-5fc2-9371-175327a0ed47 |  | note | Specification Reference: Compliance with Project Specification Tauhara Steamfields – Structural Specifications
label | 344211c3-0269-54f7-a99d-bb6df8e3b339 |  | note | Test Required: Ensure precast units have been designed for all temporary load cases
label | 2e9201df-b5c2-5ad2-b8a2-01c98ae69943 |  | note | Inspection By: UCCL
label | b9b07c5f-26b6-5ec3-8813-23bb1490efe0 |  | note | Task Timing or Task Frequency: Prior to delivery / post installation
label | 21e5dbc0-d34f-5811-a97f-853c29e96b00 |  | note | Acceptance Criteria: Supplier Fabrication ITP, Post Pour Inspection Record
checkpoint-group |  |  | section | Post-Construction
checkpoint-status |  |  | checkpoint | As Built Survey
label | bb83cc87-6a1e-5d9c-bf26-06c1e4f2cb94 |  | note | Specification Reference: Compliance to IFC Drawings / Shop Drawings.
label | f1dd9b46-7527-54e4-8415-5ca1e5f36fd5 |  | note | Test Required: Red Line Markup for any change
label | 0f40f39c-ca27-55bd-8676-7e16bee882c6 |  | note | Inspection By: UCCL
label | 50194ee6-96f5-5c12-8deb-9c3f224a4592 |  | note | Task Timing or Task Frequency: Completion
label | b2cf9e4f-d9ba-5ec1-90d3-7f52eb08e200 |  | note | Acceptance Criteria: As built drawing/ report
checkpoint-status |  |  | checkpoint | Precast panel warranty
label | 3b5482c7-ffcd-5762-9437-3f8ec90f74f1 |  | note | Specification Reference: Compliance with Project Specification Tauhara Steamfields – Structural Specifications
label | 3460c9f6-7d3d-5a36-9065-1985708acc11 |  | note | Test Required: Product warranty
label | e6da029c-3b4b-595d-af3c-b5c5211ddd04 |  | note | Inspection By: UCCL
label | 98a897f2-8fe1-5f4f-b584-78b863e4640c |  | note | Task Timing or Task Frequency: Completion of supply
label | 069ff08a-6ea2-5f27-ab30-16005962750e |  | note | Acceptance Criteria: Warranty
checkpoint-status |  |  | checkpoint | Producer Statement
label | c1045c6f-d58b-55f9-9c93-c624d24eb8e5 |  | note | Specification Reference: Compliance with Project Specification Tauhara Steamfields – Structural Specifications
label | 8aeb70ca-485e-5202-995f-be4d7b66cf70 |  | note | Test Required: Precast subcontractor producer statement
label | d79e7dac-851e-5652-9015-968827571814 |  | note | Inspection By: UCCL
label | 51517d29-7f92-59f6-8816-90faf50574e2 |  | note | Task Timing or Task Frequency: Completion of supply
label | 1b9ac540-4615-560d-91ec-239265c1403b |  | note | Acceptance Criteria: Signed PS3 Certificate
checklist-sectioned |  |  | checklist | ITP 001 Separation Slab Foundation |  |  |  |  | Yes | ITP 001 Separation Slab Foundation v4 | 67ce0164-3071-4b7a-8a6a-4ece2787a930
checkpoint-group |  |  | section | Preliminary
checkpoint-status |  |  | checkpoint | Concrete Mix Design Approved
label | 80ea9053-0e5b-5abb-8cc1-e0d87ad3acc0 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 81da0111-b975-54e2-84fa-e6180c35f617 |  | note | Test Required: Jacbos
label | e7a9fa17-5de8-5b12-8026-687bb4c36efb |  | note | Inspection By:: Engineer
label | d8f69558-d672-5b76-bfb2-e812af5653bf |  | note | Task Timing or Task Frequency: Formal request/RFI
label | d0e0c0c2-6545-52b7-bf01-4899ca011e03 |  | note | Acceptance Criteria: Approved by Engineer
label | af995c37-4e65-50e2-8597-cdb54573d7c5 |  | note | UCCL - H
label | c4bfbe86-270f-55e3-ac97-da78cafbbd02 |  | note | Client - R
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Mix Design Trails
label | 01d580b0-7983-58c8-883b-7a7485d3d9f5 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 33173005-55dc-5919-81df-c565660c3622 |  | note | Test Required: Temperature, slump and strength
label | 06e5fe9d-78bc-5e3b-b833-90f47bef71bb |  | note | Inspection By:: Engineer
label | dcad5a92-457a-5547-83c6-07979ef94d92 |  | note | Task Timing or Task Frequency: Per Mix Design
label | 473045c7-c2ac-5bfd-b2ba-47dfde3186ad |  | note | Acceptance Criteria: Approved by Engineer
label | bf9b7654-3f12-56d7-baab-22be90d1f24c |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete - 1
label | 1c64033b-b83a-5ecc-9847-23c63c66df35 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | d8d183d1-2b55-5019-a91d-e7e3446401bb |  | note | Test Required: Compressive Strength
label | d2c3e300-dd83-5e31-aed8-20fd8bfcc23d |  | note | Inspection By:: Supplier
label | e4d456c0-550c-524b-b051-d783e989cc5b |  | note | Task Timing or Task Frequency: 1 Set of 3 tests for every 50m³ testing at the plant and 100m³ on site. Slump test on first 2 trucks from each plant. Then visual slump test for the pours over 20m³ and intermitted/random testing every 100m³.
label | 53726a75-eb41-526d-b88a-41c9d54ff46f |  | note | Acceptance Criteria: Slump Test, Air Content Test, Compressive strength test results, shrinkage strain. Accreditation/ Registration certificate from Laboratory
label | 633f1ec0-315f-55d8-adbe-71aeb694b2bb |  | note | H
label | 5ddf06b2-dbc1-572b-9581-7c79657d0839 |  | note | Client - R
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete - 1.1
label | ae1adf2d-d593-5197-a1e9-6c06cae532e8 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 5a9b9f45-4b70-588d-ad3d-091da558c942 |  | note | Test Required: Slump Test
label | 2277121c-ae26-51af-9617-c087172cc3be |  | note | Inspection By:: Supplier
label | 990d738e-184b-522e-9849-89fda88e87dd |  | note | Task Timing or Task Frequency: As Per above
label | 57fde172-3a51-5d65-99a8-0983adffdd47 |  | note | Acceptance Criteria: As per Above
label | c13b15a5-c1ce-5855-b4ae-78a50eec3ab4 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete - 1.2
label | 98e04f16-8f45-5c27-9c9c-dfbbb3a2441f |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 675a71a0-5c2a-58bb-b666-8b4c4cb3b70d |  | note | Test Required: Air Content Test
label | 5a08cfd3-5f67-5cae-96ee-0b2a58e180d2 |  | note | Inspection By:: Supplier
label | cc9b0eba-c2c5-51a1-8938-d3a02b4e6079 |  | note | Task Timing or Task Frequency: As Per above
label | 929aa058-da65-5287-a1c6-30c654cc7d20 |  | note | Acceptance Criteria: As per Above
label | 6ae2ef27-2319-5bbe-81eb-1b60f4b2433d |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete - 1.3
label | c3289a7f-1e00-5748-9f20-a211287bd044 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | e691a3e1-658c-5254-8d03-9989a91b2c34 |  | note | Test Required: Shrinkage strain at 56 days
label | 3bda15f0-6120-5366-a9b7-6c5db6db634c |  | note | Inspection By:: Supplier
label | b01f1cd7-5dd7-53b3-922e-a0e92f23ad67 |  | note | Task Timing or Task Frequency: As Per above
label | 3fcb86f4-7b0b-573b-8d4a-fbb54b0e3fe9 |  | note | Acceptance Criteria: As per Above
label | 822d54ae-9a6f-5e84-9306-da6f30ba7065 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-group |  |  | section | Pre-construction site works
checkpoint-status |  |  | checkpoint | Ground Condition/Subgrade
label | 8ba90550-c8e0-5f3c-88ac-eb9d2ec4b2bc |  | note | Specification Reference: TABG-JEC-0-ULJ-STR-AGT-1201-1 Note 4
label | 4b4d9b17-76b5-533f-8911-685538f9d647 |  | note | Test Required: Geotechnical testing
label | 4ab6665b-a451-5704-9921-fe2e141685a7 |  | note | Inspection By:: Contact
label | 216c01f3-c8a5-5b93-ba22-c35c5bdd1213 |  | note | Task Timing or Task Frequency: Before placement of any site concrete, Scala penetrometer testing, proof roll.
label | 1333d415-1a9d-56ec-b46c-1082d578e912 |  | note | Acceptance Criteria: Geotech Report by Client with confirmation that Foundation is suitable (minimum 200 kPa allowable bearing capacity).
label | 27a2e7bb-d2e9-5f43-b4de-f20050d01021 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Trim Sub grade
label | 6bab0e58-0239-5221-bc63-b425ee4cf6b5 |  | note | Specification Reference: TABG-JEC-0-ULJ-STR-DET-1206
label | 5ae2baf5-d2c2-5154-9cad-3da264a28f63 |  | note | Test Required: Survey plan
label | f80f2a9b-8027-577d-a7e8-db70f112a656 |  | note | Inspection By:: UCCL/Engineer
label | 3686244d-5301-53cb-a409-eaa24acd5a71 |  | note | Task Timing or Task Frequency: Before placement of any site concrete check sub grade profile
label | fe91edca-e9db-53a7-92a9-86b6ba20a2d4 |  | note | Acceptance Criteria: Finished height for sub grade + 10/-50mm. Minimum thickness to be 50mm as per IFC Drawing. Target RL 468.950*
label | 217eb6f3-545d-5e10-86e0-9cd93f193d2b |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Site Concrete/binding
label | cbac0e25-cafd-5e21-b418-9d4470d9c5e5 |  | note | Specification Reference: TABG-JEC-0-ULJ-STR-AGT-1201-1
label | 4d28e9f1-bb0f-5397-8297-7f8fb2064c6e |  | note | Test Required: Visual Inspection
label | 33229303-26c6-59b4-9e53-93ac44a15965 |  | note | Inspection By:: UCCL/Engineer
label | 7520e96b-155e-50cc-87e6-98ffe5cc6eac |  | note | Task Timing or Task Frequency: Thickness, minimum 50mm, consider 75mm depending on subgrade.
label | 9b67fb93-1da8-5fe9-85b1-7aa5c1834dd3 |  | note | Acceptance Criteria: Finished height for site concrete to be within +/- 10mm.Thickness, minimum 50mm, consider 75mm depending on subgrade. Target finish RL 469.000
label | 5c8b9c03-5540-5d34-9237-f0b853b3423f |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Setout
label | 26512f3a-6c78-5430-83fe-9070f8061f2e |  | note | Specification Reference: TABG-JEC-0-ULJ-STR-AGT-1201-1 Note 3
label | 30ed6c89-53da-5f34-b91e-98a77cba146b |  | note | Test Required: Surveying as built/Visual Check
label | 9ad9e2f2-488a-5524-92e2-25e77c7dacf9 |  | note | Inspection By:: UCCL/Engineer
label | dbf095a9-5bf1-52fd-a6a7-1333a32df832 |  | note | Task Timing or Task Frequency: For set out of each Foundation. After placement of Formwork
label | da2bd5ab-b2b2-5e77-a6b0-f08a4788022e |  | note | Acceptance Criteria: Finished height of embedded items +/- 10mm vertically and +/-20mm laterally
label | 6962f5d6-2b89-53d0-9251-866f25fc4fb7 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-group |  |  | section | Foundation
checkpoint-status |  |  | checkpoint | Setout 1
label | b4e11969-4947-5324-a0ec-892da225a021 |  | note | Specification Reference: Design / IFC Drawings
label | 0ecb0eb5-5684-5135-a006-cf01bdf298fb |  | note | Test Required: Surveying/Visual Check
label | 875627c7-7580-5cbe-a8f2-7b00eb8dc3fb |  | note | Inspection By:: UCCL
label | 051326dc-53d9-57ec-b33f-e09500cf9e55 |  | note | Task Timing or Task Frequency: For set out of each Pour
label | fe22c94d-cfe3-5a34-bd12-3bd11af968d5 |  | note | Acceptance Criteria: As per IFC Drawings & site issue Drawing.
label | 5322a521-c781-5289-acda-9e340a00b831 |  | note | W
checkpoint-status |  |  | checkpoint | Setout 1.1
label | 8da6f5b4-25f3-59e4-a175-e9142f3aaf2b |  | note | Specification Reference: Design / IFC Drawings
label | 987f0cf2-7dc6-5731-862f-9aabf4ce3a8a |  | note | Test Required: Surveying/Visual Check
label | 1351bec5-2b04-5121-ae9c-85f52d1863f3 |  | note | Inspection By:: UCCL
label | 8adf7476-16ad-5d33-ada6-cddfe4fd48dc |  | note | Task Timing or Task Frequency: Pour -1
label | f36808e2-1443-5ec5-99e2-e621f4a8dc60 |  | note | W
checkpoint-status |  |  | checkpoint | Setout 1.2
label | ecd45e93-15e0-5618-a371-24d5044e4016 |  | note | Specification Reference: Design / IFC Drawings
label | 1db58bb6-27ae-589a-8968-5103e9772c3b |  | note | Test Required: Surveying/Visual Check
label | 3eda5231-93e2-5769-afcc-554cccc26e26 |  | note | Inspection By:: UCCL
label | 7b7ebaaf-7590-53df-b5e8-ffae243591c8 |  | note | Task Timing or Task Frequency: Pour -2
label | 24492964-1adf-5109-a221-ac211b8fd3c2 |  | note | W
checkpoint-status |  |  | checkpoint | Setout 1.3
label | fe628ab8-a9a7-5d4f-8a22-013e8ff8ee0f |  | note | Specification Reference: Design / IFC Drawings
label | 5080074d-0183-51a5-93bf-83fcdaa59080 |  | note | Test Required: Surveying/Visual Check
label | 97f8be22-f052-5950-a572-33b51a380134 |  | note | Inspection By:: UCCL
label | 25cbfef7-ae5f-5ccb-a281-f11833c59ca0 |  | note | Task Timing or Task Frequency: Pour -3
label | d016ec40-503f-524f-afa6-ca226eae9a68 |  | note | W
checkpoint-status |  |  | checkpoint | Setout 1.4
label | 130a3eb6-b653-5c31-be5c-f5c9c9f03300 |  | note | Specification Reference: Design / IFC Drawings
label | 7016d35b-6141-5555-be07-02ca5d4de8b7 |  | note | Test Required: Surveying/Visual Check
label | af88b37b-e136-53cb-ac42-38e59a5d1581 |  | note | Inspection By:: UCCL
label | 23f45d40-553f-5fa8-8fe7-c36f0684b638 |  | note | Task Timing or Task Frequency: Pour -4
label | 18d44321-9e48-58e5-b17d-1178c0927a16 |  | note | W
checkpoint-status |  |  | checkpoint | Setout 1.5
label | 0a641113-f04b-5ea4-9fdd-20b4d5574c0f |  | note | Specification Reference: Design / IFC Drawings
label | 0a42e543-28ea-579c-b246-da1334ddb293 |  | note | Test Required: Surveying/Visual Check
label | 093fad23-01bc-5595-b60d-9af4e6501146 |  | note | Inspection By:: UCCL
label | cc3b755c-36bb-5ba2-854d-500006e5209e |  | note | Task Timing or Task Frequency: Pour -5
label | b98e1500-ac59-5dd1-8d24-90fd74079fa1 |  | note | W
checkpoint-status |  |  | checkpoint | Setout 1.6
label | e05cc5d2-2547-5dbb-a009-7c8bcc056ce4 |  | note | Specification Reference: Design / IFC Drawings
label | 929f7574-4ff8-5d73-8844-47a69b97c760 |  | note | Test Required: Surveying/Visual Check
label | 8adcb472-29c8-5af9-bb52-eef1be6704ec |  | note | Inspection By:: UCCL
label | 17b50dd3-f071-51d7-b4ff-0c1b8f10f24b |  | note | Task Timing or Task Frequency: Pour -6
label | 8a01fd81-d22c-56ac-90d4-30285ecebfe9 |  | note | W
checkpoint-status |  |  | checkpoint | Setout 1.7
label | 601ec1dc-7204-5dd4-9695-b882600ef4d0 |  | note | Specification Reference: Design / IFC Drawings
label | 836ee45b-a416-500d-bce3-69aa832cf57f |  | note | Test Required: Surveying/Visual Check
label | 2acb5c52-be43-5cb3-a08b-6fffa06ca6d0 |  | note | Inspection By:: UCCL
label | 7f7ef144-56d1-5775-a5c8-1aba9acb994c |  | note | Task Timing or Task Frequency: Pour -7
label | 0bdd99d5-7a54-5aca-82df-ec1d34e52dc7 |  | note | W
checkpoint-status |  |  | checkpoint | Setout 1.8
label | 4ff79f01-9293-541a-8440-0fd67f80a752 |  | note | Specification Reference: Design / IFC Drawings
label | 3bff3e33-c427-5113-9597-660aba4b2c34 |  | note | Test Required: Surveying/Visual Check
label | d9cf844f-3d8b-5704-94ad-fcf3b5cf6edb |  | note | Inspection By:: UCCL
label | b329d1a1-e25a-5aad-bb73-74d959b5d7cd |  | note | Task Timing or Task Frequency: Pour -8
label | 45efcdca-03d5-5ca5-9ce9-5ee454ab46ef |  | note | W
checkpoint-group |  |  | section | Pre-Pour Inspection
checkpoint-status |  |  | checkpoint | Pre pour inspection for each Pour
label | 0a26eaae-fc76-5286-8ef8-f0fa7d2d60a2 |  | note | Test Required: Visual Inspection
label | 7b59f77c-659f-55f1-b504-565247b1398b |  | note | Inspection By:: Engineer
label | d0edd09f-17d8-5083-adbe-1b13636412cf |  | note | Task Timing or Task Frequency: Pre pour inspection for each Pour
label | 994bdea6-852c-5f4c-9a3e-78e436c178fc |  | note | Acceptance Criteria: Pre pour inspection check sheet
label | 5aa55cad-c200-5ccf-9437-2a148accef11 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Pour 1
label | f76f23f7-ad33-594d-befe-b5bd4c18745d |  | note | Test Required: Visual Inspection
label | e31c9445-fe9a-50f1-aa5b-b6f264b602b7 |  | note | Inspection By:: Engineer
label | 2adf366c-4b58-5855-aaee-59db3d7f7f5d |  | note | Task Timing or Task Frequency: Pour - 1
label | 4603ffb7-cee9-53a1-881e-2340786483b6 |  | note | Acceptance Criteria: Pre pour inspection check sheet
label | 5e267415-df5b-5a41-b9d2-3a808034bac0 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Pour 2
label | 34848b46-d51e-5295-96f5-ce6a425aae82 |  | note | Test Required: Visual Inspection
label | 9028e558-a559-5363-aec3-d805fd545d3d |  | note | Inspection By:: Engineer
label | 442f4669-b531-5669-bfc5-24a12c421a36 |  | note | Task Timing or Task Frequency: Pour - 2
label | 41c13338-055a-54a6-94e7-1a1d7695593d |  | note | Acceptance Criteria: Pre pour inspection check sheet
label | a378647b-5705-5f9a-9c09-17c5aa24cac1 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Pour 3
label | bbbf182a-6e17-50de-a6ad-1525193680f1 |  | note | Test Required: Visual Inspection
label | 7a53fd3e-ab83-5353-b4b9-5f40ce96c005 |  | note | Inspection By:: Engineer
label | 2db2dd2e-f3c2-591c-94df-db1f57ea5c7a |  | note | Task Timing or Task Frequency: Pour - 3
label | 348d21b8-6c7d-549c-87b7-a70ae3ea49ed |  | note | Acceptance Criteria: Pre pour inspection check sheet
label | 26f3a496-1264-58a6-b7ae-f535f43ae4b7 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Pour 4
label | ecb91866-42a8-5471-979a-1ea255bbef00 |  | note | Test Required: Visual Inspection
label | bce5c373-e885-5709-8ebc-9737b963f0ee |  | note | Inspection By:: Engineer
label | 0883dec8-79e8-58c0-ba11-72a586866354 |  | note | Task Timing or Task Frequency: Pour - 4
label | c6e259bf-e4d6-5835-9f46-19886d286be7 |  | note | Acceptance Criteria: Pre pour inspection check sheet
label | 9beb02e8-e1e9-5921-8683-2e23842f88ee |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Pour 5
label | f35d6616-c46c-5f5a-9771-6440ae05fec2 |  | note | Test Required: Visual Inspection
label | 20cb1a8d-98f1-5b0a-b1c7-3d1972f6f398 |  | note | Inspection By:: Engineer
label | e32e62f2-525e-52e9-95d8-cfeebdc52fea |  | note | Task Timing or Task Frequency: Pour - 5
label | 2c78bc9b-5b6a-51ba-9c88-2f9eaf1ee164 |  | note | Acceptance Criteria: Pre pour inspection check sheet
label | c34a72ab-53f9-5e95-ab8f-64071d3dfa9b |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Pour 6
label | 61e8e445-2549-5fd3-a5dd-43137f1fdc28 |  | note | Test Required: Visual Inspection
label | 0b32dd6a-60c6-513f-8419-47387680fe84 |  | note | Inspection By:: Engineer
label | 9400a1d8-0ac8-59f0-abfb-0e9c925ae67b |  | note | Task Timing or Task Frequency: Pour - 6
label | b0d03ae6-bed5-5495-949a-50ef2ea804df |  | note | Acceptance Criteria: Pre pour inspection check sheet
label | 33ac1987-a9cd-5f44-a77c-5e57d0b53055 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Pour 7
label | b5239922-1124-51d5-9897-ab6a16979e75 |  | note | Test Required: Visual Inspection
label | 978236f0-36b6-54e9-8921-26617415634b |  | note | Inspection By:: Engineer
label | d770a647-66da-500c-884d-1de7b4fe526b |  | note | Task Timing or Task Frequency: Pour - 7
label | 2a0f7ddf-c22b-5672-9963-e515cbbd0c4b |  | note | Acceptance Criteria: Pre pour inspection check sheet
label | 8c04063b-4c35-54a1-ad2c-9366c475074b |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Concrete Pour 8
label | 14166cef-e7f8-5c74-ab81-e7fe62bad3e6 |  | note | Test Required: Visual Inspection
label | 39114b1f-b917-5712-846c-10fc17bde910 |  | note | Inspection By:: Engineer
label | be4721ea-240a-5248-b367-09277fb02044 |  | note | Task Timing or Task Frequency: Pour - 8
label | 3712d3db-ae51-54d7-af29-c4fffad25f93 |  | note | Acceptance Criteria: Pre pour inspection check sheet
label | a51b48b0-d982-5146-b623-dea7487262c2 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Embedded Items for Concrete Pour
label | b80f4590-f590-5676-803e-644101247194 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 39df5ea9-66df-5784-9d10-fa27b278da40 |  | note | Test Required: QA Documents and PS4
label | c470a495-6379-5a40-b8e4-1d73adebe829 |  | note | Inspection By:: Engineer
label | dee37c91-abf4-5cc3-a11c-66b91c234439 |  | note | Task Timing or Task Frequency: Pour-1
label | c1919a0e-ebfa-5fa8-9a80-caec499a6e04 |  | note | Acceptance Criteria: As per specifications. Confirmation from Engineer
label | cc42d172-a860-5138-b139-b54cab3f9109 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Embedded Items for Concrete Pour 1
label | dba95c33-e72d-5cfe-a802-5800deac930b |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | a5bfbb56-59b5-590d-be93-0aa3e969922f |  | note | Test Required: Visual Inspection
label | 10d1d43b-1588-5e5f-9db4-cac72003e7df |  | note | Inspection By:: Engineer
label | 6dd27c7e-8598-59bb-b0d0-8cfbf336ac2d |  | note | Task Timing or Task Frequency: Pour-2
label | bc2b117c-3465-5d66-85df-ed7eb5688d6f |  | note | Acceptance Criteria: as above
label | 6d1c17f3-9e93-55e7-bb50-048ec1a905bd |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Embedded Items for Concrete Pour 2
label | 51def203-4731-5f95-9fa5-43e593366bdf |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 11bcf67f-54d5-50bf-b458-c47ca4e8f314 |  | note | Test Required: Visual Inspection
label | f9a9c11a-023a-56c4-8004-0f4fe96bb3e6 |  | note | Inspection By:: Engineer
label | 125143a9-553a-5840-b603-d40691fca702 |  | note | Task Timing or Task Frequency: Pour-3
label | 48f7e1a3-9d3b-58ae-aa59-438ed5303c25 |  | note | Acceptance Criteria: as above
label | cc948da5-c979-58be-9526-14b49dd09d7a |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Embedded Items for Concrete Pour 3
label | 61380c29-5553-5dff-8084-a6813eb725fd |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 95d969f0-f2ac-53fe-ba42-9ec72d093b7f |  | note | Test Required: Visual Inspection
label | 91d7b374-44a5-5a7c-8d7f-84585abf7764 |  | note | Inspection By:: Engineer
label | 012f9581-bc54-5a3f-ad14-b35a74e0534d |  | note | Task Timing or Task Frequency: Pour-4
label | d8a82ca9-77ff-5b18-a721-6e0a27b9a3f9 |  | note | Acceptance Criteria: as above
label | 33f9c6bd-af44-5337-9ce4-d211b0543e28 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Embedded Items for Concrete Pour 4
label | 4b0704b0-6d18-5fff-9518-371e79d29f96 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | cb2eabc3-7509-5702-8015-768575173de4 |  | note | Test Required: Visual Inspection
label | 864c0b2c-fab5-527f-8869-058acb8727a2 |  | note | Inspection By:: Engineer
label | 5885937d-5af0-5043-9f1e-f4b7486fd298 |  | note | Task Timing or Task Frequency: Pour-5
label | 9553dbc2-829b-5f2b-b2ed-17173648a5eb |  | note | Acceptance Criteria: as above
label | 2858eb17-171c-5921-b8c5-bb37d9a23624 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Embedded Items for Concrete Pour 5
label | a8df3af9-e417-5ef9-ac37-2deb47a1227d |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | ab5e348a-7184-5505-b330-4f4c13544bd5 |  | note | Test Required: Visual Inspection
label | 2811ecd2-6005-5537-9f4b-aafd297d9dcf |  | note | Inspection By:: Engineer
label | 0929600f-d288-51f4-9e76-9063ee09a4c7 |  | note | Task Timing or Task Frequency: Pour-6
label | 50f5495b-5fff-535d-a330-cb9022995e0a |  | note | Acceptance Criteria: as above
label | d4b48a93-877b-5ab8-b923-919316c2a1e3 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Embedded Items for Concrete Pour 6
label | 44bbc94d-3076-5305-a84e-9548ae99d1fb |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 5a5314a0-c4ac-5613-8840-dcb451d1fd00 |  | note | Test Required: Visual Inspection
label | b7016360-97f1-5d3b-bbd7-536bf62b4485 |  | note | Inspection By:: Engineer
label | 155050b4-5eac-5624-bbee-8056c484667b |  | note | Task Timing or Task Frequency: Pour-7
label | c912a756-d82f-5e69-8e7d-c56691c6ca76 |  | note | Acceptance Criteria: as above
label | 55fee6c7-6249-5df7-956f-e145cd1fa214 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | Embedded Items for Concrete Pour 7
label | e924e2aa-fae3-5ac8-af18-9bed6dc06904 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 67965e6d-085f-567f-958e-a7a879ef62c4 |  | note | Test Required: Visual Inspection
label | f3fd4673-e697-56f2-aefb-23db102e621b |  | note | Inspection By:: Engineer
label | 6ae37027-8919-537b-b557-911982739057 |  | note | Task Timing or Task Frequency: Pour-8
label | bbfe9806-3387-542c-ad5b-029fff0fbd18 |  | note | Acceptance Criteria: as above
label | effba40f-fc06-531a-8319-f1116cb37cae |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checkpoint-group |  |  | section | Post pour Inspection/Curing
checkpoint-status |  |  | checkpoint | Post Pour Inspection for each pour
label | c507c3a3-d42f-5904-a02d-86875f0edbc4 |  | note | Test Required: Surveying/Visual Check
label | e08b2f33-582a-5901-994b-b3e556a4d577 |  | note | Inspection By:: UCCL
label | d6db6e64-00d9-577c-aa08-5c1c333e47ba |  | note | Task Timing or Task Frequency: Post Pour Inspection for each pour
label | 998cc236-f777-5e5b-b7bd-788561792bc6 |  | note | Acceptance Criteria: Post Pour Inspection Check sheet
label | 2fe3d0d6-14df-593e-b07b-2029394d989f |  | note | W
checkpoint-status |  |  | checkpoint | Concrete Pour 1
label | c4b3c483-cbfb-55b5-b2bc-b7cb809f2962 |  | note | Test Required: Surveying/Visual Check
label | 5859797c-1115-59a7-a460-9301350c52a3 |  | note | Inspection By:: UCCL
label | 47c5bfdc-872d-5ee4-a543-d74e7db54fcd |  | note | Task Timing or Task Frequency: Pour - 1
label | a251e9fd-99c3-5479-834e-2a1eae48df4b |  | note | Acceptance Criteria: Post Pour Inspection Check sheet
label | c59d5d24-0878-5098-92a2-d06da9e0c1f2 |  | note | W
checkpoint-status |  |  | checkpoint | Concrete Pour 2
label | 18422bba-974f-5983-9f02-7464df1d894d |  | note | Test Required: Surveying/Visual Check
label | 065378c3-bb78-5fe0-8837-7dc98bb11686 |  | note | Inspection By:: UCCL
label | 5ab30b9a-6eb8-5468-bac0-25d097d97a49 |  | note | Task Timing or Task Frequency: Pour - 2
label | e2ed0050-b3cd-58c7-8572-f76f7bfb50a8 |  | note | Acceptance Criteria: Post Pour Inspection Check sheet
label | 382c402a-befa-51a5-908f-7a2fcfb17a67 |  | note | W
checkpoint-status |  |  | checkpoint | Concrete Pour 3
label | cf54e21c-27a3-51bd-97cf-a00541448953 |  | note | Test Required: Surveying/Visual Check
label | 9ee0f0a1-29f5-5c50-9166-d025a7a2d29a |  | note | Inspection By:: UCCL
label | 3494a6ae-de79-508b-8886-7b0a5d3731b5 |  | note | Task Timing or Task Frequency: Pour - 3
label | 4b4e8b29-b6b0-55b8-a29e-8e53028852c6 |  | note | Acceptance Criteria: Post Pour Inspection Check sheet
label | 8a61821b-707a-5eee-9cd8-6e7270973fb5 |  | note | W
checkpoint-status |  |  | checkpoint | Concrete Pour 4
label | 0f7cd065-90ca-5b2a-93d6-ea01895b3811 |  | note | Test Required: Surveying/Visual Check
label | 15fe6e21-feea-5f37-aa78-deb071fda862 |  | note | Inspection By:: UCCL
label | 18316bf8-57be-5d41-b41f-e998369add02 |  | note | Task Timing or Task Frequency: Pour - 4
label | fcf1f3a6-8eba-58e5-8217-07c6fd320d19 |  | note | Acceptance Criteria: Post Pour Inspection Check sheet
label | ad051272-6b05-5297-b3d2-2245499085af |  | note | W
checkpoint-status |  |  | checkpoint | Concrete Pour 5
label | f7fb9e80-12ed-5e33-a336-09fea5208e66 |  | note | Test Required: Surveying/Visual Check
label | c98f0036-e7fa-5e13-a6a6-34c2e7b9e34b |  | note | Inspection By:: UCCL
label | bd9799e2-aefc-5fc6-8b52-dd6052b30f3a |  | note | Task Timing or Task Frequency: Pour - 5
label | 80753713-80a0-57d9-bd17-6ebf5c093f93 |  | note | Acceptance Criteria: Post Pour Inspection Check sheet
label | c4999389-3e5b-5c54-ada5-cd35452938b0 |  | note | W
checkpoint-status |  |  | checkpoint | Concrete Pour 6
label | 8d199dad-dc74-52c2-afd9-39f480a1aa05 |  | note | Test Required: Surveying/Visual Check
label | 257eaa9d-ca80-51c0-b6b7-0ab2eef58005 |  | note | Inspection By:: UCCL
label | 5ac87fdf-97fb-5a7b-a6d9-0e3ef72caf3f |  | note | Task Timing or Task Frequency: Pour - 6
label | b1ccb856-554f-54f0-80e2-8d1a41cd345a |  | note | Acceptance Criteria: Post Pour Inspection Check sheet
label | 5ef3db55-3feb-5e81-9927-9f9ab4809cbd |  | note | W
checkpoint-status |  |  | checkpoint | Concrete Pour 7
label | 3b375026-6472-5d31-b925-268b06a68ca0 |  | note | Test Required: Surveying/Visual Check
label | 89ea7a76-ccb9-58a8-90f9-1dbbc45cce46 |  | note | Inspection By:: UCCL
label | e37a92cb-a83f-5685-a737-27e5acb24541 |  | note | Task Timing or Task Frequency: Pour - 7
label | 78822c18-e225-5f81-bcfc-8be85c4cae47 |  | note | Acceptance Criteria: Post Pour Inspection Check sheet
label | 0e84efcb-71f2-5fad-a52d-ae9c9887e095 |  | note | W
checkpoint-status |  |  | checkpoint | Concrete Pour 8
label | 47484031-bc65-59e1-bef1-4b0dd8fa7247 |  | note | Test Required: Surveying/Visual Check
label | 6dd07510-2f1a-56b8-836b-39341a8a2b4f |  | note | Inspection By:: UCCL
label | 88038cef-451b-5b1d-aa83-8e8e1469ba89 |  | note | Task Timing or Task Frequency: Pour - 8
label | 2191965b-23e7-5158-b27f-0779dbe000a0 |  | note | Acceptance Criteria: Post Pour Inspection Check sheet
label | fe2bc70c-7843-55c2-91a4-92cf611e6a65 |  | note | W
checkpoint-group |  |  | section | As Built
checkpoint-status |  |  | checkpoint | As Built
label | 7df6a31c-4e71-55c1-9e7e-58354deeacfd |  | note | Test Required: Surveying
label | ad0c0c11-6bd3-5090-9610-deef66352ea2 |  | note | Inspection By:: UCCL
label | 676fb21d-5ba3-504f-b0e7-161df81f4fd1 |  | note | Task Timing or Task Frequency: For each Pour
label | 40b08f98-9a8e-55f8-ab97-55b61d77f319 |  | note | Acceptance Criteria: Confirmation From Engineer on as built records
label | 2435cd3b-fd1f-58ec-a89a-a6968a639010 |  | note | H
holdpoint |  |  | signoff | HOLD POINT
checklist-sectioned |  |  | checklist | ITP - Site Wide Drainage R1 | itp |  |  |  | Yes | ITP - Site Wide Drainage R1 | 6f1a6875-5107-48e1-9476-019d7d8d5d5a
checkpoint-group |  |  | section | Preliminary
checkpoint-status |  |  | checkpoint | Material - Precast Concrete Pipe
label | 78e8a81f-d89a-57ae-a293-77e4644261cb |  | note | SPECIFICATION REFERENCE - TABG-JEC-0-000-GVC- SPC-0002 - Civil and Geotechnical Specification
label | 152e3210-9aa1-5735-92f4-f8dc97e44d43 |  | note | TEST REQUIRED - Producer statement
label | 6a20a0e6-b348-54f7-9343-e404103dd598 |  | note | INSPECTION BY - UCCL
label | 553b8ec4-fe35-5149-b16a-425c9bccf579 |  | note | TASK TIMING OR TASK FREQUENCY - Prior to Construction
label | 17c569fd-6380-5664-af70-a3ad073a103f |  | note | ACCEPTANCE CRITERIA - Concrete pipes shall be of the correct Class, made from Sulphate Resistant Concrete and comply with AS/NZS 4058:2007
label | 54c3faaa-e97c-54bf-93f2-8b319f248940 |  | note | UCCL - V
label | f9c3e282-72ef-5211-9be4-d65bbd784708 |  | note | Client - V
text | a3f5d8a2-c902-5724-a1b5-3d79d699a879 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Material - Manholes, catchpits and wingwalls
label | 52dfddaf-e353-54f9-a89c-918ae35a78f0 |  | note | SPECIFICATION REFERENCE - TABG-JEC-0-000-GVC- SPC-0002 - Civil and Geotechnical Specification
label | 55e6c44b-b5b0-52d9-bc62-edbbc02dba5f |  | note | TEST REQUIRED - Producer statement
label | 553c0b41-b874-52ed-89b0-2f30775e3807 |  | note | INSPECTION BY - UCCL
label | 80745118-8b15-58a3-a0ff-64ed6f705170 |  | note | TASK TIMING OR TASK FREQUENCY - Concrete Manholes
label | f136cf34-b7a9-5b4a-818f-addc3e2cd0ac |  | note | ACCEPTANCE CRITERIA - Manholes shall be centrifugally spun and comply with AS/NZS 4058. Concrete products shall be made with Sulphate Resistant Concrete. Manholes shall also have holes cast in for steps. Catchpits shall be precast reinforced concrete as per NZS 3109. Wingwalls shall be precast reinforced concrete in accordance with NZS3109.
label | dd782d2f-af91-5c75-ab66-45b29920dd12 |  | note | UCCL - V
label | 28f96e51-65b9-5d66-be8c-047d80718a93 |  | note | Client - V
text | 4acd9237-7b07-56a6-982f-32588b761e50 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Material - Frame, Covers and steps
label | 5197e5b8-75d1-53c7-bd9b-d352c2b2f8fc |  | note | SPECIFICATION REFERENCE - TABG-JEC-0-000-GVC- SPC-0002 - Civil and Geotechnical Specification
label | 8a644890-92c0-5453-b751-951f05580cd9 |  | note | TEST REQUIRED - Producer statement
label | 3528e2e9-114b-522d-9dcb-fb4015bc8f6f |  | note | INSPECTION BY - UCCL
label | 60b739f4-f6b8-553e-876c-6ff2b6c6e03a |  | note | TASK TIMING OR TASK FREQUENCY - Frames, Covers and steps
label | 95c2cd17-9f95-5545-8097-0f7498ad4afc |  | note | ACCEPTANCE CRITERIA - Heavy Duty lids are to be used unless otherwise stated. Cast iron cover and frames to be light duty in non-trafficable areas and heavy duty non rock in trafficable situations. Steps are to be 20mm hot dip galvanised steel.
label | 35f1767a-5d0f-53c3-a779-1e3bdee4e3bc |  | note | UCCL - V
label | acb3f87d-8781-50af-91f7-4f0349af7cac |  | note | Client - V
text | 5f744114-6f5b-5a2e-8882-f7b05b1a5419 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Materials - Aggregate
label | c43159e5-03fd-5d74-8621-d0104bf1dc27 |  | note | SPECIFICATION REFERENCE - TABG-JEC-0-000-GVC- SPC-0002 - Civil and Geotechnical Specification
label | 77de582c-f1ae-5d25-883e-bf1d68d39611 |  | note | TEST REQUIRED - Reports
label | 63949c1d-eaba-5ba6-9c6f-268c6ccacc0c |  | note | INSPECTION BY - UCCL
label | 4df7da5c-3aa7-5c19-987f-5f7156fdfb1d |  | note | TASK TIMING OR TASK FREQUENCY - All imported aggregates
label | f099cede-5126-5edc-8f6d-61a604a3d4b4 |  | note | ACCEPTANCE CRITERIA - Aggregates shall be in accordance with the drawing details. Bedding material shall be in accordance with AS/NZS 3725 or 7.10.3 parts A and B of the Civil Specification
label | 4b239f62-6038-5bd9-bb41-45194545cdcf |  | note | UCCL - V
label | 8c0c5cf3-84d7-5997-a366-1e9ba541ce82 |  | note | Client - V
text | 32f2f2b4-762e-5149-a924-53b81d404491 |  | textbox | Date Completed:
checkpoint-group |  |  | section | Stormwater Drainage - Construction
checkpoint-status |  |  | checkpoint | Setout of trench
label | 2e1b69ea-635e-578f-9f58-c68304d72c16 |  | note | SPECIFICATION REFERENCE - As per IFC Drawings and approved CAD files
label | d362e912-9350-52c1-bb40-028bf03edf30 |  | note | TEST REQUIRED - Surveying
label | 166b36dd-5d22-5da1-b4ba-ed3f0bc71dcd |  | note | INSPECTION BY - Surveyor
label | a4998d31-7400-5f64-a1d7-fe7171900ab3 |  | note | TASK TIMING OR TASK FREQUENCY - For set out of each trench line
label | a20aefaa-ad22-5a3d-98d6-42b092b187f1 |  | note | ACCEPTANCE CRITERIA - Horizontal Alignment to be within +/-100mm of trench position Vertical alignment to be within +/-50mm based on existing Ground levels. Separation to other in ground services shall be 300mm minimum
label | d7fb0e09-de01-545a-b997-3d949493d1a3 |  | note | UCCL - W
label | 73af10b3-2b39-5719-aeac-213d74b6016e |  | note | Client - Su
text | facdb9b7-627f-5067-9a02-ca89bd945cc1 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Excavation/ Subgrade
label | 5dab7cdb-2c4d-5062-a6c0-a560a6ce0cdb |  | note | SPECIFICATION REFERENCE - As per IFC Drawings
label | 96393ba6-2059-5d85-86b8-3ab7bae3fb37 |  | note | TEST REQUIRED - Scala tests
label | 9ec75445-6972-59cb-9f20-ac080f4b93ed |  | note | INSPECTION BY - UCCL
label | 960cf632-ae5b-514f-903c-8626be893385 |  | note | TASK TIMING OR TASK FREQUENCY - Each manhole excavated invert of drainage trench line
label | bfb6aef6-e4f0-5309-9a9e-bea68bb20628 |  | note | ACCEPTANCE CRITERIA - Excavation Depth Correct to allow for specified cover and drainage invert levels.
label | 686be4da-708f-5e1e-9c83-189ea3e51beb |  | note | Excavation stability to be monitored, trench walls in poor soil conditions may need to be excavated in steps, or be battered, to prevent collapse of trench wall materials.
label | 273f6b6c-796d-5ab4-9140-dbfa7ffc58f4 |  | note | Subgrade beneath pipes and manholes to be well compacted material
label | c2b3d804-c1dc-5980-91a6-32c80c108e63 |  | note | Scala testing undertaken at the base of pipe trenches (20m crs) and manhole positions, 3 blows/100mm
label | 962b9322-cc7f-5b6b-898e-18bc5918f5a0 |  | note | UCCL - V
label | 6cb030c5-2ae6-5d0e-8b19-571d2bd9d82c |  | note | Client - Su
text | 7e5081f0-0029-5b83-8d21-ad11fe59aecb |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Bedding, Surround and Filling Materials
label | af73e99d-85ea-5eb2-bdf2-0cc488943707 |  | note | SPECIFICATION REFERENCE - TABG-JEC-0-000-GCV-SPC-0002-B_-CIVIL AND GEOTECHNICAL PROJECT SP
label | 9809ef18-3bfe-5520-a2ca-6f96e66621ad |  | note | Section 7.10.3
label | fa03ae1c-3752-5d6f-847a-16befa223c31 |  | note | TEST REQUIRED - Refer Backfilling
label | f0980682-661c-53d1-808c-84610f1c03b4 |  | note | INSPECTION BY - UCCL
label | e464ea0a-85a1-5d03-b82f-7c04a28288a9 |  | note | TASK TIMING OR TASK FREQUENCY - Each drainage structure
label | 233cd9f9-2e55-5101-9af0-0fdde2e5a83c |  | note | ACCEPTANCE CRITERIA - A) Granular
label | 219b1926-e71d-5e2b-a953-36ced900e6f4 |  | note | • Clean site won pumice, gravel, crushed stone or a blend of these. Particle size from minimum 7mm to maximum 20
label | a18ce0ca-ad17-5716-b9ea-7a81ec66f802 |  | note | mm for pipes less than 525mm diameter;
label | 711286c4-0e7b-5de0-a9c1-f4ded479ef85 |  | note | • Approved GAP 40 for pipes 525mm diameter and greater;
label | d50bcd77-0680-5115-811b-a07af24345ff |  | note | • Approved GAP 65 for all drainage structure foundations. This includes manholes, cesspits
label | 52eff6b4-f8ee-5150-ae57-fc6317746708 |  | note | B) Aggregate Concrete
label | f2d46d6c-2c50-5835-a34f-77c803468aca |  | note | Bedding and surrounding concrete - 10 MPa.
label | 0a34c5b3-7a4a-50f4-92dd-2091387a27fc |  | note | UCCL - W
label | e1d1dbaf-4c57-5b92-a22c-8ac03e8d6a0b |  | note | Client - Su
text | 4450ebda-2493-5d22-ba2f-a076bdb983bf |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Laying of Pipes
label | 52a4305f-2b53-5039-9782-82ab5db3551e |  | note | SPECIFICATION REFERENCE - TABG-JEC-0-000-GCV-PLN-0003
label | 3b6dad76-48bd-507a-aa96-3a7f83a45061 |  | note | GENERAL NOTES
label | 54724cff-9222-5f4c-81b5-4095b67c5a85 |  | note | CIVIL AND STRUCTURAL DESIGN - SHEET 1
label | 475ac23b-c9b9-558b-8120-5c64a728fcb7 |  | note | TABG-JEC-0-000-GCV-SPC-0002-B_-CIVIL AND GEOTECHNICAL PROJECT SP
label | d8d90e8a-89f7-5f09-950e-c912d094c3a3 |  | note | Section 7.11 TABG-JEC-0-000-GCV-DET-0014
label | b800374a-d337-5215-8715-10020aadff70 |  | note | TEST REQUIRED - As-built Survey
label | 4e0c5e31-795e-56b1-a857-12dfde74c856 |  | note | INSPECTION BY - UCCL
label | c6d688a3-3806-5fa9-bae3-945ae5c00c3e |  | note | TASK TIMING OR TASK FREQUENCY - Each pipe installed
label | 7de38976-44c4-5ea3-814c-9aa695e4ba49 |  | note | ACCEPTANCE CRITERIA - Pipelines shall be within 100 mm of the position indicated on the plan unless otherwise directed by CEL
label | d168b12b-e6d8-58e4-8643-5e7b736349ec |  | note | Pipelines are to be laid to grade such that no pipe shall be more than 15 mm out of grade and adjoining pipes shall not vary in error by more than 5 mm from the adjacent pipe.
label | 710e8bc4-66df-5138-8eeb-409d69f0aeb3 |  | note | The gradient shall not be less than 0.5%
label | 93fd900f-6236-540d-b7e0-c20040cd3263 |  | note | The minimum embedment depth from the top of reinforced concrete pipe, which has not been capped, to the surface shall be 600 mm.
label | 05b911d0-9438-5d33-be9b-4da6440f5eb4 |  | note | UCCL - W
label | 40d1c73b-fc51-53ab-be98-172b94219af9 |  | note | Client - Su
text | f331cc88-d9d0-56f9-b371-f11eae18944b |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Joints
label | fb8b5c58-29ae-57ab-bd86-4d94bcd0a43c |  | note | SPECIFICATION REFERENCE - TABG-JEC-0-000-GCV-SPC-0002-B_-CIVIL AND GEOTECHNICAL PROJECT SP
label | 95ab5a58-4490-51b2-a87e-704618030fd1 |  | note | Section 7.10.5
label | e17e94dc-4e2a-5f44-98f3-6faeb98d241e |  | note | TEST REQUIRED - As-built Survey
label | b3c605dd-9837-58fe-bce0-f481ca30cd98 |  | note | INSPECTION BY - UCCL
label | 3ff39279-e3f5-5657-b38c-46c548146c6f |  | note | TASK TIMING OR TASK FREQUENCY - All pipe joints
label | f9418a55-6c68-511b-82d2-3d1a80a1e7d4 |  | note | ACCEPTANCE CRITERIA - All joints shall be of a type suitable for the pipe material used as follows:
label | 4681b3f7-f0b4-52a9-a991-2b99d779479c |  | note | • Flush joints shall be as per AS/NZS 4058;
label | 649096b7-656f-5461-aaeb-fe979842efde |  | note | • Elastomeric Joint Rings as per BS 7874 & BS EN 681.
label | 81512097-d14a-58b9-8e7d-ce641f9609a1 |  | note | UCCL - W
label | 23d0057c-46e5-565e-a220-7a8f9ed645f5 |  | note | Client - Su
text | 5aa271eb-418c-54d2-b1d9-c23941b027bf |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Concrete Capping
label | dbe44eb0-c5a2-5698-b510-118f182c84fb |  | note | SPECIFICATION REFERENCE - TABG-JEC-0-000-GCV-SPC-0002-B_-CIVIL AND GEOTECHNICAL PROJECT SP
label | e3e2f09d-f136-52c0-b9bc-fe1d4116da85 |  | note | Section 7.10.5
label | 8a7339dd-a8f0-54d3-9418-13b1cd97141b |  | note | TEST REQUIRED - As-built Survey
label | f1aa72d1-df77-56ea-9dbc-9c1d5e0dcc7a |  | note | INSPECTION BY - UCCL
label | ab78d2b5-006b-575e-95da-b026d9936a24 |  | note | TASK TIMING OR TASK FREQUENCY - Sections of drainage with less than 375mm cover
label | 60596c68-3c00-5b1b-a30b-a4e2f82bc344 |  | note | ACCEPTANCE CRITERIA - Concrete capping is required to all drains with less than 375mm cover
label | ea84c706-a5a9-5062-981a-f26a6b223902 |  | note | UCCL - W
label | 93edb48e-da2c-556a-8fce-e122f470a3ae |  | note | Client - Su
text | 186adbbb-2f6c-5f57-9e55-f9974af43778 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Manhole Installation
label | 3f02b1ef-7883-5f89-8f46-07e8c5471a31 |  | note | SPECIFICATION REFERENCE - TABG-JEC-0-000-GCV-SPC-0002-B_-CIVIL AND GEOTECHNICAL PROJECT SP
label | 68466511-53d6-5b29-88d2-1bdebbed8d94 |  | note | Section 7.11
label | a5e4ca42-b5b0-5af2-a2ba-a68deb737c7d |  | note | TABG-JEC-0-000-GCV-DET-0033
label | 6811240e-ca8b-557d-8946-901f180fe622 |  | note | TYPICAL DETAILS
label | 651b5db5-d766-5d34-b710-1177ab14c39a |  | note | MANHOLE
label | 8a557d2b-abd1-55cd-b99a-5022465b2afb |  | note | TEST REQUIRED - As-built Survey
label | 354fde10-ecb0-5824-8903-c2423fb6774f |  | note | INSPECTION BY - UCCL
label | 920e430b-890c-59a4-84a7-3c3190447d87 |  | note | TASK TIMING OR TASK FREQUENCY - Each Manhole Structure
label | c29bca0e-8bcd-58bf-97d2-6af3c1881c0b |  | note | ACCEPTANCE CRITERIA - Manholes and other drainage structures shall be within 150 mm of the position indicated on the plan unless otherwise directed by the Owner.
label | bf7257ef-778e-5735-960a-5a1d196be414 |  | note | Pipelines shall not extend into the internal wall of drainage structures more than 10 mm for pipes not entering at invert level
label | d1f4fb1c-0f64-54a8-bc53-1a5c55b123ae |  | note | Vertical Tolerance
label | eabdec6b-f02f-54f5-9a0f-966af0ebe93f |  | note | Manhole and other drainage structures cover levels shall be within 15 mm to adjacent surface for grass surfaces and 5 mm for concrete and seal surfaces.
label | d8025bc8-8093-528e-801b-be2ec7585655 |  | note | Manhole invert levels are to be within 15 mm of the design level.
label | ba090cbf-49ea-50ec-87b8-58a5c5dd13f4 |  | note | Round Process Drains
label | 7ed05da9-f07b-561b-b868-ef6faf509396 |  | note | 6mm sikaswell bead all round, min. 65mm cover
label | a1af7eac-2168-5d7e-b227-f438bade6ed7 |  | note | Bead at interface of pipe/ MH - 20mm x 20mm epoxy non shrink grout
label | c8de7c6f-e3a0-5e1b-b370-71035935d02f |  | note | UCCL - W
label | 9dc276f8-d04f-51f4-8559-e9808e0034e7 |  | note | Client - Su
text | 438845f3-5e66-5624-89fa-5acd3f1bc573 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Anchor Blocks
label | 8b0cc3fd-4119-57ed-9a1b-c8eefff3e585 |  | note | SPECIFICATION REFERENCE - TABG-JEC-0-000-GCV-SPC-0002-B_-CIVIL AND GEOTECHNICAL PROJECT SP
label | 587297c5-c3ef-5071-81c6-db1ba5f43457 |  | note | Section 7.9
label | ffa0d6eb-810d-59bf-91c8-226ae4aa4164 |  | note | TEST REQUIRED - N/A
label | 5845f131-7814-5227-a93f-5c80d8ab21be |  | note | TASK TIMING OR TASK FREQUENCY - Not exceeding 6m spacings
label | df0887ed-2ffc-5130-8afa-2cd4005f5c06 |  | note | ACCEPTANCE CRITERIA - Anchor blocks shall be installed at the pipe joins for drainage lines exceeding 20% in grade
label | a5e986e5-b651-5085-ba80-11335f937a7c |  | note | UCCL - W
label | f31f0a95-c4a8-5a74-a9f8-0b8557fc18ff |  | note | Client - Su
text | 59d856f9-c5d9-594b-a678-dc10616ba83b |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Compaction/Backfill
label | a6ae5967-e6c9-5b54-83f8-fcc17e6b250d |  | note | SPECIFICATION REFERENCE - TABG-JEC-0-000-GCV-SPC-0002-B_-CIVIL AND GEOTECHNICAL PROJECT SP Section 7.10.7
label | d1430571-73e3-591d-9a12-965c7e16fbd7 |  | note | TEST REQUIRED - Track rolling with excavator
label | 9ca6f5f1-6619-5b2f-a981-26b2651bd41f |  | note | INSPECTION BY - UCCL
label | 5b005371-6a12-5481-aa12-2f34ac7891be |  | note | TASK TIMING OR TASK FREQUENCY - All buried drainage elements
label | 581571f9-a4dd-5ca0-8d5d-b5548d06bf87 |  | note | ACCEPTANCE CRITERIA - Backfilling with site won material with small plate compactor in confined space and roll with 2T Trench Roller where applicable with max. of 300mm lift. Reinstate to match existing surface. 150mm zone above the pipes shall be approved selected cushion material free from large stones (clean pumice). Prior to final surfacing, all trenches that lay within the roadway shall test in accordance with the pavement ITP
label | 346a8570-9ce7-5697-a0d0-247dcb1b1945 |  | note | UCCL - W
label | 4231f166-9c35-52a7-8eab-b4276d14c9b1 |  | note | Client - Su
text | e98ebc2d-9de2-5b5b-990c-414999d2c023 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Inlets & Outlets including Aprons
label | 039203fc-9529-53f5-9551-dd96c0790373 |  | note | SPECIFICATION REFERENCE - TABG-JEC-0-000-GCV-DET-0011 and 0012 TYPICAL DETAILS DRAINAGE - SHEET 2
label | 59a68220-c645-5760-9fc7-a26eb1a4f0bf |  | note | TEST REQUIRED - N/A
label | 5c5f94f9-d0b8-5401-81a5-f47c2772f930 |  | note | INSPECTION BY - UCCL
label | 2b8f7412-2430-5af5-9c61-efc8ef856595 |  | note | TASK TIMING OR TASK FREQUENCY - Each inlet, outlet apron
label | fe054dfd-f11f-5c14-9168-4fbb926dc1dc |  | note | ACCEPTANCE CRITERIA - Concrete headwall and apron details and reinforcement to be provided in specific drawings which accommodate the specific site situations for each culvert
label | 7bee799e-25dc-5b89-b1df-5236ae66a273 |  | note | UCCL - W
label | ddf0f439-1dc2-58ce-b33f-30b80b8173b8 |  | note | Client - Su
text | 21a76f70-70bf-5ae7-adc3-f5c825c34deb |  | textbox | Date Completed:
checkpoint-group |  |  | section | Swale Drains/ Riprap Drains
checkpoint-status |  |  | checkpoint | Swale Drains, Lined Drains
label | df4a9cfb-a1c3-5466-bc0d-a2115a276bcb |  | note | SPECIFICATION REFERENCE - TABG-JEC-0-000-GCV-DET-0013
label | ab847951-b65a-5e45-906e-fd38dbb59b82 |  | note | TEST REQUIRED - N/A
label | ff9f5a38-d9e3-5a32-b3be-511af3fe1367 |  | note | INSPECTION BY - UCCL
label | d95eacf2-5945-561f-84fc-32227a724c57 |  | note | TASK TIMING OR TASK FREQUENCY - Unlined drainage channel longitudinal grade < 10% Cemented rock lined drainage channel longitudinal grade ≥ 10%
label | e1c4bbda-754c-5118-8446-107bba500330 |  | note | ACCEPTANCE CRITERIA - Lined & unlined drains to be installed in locations and detailed as specified in IFC Drawings.
label | d7c243cd-837b-567c-bd44-b9b35729e5c6 |  | note | UCCL - W
label | 4fa7bba8-1c2c-5044-b271-9fec93d33e34 |  | note | Client - Su
text | b35bc2da-18e8-5690-a180-ee2af4ff85aa |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Subsoil drains
label | 26391132-b240-558f-8f5e-959a346c7150 |  | note | SPECIFICATION REFERENCE - TABG-JEC-0-000-GCV-DET-0013
label | fee8f652-7740-5f0a-bf90-582c36046018 |  | note | TEST REQUIRED - N/A
label | 408d3f16-59ec-5a41-b0eb-4d1f2adefad4 |  | note | INSPECTION BY - UCCL
label | 3f8cbca9-420c-5a4e-bd7f-96bd2b926272 |  | note | TASK TIMING OR TASK FREQUENCY - All subsoil drains
label | 00b4f000-ce9f-5a9f-abf2-e2f5d05404aa |  | note | ACCEPTANCE CRITERIA - Subsoil drains to be installed in locations and sized as specified in IFC Drawings.
label | 34e1921e-f5a6-5ba8-b6b9-526bb1ff4238 |  | note | UCCL - W
label | 87707a3f-074e-5c62-8725-f5f8fbd2b6ed |  | note | Client - Su
text | eecf4639-40d3-5ede-84ad-b5e7b86172a4 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Refer Pavement ITP for V dish & channel & pipe crossing beneath roads
checkpoint-group |  |  | section | Post Construction
checkpoint-status |  |  | checkpoint | As Built & Final Design Documentation
label | 6c233de7-f5fa-5612-aede-1e7e6afd3209 |  | note | TEST REQUIRED - Surveying
label | f0c6e536-e3c7-562b-8035-583f4fc26574 |  | note | INSPECTION BY - UCCL
label | 5e528528-4909-51ab-b866-2548cd5c53fe |  | note | TASK TIMING OR TASK FREQUENCY - For each Trench line
label | a5d3b5c5-9202-5ec5-97ac-364a7b697d59 |  | note | ACCEPTANCE CRITERIA - Confirmation From Engineer on as built records & redline markups
label | 3b8f9335-0266-5060-beaa-8d52b90b8260 |  | note | UCCL - H
label | fa0fec35-dbb0-5c73-afab-10ef5613e6b9 |  | note | Client - R
text | cca2a65f-3bc5-5c0e-8fd6-023e3403d289 |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Completion Inspection inc. Construction Defects Report
label | 4a78183c-321b-54b9-b6ec-468be138c77b |  | note | TEST REQUIRED - Completion inspection on each Line by CEL
label | bd5144e2-6f73-5120-90a2-c8aba44084c0 |  | note | INSPECTION BY - CEL/ UCCL
label | 9a6611d6-570d-5109-a6c6-80990cce1876 |  | note | TASK TIMING OR TASK FREQUENCY - For each DuctLine
label | 8688c511-54e9-53e5-868a-7e0694834fe3 |  | note | ACCEPTANCE CRITERIA - Provided a completed construction defect report that that details any remedial measures taken, & snag lists closed out
label | c5d1f329-aad2-5fd5-a0b1-bb8214a4558a |  | note | UCCL - H
label | aa9ad83a-320d-5d94-a87f-10ff90576e37 |  | note | Client - R
text | 96e1d608-58d5-5b51-9c30-1088861d6f62 |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checklist-sectioned |  |  | checklist | ITP - Underground Services |  |  |  |  | Yes | ITP - Underground Services | 86da54b3-c3f3-4a60-9502-16c0e9e84520
checkpoint-group |  |  | section | Preliminary
checkpoint-status |  |  | checkpoint | Material Supplied by Client
label | 6fc0db55-967f-515f-93d8-cc8f1c7cf626 |  | note | Specification Reference - IFC Drawings / AS/NZS2053
label | ce50ee0b-31d8-581c-b0eb-a9be82afd8f3 |  | note | Test Required - Visual Inspection
label | d5b717d6-1c84-55c4-90d5-10cb9727ff51 |  | note | Inspection By - UCCL/ Engineer
label | f5048b00-6279-554b-be3a-e19fb43f8500 |  | note | Task Timing Or Task Frequency - For all Material Delivered to site
label | 33bbc28e-b5b1-50c0-8efe-c33f5a09c51c |  | note | Acceptance Criteria - UCCL to do visual inspection and confirm that material supplied by client meets required specifications. Certificate from manufacturer that materials comply with specification/Drawings
label | 631c9467-aac0-53a9-aaff-aa8096839ca1 |  | note | UCCL - V
text | 8e628693-545e-52c9-abe3-89d95b67570f |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Material Supplied by UCCL
label | 23158694-fd85-5673-871c-4a3b3c8a63a5 |  | note | Specification Reference - IFC Drawings / AS/NZS2054
label | 8f7ed594-6954-59fa-ba66-affad1102c87 |  | note | Test Required - Visual Inspection
label | 465c11d6-1304-5788-9c96-5b4d02f01ba2 |  | note | Inspection By - UCCL/ Engineer
label | 87b51a10-aba9-5bc5-ac2f-d554c91416a1 |  | note | Task Timing Or Task Frequency - For all Material Delivered to site
label | 72bb4430-9088-5304-a51b-dc94fb3d246a |  | note | Acceptance Criteria - Materials to comply with IFC Drawings. Product data sheet to be provided for CEL's Review
label | dcd17208-a4d3-5559-836f-8be3917cacef |  | note | UCCL - H
text | b664528c-56a8-5d57-bc7c-03fccfcc23ce |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-group |  |  | section | Services
checkpoint-status |  |  | checkpoint | Setout of trench
label | aee96b34-6a7f-5f72-9bdd-81a0d20baf46 |  | note | Specification Reference - As per IFC Drawings and approved CAD files
label | c8c5b13d-dfb4-53ba-afed-d679f818f94d |  | note | Test Required - Surveying
label | 71b281e5-e054-5e50-9985-00d8c004bbda |  | note | Inspection By - Surveyor
label | 0bb1c0fe-404d-5ae7-9ad7-23bd8d4ed03b |  | note | Task Timing Or Task Frequency - For set out of each trench line.
label | 337b286d-fe93-53d1-866a-e0958045ca70 |  | note | Acceptance Criteria - Horizontal Alignment to be within +/-100mm of trench position Vertical alignment to be within +/-50mm based on existing Ground levels
label | bda80f03-7997-5bdf-b715-8817710c3533 |  | note | UCCL - W
text | 3e1f7133-5dab-5148-ada4-4a57983d6d06 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Excavation
label | a93730e2-d918-56fb-beb9-238c836e2265 |  | note | Specification Reference - As per IFC Drawings and approved CAD files
label | b46acbba-54dd-5b66-a077-e333e0f225d6 |  | note | Test Required - Visual Check/Photos
label | f53b265a-df9c-52eb-9cb0-6d071aae0632 |  | note | Inspection By - UCCL
label | 1a82cdbf-8ed1-57ac-8efb-df34d9dc6c5e |  | note | Task Timing Or Task Frequency - UG-1
label | 0d34529d-156b-52ff-9087-853184ee4248 |  | note | Acceptance Criteria - Excavation Depth Correct to allow for specified cover and concrete capping. No testing required on subgrade. Visual check by CEL.Trench floor shall be free of Water and/or Sludge prior to placement thermal Backfill.
label | f8bb3ac4-9bb8-5dd3-b2e9-a5b067b83bef |  | note | UCCL - W
text | f4e27258-6ac5-5e44-baf0-58a782bd74dd |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Excavation
label | c8fdc4f2-a9fc-5ac6-8890-c79ccada702a |  | note | Specification Reference - As per IFC Drawings and approved CAD files
label | ec5181e4-57b4-520f-9b5a-cd8f6f6f8981 |  | note | Test Required - Visual Check/Photos
label | 98c02f67-940a-5ec1-9169-c6cba158b1b3 |  | note | Inspection By - UCCL
label | 1a891d6b-8b71-54cb-817c-4b1498fa3b5d |  | note | Task Timing Or Task Frequency - UG-2
label | a55f42cf-7cc5-56b4-9f63-d9dd8afffa46 |  | note | Acceptance Criteria - Excavation Depth Correct to allow for specified cover and concrete capping. No testing required on subgrade. Visual check by CEL.Trench floor shall be free of Water and/or Sludge prior to placement thermal Backfill.
label | 9aff54ff-306c-5ae5-a792-0ad1b5239f0d |  | note | UCCL - W
text | 19374ec0-21ae-5e38-aefd-c79bae3cc7a0 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Excavation
label | f9f1d935-f956-59c1-8ed0-a4d1b9ac956e |  | note | Specification Reference - As per IFC Drawings and approved CAD files
label | e9ccea34-d8c2-5c05-8444-6d4f6712a7a3 |  | note | Test Required - Visual Check/Photos
label | 54e95f99-dcc5-5ade-89fc-a0489b2ca224 |  | note | Inspection By - UCCL
label | 6c673771-404b-5044-b7f6-b5e11116a770 |  | note | Task Timing Or Task Frequency - UG-3
label | e92b53d2-d11e-531c-a48a-c193e9cd51cd |  | note | Acceptance Criteria - Excavation Depth Correct to allow for specified cover and concrete capping. No testing required on subgrade. Visual check by CEL.Trench floor shall be free of Water and/or Sludge prior to placement thermal Backfill.
label | 436c957f-b036-513b-bba3-3926c76e5e4d |  | note | UCCL - W
text | 70d64003-2969-591f-9100-81db0ec842d2 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Excavation
label | 860da003-ac62-59be-bfc5-3b802a70f6bc |  | note | Specification Reference - As per IFC Drawings and approved CAD files
label | 4d0475ee-cd51-5328-892f-f509850802c4 |  | note | Test Required - Visual Check/Photos
label | 11a6040f-6f75-5b0f-862e-972f7eb0bd3c |  | note | Inspection By - UCCL
label | c834ad8c-febe-5d97-8958-d0b725b05eb8 |  | note | Task Timing Or Task Frequency - UG-4A
label | 8ea6437b-c495-53de-884b-3f9478536fba |  | note | Acceptance Criteria - Excavation Depth Correct to allow for specified cover and concrete capping. No testing required on subgrade. Visual check by CEL.Trench floor shall be free of Water and/or Sludge prior to placement thermal Backfill.
label | ba1fbdc2-deaa-5e8a-9869-4e247b421e81 |  | note | UCCL - W
text | 896dbcf6-4835-59ff-84a3-8b9ce9ed6756 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Excavation
label | 06b9787e-6a16-5ed2-8a7f-9850b64281e4 |  | note | Specification Reference - As per IFC Drawings and approved CAD files
label | a1e17377-3411-5a32-ad7c-7edbd2bfb591 |  | note | Test Required - Visual Check/Photos
label | 3c17f8fb-02c8-513c-8eff-08ebdd0ff53e |  | note | Inspection By - UCCL
label | a9a180b8-7519-58a3-b8b1-ca486aa509ef |  | note | Task Timing Or Task Frequency - UG-4B
label | efd5f914-e250-5892-a06a-742a82d40910 |  | note | Acceptance Criteria - Excavation Depth Correct to allow for specified cover and concrete capping. No testing required on subgrade. Visual check by CEL.Trench floor shall be free of Water and/or Sludge prior to placement thermal Backfill.
label | e4c6ea78-3d83-5031-8dc9-a2b4f87da415 |  | note | UCCL - W
text | b016ab2f-bb4f-5530-9396-25dc26da92c2 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Excavation
label | e04bf4f7-0f08-53a6-a2f7-9f437fd69a98 |  | note | Specification Reference - As per IFC Drawings and approved CAD files
label | 3677f0c2-9073-57ed-9d9b-d790b10bd49a |  | note | Test Required - Visual Check/Photos
label | b06f249b-dc49-56ae-935a-bf80301f7e74 |  | note | Inspection By - UCCL
label | d8e44969-d13c-52bf-a290-902c82040c6c |  | note | Task Timing Or Task Frequency - UG-5
label | a14d9f72-89d0-52b6-970c-78552af5b689 |  | note | Acceptance Criteria - Excavation Depth Correct to allow for specified cover and concrete capping. No testing required on subgrade. Visual check by CEL.Trench floor shall be free of Water and/or Sludge prior to placement thermal Backfill.
label | a84f932e-92b5-5d30-88c2-ec240d7c99ff |  | note | UCCL - W
text | 2b7d43b0-c1ca-5230-bb46-b386c0535f8e |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Excavation
label | 4315e7d6-ff58-5069-80f3-37e53007381c |  | note | Specification Reference - As per IFC Drawings and approved CAD files
label | 5d1485f1-a039-594a-a150-9664f357eabb |  | note | Test Required - Visual Check/Photos
label | 1073d9ae-9434-5b08-8d73-73785b4ce659 |  | note | Inspection By - UCCL
label | a5104af1-af46-59d2-87a1-180a6bef474d |  | note | Task Timing Or Task Frequency - UG-6
label | 5070f714-0b09-513e-89f3-64040e2338d7 |  | note | Acceptance Criteria - Excavation Depth Correct to allow for specified cover and concrete capping. No testing required on subgrade. Visual check by CEL.Trench floor shall be free of Water and/or Sludge prior to placement thermal Backfill.
label | 3d1e7a88-586f-5e21-9b22-9f3001f5a72f |  | note | UCCL - W
text | 57c4219f-ebdc-5b17-afe9-9afadfccb1dd |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Excavation
label | a9a0a3a5-6ebe-581e-a17a-15a62007769c |  | note | Specification Reference - As per IFC Drawings and approved CAD files
label | 5a00c5ed-5d05-5692-a428-fbdc25346b72 |  | note | Test Required - Visual Check/Photos
label | ad8fd954-3fe7-5a52-a35b-cb332b180eef |  | note | Inspection By - UCCL
label | d9702742-d409-5365-95dc-e2c14bf923dc |  | note | Task Timing Or Task Frequency - UG-7A
label | 99692b1f-01a4-5beb-803a-3564125d1f43 |  | note | Acceptance Criteria - Excavation Depth Correct to allow for specified cover and concrete capping. No testing required on subgrade. Visual check by CEL.Trench floor shall be free of Water and/or Sludge prior to placement thermal Backfill.
label | 17e3078b-eda8-5ae8-9105-427dcf56ceda |  | note | UCCL - W
text | 67b4ee4e-f1c8-5065-bb49-e389a7ecb3a0 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Excavation
label | 3de012bf-93ea-52d6-8df0-f58341443353 |  | note | Specification Reference - As per IFC Drawings and approved CAD files
label | 4a5aca62-64cf-5ad6-b75a-0dcb292b6e83 |  | note | Test Required - Visual Check/Photos
label | 9be28448-0f04-523c-86cc-1cd112dc0a7c |  | note | Inspection By - UCCL
label | 6c45068a-fdca-5de3-b03d-e6411d2b7bf3 |  | note | Task Timing Or Task Frequency - UG-7B
label | ee5ccc76-a8ce-5d00-a7d6-3dc94feaabc8 |  | note | Acceptance Criteria - Excavation Depth Correct to allow for specified cover and concrete capping. No testing required on subgrade. Visual check by CEL.Trench floor shall be free of Water and/or Sludge prior to placement thermal Backfill.
label | 5e354b7e-0d4a-590a-8347-7954a2d5eb61 |  | note | UCCL - W
text | c3d7f4a9-b641-5c76-a633-dded8e0c9866 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Installation of Trench Drain Embedment Zone
label | 49725615-f1ca-5f28-9a5f-c7468bad0a24 |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542,
label | 41470eeb-18dc-549a-a92d-2158e63fc54b |  | note | Test Required - Visual Check/Photos
label | cbfeac89-2778-5c24-a0f3-5e5e7ea64a50 |  | note | Inspection By - UCCL
label | ddaf4b2c-e3de-5821-9455-e51c02a4de2d |  | note | Task Timing Or Task Frequency - UG-1
label | 683f59b2-70eb-53ea-8629-72a59e608cc2 |  | note | Acceptance Criteria - Trench Drain Embedment zone to be Ø110 Corrugated Novaflo with Thermal backfilling. Minimum distance between top of Trench Drain Pipe and service duct invert to be 100mm (Min. 220mm from subgrade to duct inlet)
label | dbf2129c-5e28-5b6f-a606-b99ba845bcbb |  | note | UCCL - W
text | 0c5047b8-7e23-5a69-b07f-5101fab56bba |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Installation of Trench Drain Embedment Zone
label | 832ea642-daae-5664-bb0f-9dc25a58f143 |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542,
label | 204327fa-0373-5c3b-823d-e7ec46774f13 |  | note | Test Required - Visual Check/Photos
label | 36a8739e-791a-57a0-a1a4-0cbfd61cb590 |  | note | Inspection By - UCCL
label | 8bef481e-c2cd-57ff-8a90-1bf6f108874b |  | note | Task Timing Or Task Frequency - UG-2
label | a8b855a4-f5a3-5691-919a-eee4fd4e4839 |  | note | Acceptance Criteria - Trench Drain Embedment zone to be Ø110 Corrugated Novaflo with Thermal backfilling. Minimum distance between top of Trench Drain Pipe and service duct invert to be 100mm (Min. 220mm from subgrade to duct inlet)
label | 28d1dc09-a1fb-5a44-bbca-c06dfb704099 |  | note | UCCL - W
text | 8505ed7f-8de4-5408-acbb-2f862cfdf61f |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Installation of Trench Drain Embedment Zone
label | e0dfcf9e-07c3-5a06-b74e-94776f9eaebf |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542,
label | 1c4307e0-4d95-5918-a4f6-06b4164bacd6 |  | note | Test Required - Visual Check/Photos
label | b01877d3-3145-5c7a-a2dd-f04231b03626 |  | note | Inspection By - UCCL
label | 4b15d4b8-bdb5-5745-8819-adfb0e4e828f |  | note | Task Timing Or Task Frequency - UG-3
label | 371ee1fc-f823-5b12-9689-f16b517084ce |  | note | Acceptance Criteria - Trench Drain Embedment zone to be Ø110 Corrugated Novaflo with Thermal backfilling. Minimum distance between top of Trench Drain Pipe and service duct invert to be 100mm (Min. 220mm from subgrade to duct inlet)
label | f2255c6a-96c0-5fba-95fc-3e44b66d4922 |  | note | UCCL - W
text | ec32672a-e4cb-572d-976e-5e53e615afab |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Installation of Trench Drain Embedment Zone
label | 1ee2b0c4-2ddc-53c4-a648-0238aaf519d5 |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542,
label | 06d558fa-bef1-55f3-8623-462e9bb21aaf |  | note | Test Required - Visual Check/Photos
label | 11517ea0-8917-594c-a481-099bf8e90c44 |  | note | Inspection By - UCCL
label | 062e9398-6c37-5c93-82e7-f212daac341d |  | note | Task Timing Or Task Frequency - UG-4A
label | cede03aa-00ea-5f64-9178-54739dceef74 |  | note | Acceptance Criteria - Trench Drain Embedment zone to be Ø110 Corrugated Novaflo with Thermal backfilling. Minimum distance between top of Trench Drain Pipe and service duct invert to be 100mm (Min. 220mm from subgrade to duct inlet)
label | c2e6cec9-9326-5b26-9983-4abc5bcc31c2 |  | note | UCCL - W
text | 67c3160f-04a4-5388-a4c7-b5335eba8756 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Installation of Trench Drain Embedment Zone
label | f90550c8-f51e-511b-9a90-3a7a2c637c42 |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542,
label | 79737b0c-286e-5720-b335-8af290b509a1 |  | note | Test Required - Visual Check/Photos
label | 60fd98e8-edbd-5058-a7d2-42b0a5b74f65 |  | note | Inspection By - UCCL
label | 448896e8-8b79-59bb-afac-76e86ac51f64 |  | note | Task Timing Or Task Frequency - UG-4B
label | dcfd5662-461e-5df0-b9de-281bf136fb47 |  | note | Acceptance Criteria - Trench Drain Embedment zone to be Ø110 Corrugated Novaflo with Thermal backfilling. Minimum distance between top of Trench Drain Pipe and service duct invert to be 100mm (Min. 220mm from subgrade to duct inlet)
label | 4f0daeed-5154-5e8e-9363-388162313706 |  | note | UCCL - W
text | ced4da9b-83fd-5ae6-a4c7-93e3cd9a92b8 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Installation of Trench Drain Embedment Zone
label | 4a78b3b7-c668-5c01-b495-b376025f7426 |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542,
label | 0be99e7c-ddda-5927-a93b-74e1c8d5e12d |  | note | Test Required - Visual Check/Photos
label | d845870c-4e5a-5bd1-9f76-c4b0c780b3af |  | note | Inspection By - UCCL
label | c906521d-d354-531c-a4f6-54b9044fde53 |  | note | Task Timing Or Task Frequency - UG-5
label | 00eb17c7-c04d-58d6-8c01-3316ceffd810 |  | note | Acceptance Criteria - Trench Drain Embedment zone to be Ø110 Corrugated Novaflo with Thermal backfilling. Minimum distance between top of Trench Drain Pipe and service duct invert to be 100mm (Min. 220mm from subgrade to duct inlet)
label | 552f22b8-3f56-5e75-8818-db4eb17210e1 |  | note | UCCL - W
text | 59816765-8b43-5add-82b6-80efa919ff8a |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Installation of Trench Drain Embedment Zone
label | 833fa31a-707e-5d08-a921-b5482b47ac8d |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542,
label | e0d67c22-482d-5b21-acc8-549d7c4f69ee |  | note | Test Required - Visual Check/Photos
label | 671ebcb1-48c7-59f5-a9a9-7d6179faa674 |  | note | Inspection By - UCCL
label | 0c94e404-806d-5a27-8ef6-d3858df45a5c |  | note | Task Timing Or Task Frequency - UG-6
label | 11931126-b59c-58bd-b4aa-e128734948d5 |  | note | Acceptance Criteria - Trench Drain Embedment zone to be Ø110 Corrugated Novaflo with Thermal backfilling. Minimum distance between top of Trench Drain Pipe and service duct invert to be 100mm (Min. 220mm from subgrade to duct inlet)
label | 26116aa8-add2-5c33-a1c1-7bb7e93b08d5 |  | note | UCCL - W
text | f58fa2c4-bd15-5de2-ac89-91b1381b8543 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Installation of Trench Drain Embedment Zone
label | 6858bbf2-6f3d-57e6-a616-aa961f7ea2a5 |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542,
label | e136e14e-bff3-517c-8494-719e4f090c02 |  | note | Test Required - Visual Check/Photos
label | f1a2fc6f-c7bd-5dbf-b913-ef79bcac7e8d |  | note | Inspection By - UCCL
label | f3b9126e-bc51-5ca5-a309-8022a2a78e55 |  | note | Task Timing Or Task Frequency - UG-7-A
label | 1bc94601-a18c-5270-8097-6d5b6d0d45fd |  | note | Acceptance Criteria - Trench Drain Embedment zone to be Ø110 Corrugated Novaflo with Thermal backfilling. Minimum distance between top of Trench Drain Pipe and service duct invert to be 100mm (Min. 220mm from subgrade to duct inlet)
label | fa5d174d-ec7a-58c0-a1cd-818efe665321 |  | note | UCCL - W
text | eecc22bf-7fc9-55b0-8b3e-607f43115605 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Installation of Trench Drain Embedment Zone
label | 85cb187d-a148-592e-9924-7534a1778ac0 |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542,
label | a8b1d1cc-657f-510c-aab9-ee72b0bb7696 |  | note | Test Required - Visual Check/Photos
label | c174582e-3989-5b65-b798-3aa1b75c31d2 |  | note | Inspection By - UCCL
label | 1655356d-7e9d-5562-936c-7a25ebdd3c4f |  | note | Task Timing Or Task Frequency - UG-7-B
label | 86adc118-2cc8-5504-8c8a-92280a366b46 |  | note | Acceptance Criteria - Trench Drain Embedment zone to be Ø110 Corrugated Novaflo with Thermal backfilling. Minimum distance between top of Trench Drain Pipe and service duct invert to be 100mm (Min. 220mm from subgrade to duct inlet)
label | f98bdf9f-b3b0-5620-8668-01031535dcfa |  | note | UCCL - W
text | 4a78ca24-0ade-5bdb-8748-a229ed612e48 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Installation Of Ducts / Thermal Backfill
label | 2466de64-6fe9-5fe1-b8ef-222e39d4eb66 |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | ebd77dbb-c7e5-5611-96af-c5fd0ee92d9b |  | note | Test Required - Visual Check/Photos
label | 283622e0-1287-5ad1-b283-4cbff90624d7 |  | note | Inspection By - UCCL
label | 88ef35e3-9bfc-5ef6-b70a-ad9e6cad972e |  | note | Task Timing Or Task Frequency - UG-1
label | b194d68f-e250-5b29-b6ca-0066d9096cd5 |  | note | Acceptance Criteria - 2X 100mm Heavy Duty Orange uPVC Ducts, Backfilled with Thermal backfill min. 100mm above top layer of ducts. MAG SLAB to be installed on Top of thermal backfill layer to cover entire width of cable trench. Install Tracer wire on each side of trench. Compaction test to be done with Scala at every 20m Interval for 3blows/100mm
label | e82e9123-21c5-5ed0-897e-f713e7323d6f |  | note | UCCL - H
text | af921223-6be5-580a-96e5-afda7956d38b |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Installation Of Ducts / Thermal Backfill
label | 859dc5e8-a0b2-5fa7-a9d9-46b2dc6865e1 |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | 4de11fcf-513b-5e69-828c-d7323c081248 |  | note | Test Required - Installation Of Ducts / Thermal Backfill
label | 734796c2-1469-5874-be6f-02d84e695ce9 |  | note | Inspection By - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | 4352ac18-4f18-50ca-8090-5eea4fde450f |  | note | Task Timing Or Task Frequency - UG-1
label | f0992a96-482e-5f9b-8a00-5e0065251926 |  | note | Acceptance Criteria - 2X 100mm Heavy Duty Orange uPVC Ducts, Backfilled with Thermal backfill min. 100mm above top layer of ducts. MAG SLAB to be installed on Top of thermal backfill layer to cover entire width of cable trench. Install Tracer wire on each side of trench. Compaction test to be done with Scala at every 20m Interval for 3blows/100mm
label | 886867d6-1a6a-528a-8908-9c905fb4b997 |  | note | UCCL - H
text | d2a304d3-9c3e-543a-a992-5840bf169caf |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Installation Of Ducts / Thermal Backfill
label | 58fb2537-6e4d-50d8-a32a-cf5940386427 |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | 0e1579c2-91c1-5fd4-a362-65a31470f531 |  | note | Test Required - Installation Of Ducts / Thermal Backfill
label | 34b43035-70ac-573b-8e59-29350a6c0a44 |  | note | Inspection By - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | 7c22d9dc-a955-5a7f-bac8-3c9f265a3c13 |  | note | Task Timing Or Task Frequency - UG-2
label | e98de893-0c18-51ec-8572-08c2e3bea69b |  | note | Acceptance Criteria - 6X 100mm Heavy Duty Orange uPVC Ducts, Backfilled with Thermal backfill min. 100mm above top layer of ducts. MAG SLAB to be installed on Top of thermal backfill layer to cover entire width of cable trench. Install Tracer wire on each side of trench. Compaction test to be done with Scala at every 20m Interval for 3blows/100mm
label | 06078a1d-d509-5709-8b77-696f28245c02 |  | note | UCCL - H
text | e59e8392-5875-5e2c-a076-688a1fa3e636 |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Installation Of Ducts / Thermal Backfill
label | 524fe1f8-39f7-5695-b832-a3b5f85d2c9d |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | 8ab6ac24-4752-5203-88a1-61ef78993ac3 |  | note | Test Required - Installation Of Ducts / Thermal Backfill
label | f50b8754-7739-54e1-af4b-3717ac55814a |  | note | Inspection By - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | 54e52e1d-0ccd-5348-b357-f5050deec903 |  | note | Task Timing Or Task Frequency - UG-3
label | 0edef31e-fbdc-568f-b122-2058bf3faf2e |  | note | Acceptance Criteria - 4X 100mm Heavy Duty Orange uPVC Ducts, Backfilled with Thermal backfill min. 100mm above top layer of ducts. MAG SLAB to be installed on Top of thermal backfill layer to cover entire width of cable trench. Install Tracer wire on each side of trench. Compaction test to be done with Scala at every 20m Interval for 3blows/100mm
label | 6e7039c4-d1da-5257-bb08-934cfa234741 |  | note | UCCL - H
text | ef97709d-6b3d-5558-8354-c2bf2d7840b4 |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Installation Of Ducts / Thermal Backfill
label | d075fecb-8a80-556d-9482-101e8670466e |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | 8bfb816b-0a89-50e1-9071-d24dfe5ac0c3 |  | note | Test Required - Installation Of Ducts / Thermal Backfill
label | 00d025e3-10df-5f7d-ab6d-e874cfb5427d |  | note | Inspection By - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | dd07563b-c2aa-52b3-8905-db6ded64e0df |  | note | Task Timing Or Task Frequency - UG-4A
label | 71294c10-6cac-539c-8e8a-5b0dd4bb55fc |  | note | Acceptance Criteria - 2X 100mm, 6X150mm Heavy Duty Orange uPVC Ducts, Backfilled with Thermal backfill min. 100mm above top layer of ducts. MAG SLAB to be installed on Top of thermal backfill layer to cover entire width of cable trench. Install Tracer wire on each side of trench. Compaction test to be done with Scala at every 20m Interval for 3blows/100mm
label | ce0e0f0a-63f4-58bf-a795-15b4b3044d76 |  | note | UCCL - H
text | d1f6134d-3fa1-5222-9a8c-b4bed046a2af |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Installation Of Ducts / Thermal Backfill
label | 7fe00975-b59f-5843-b919-777eaad37b9d |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | a6795025-a0d5-50f3-9d4c-a327fd5c7b51 |  | note | Test Required - Installation Of Ducts / Thermal Backfill
label | 5699797c-2434-5d2b-a195-0ebce70d77b9 |  | note | Inspection By - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | ef8ba126-9cc9-52c1-8b83-a78d3f7892bd |  | note | Task Timing Or Task Frequency - UG-4B
label | dce7bd71-1ba4-5be4-bfd3-572574fc1987 |  | note | Acceptance Criteria - 3X 150mm Heavy Duty Orange uPVC Ducts, Backfilled with Thermal backfill min. 100mm above top layer of ducts. MAG SLAB to be installed on Top of thermal backfill layer to cover entire width of cable trench. Install Tracer wire on each side of trench. Compaction test to be done with Scala at every 20m Interval for 3blows/100mm
label | 1c685255-6871-5e8b-ac03-a1048cc6cb2d |  | note | UCCL - H
text | 15fd0e48-808a-5719-971b-7d50236774f4 |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Installation Of Ducts / Thermal Backfill
label | 2fb8060d-e2c4-551e-9361-4bd92f7201df |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | 6ab11205-5123-59e8-809b-d75b053e4067 |  | note | Test Required - Installation Of Ducts / Thermal Backfill
label | c6f704b2-aaa0-5c22-8752-165de92a083f |  | note | Inspection By - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | e96a01b8-56ed-5745-9151-cbcc94ca7a7a |  | note | Task Timing Or Task Frequency - UG-5
label | e91dd8de-b3bd-5668-9483-2404b3a35ad8 |  | note | Acceptance Criteria - 8X 150mm Heavy Duty Orange uPVC Ducts, Backfilled with Thermal backfill min. 100mm above top layer of ducts. MAG SLAB to be installed on Top of thermal backfill layer to cover entire width of cable trench. Install Tracer wire on each side of trench. Compaction test to be done with Scala at every 20m Interval for 3blows/100mm
label | 3b4f244f-3f64-5eeb-8eec-eeea86bbc5d8 |  | note | UCCL - H
text | d82492bc-dd54-5758-9742-df19251e71fe |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Installation Of Ducts / Thermal Backfill
label | 61cf028b-0caa-5614-8a70-5fce5b73840f |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | 686e58cb-3589-59fa-be36-cfe5c66e5825 |  | note | Test Required - Installation Of Ducts / Thermal Backfill
label | 034481f4-c428-5f78-b9ff-3fd0bbae6de2 |  | note | Inspection By - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | 75d6e115-b2d3-5fd9-838c-6ab3b1fb283b |  | note | Task Timing Or Task Frequency - UG-6
label | e55fc945-2f2c-5aff-8415-1de032a0c04e |  | note | Acceptance Criteria - 8X 100mm Heavy Duty Orange uPVC Ducts, Backfilled with Thermal backfill min. 100mm above top layer of ducts. MAG SLAB to be installed on Top of thermal backfill layer to cover entire width of cable trench. Install Tracer wire on each side of trench. Compaction test to be done with Scala at every 20m Interval for 3blows/100mm
label | 31477790-44a3-5bd9-a3b9-cdb7ae6ed86c |  | note | UCCL - H
text | fea4e64f-a31a-51d6-83e7-60252643ac21 |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Installation Of Ducts / Thermal Backfill
label | 740c7e0c-ae49-55fa-97fe-64d20bc41cac |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | 8b5980f0-5a93-5d38-ac0d-cbed500d2f01 |  | note | Test Required - Installation Of Ducts / Thermal Backfill
label | c9d3959b-1aa4-547b-b1bc-82f3da60bae0 |  | note | Inspection By - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | 86d8565a-1a19-51ee-8b22-2071b93648b5 |  | note | Task Timing Or Task Frequency - UG-7A
label | 0ef36659-a3d8-57c5-b443-f6f0f721791b |  | note | Acceptance Criteria - 2X 100mm, 9X150mm Heavy Duty Orange uPVC Ducts, Backfilled with Thermal backfill min. 100mm above top layer of ducts. MAG SLAB to be installed on Top of thermal backfill layer to cover entire width of cable trench. Install Tracer wire on each side of trench. Compaction test to be done with Scala at every 20m Interval for 3blows/100mm
label | 17aa68e1-000a-512a-8a5d-504fa600e369 |  | note | UCCL - H
text | 72e180eb-7282-53ca-8da1-ba0d8c46214e |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Installation Of Ducts / Thermal Backfill
label | 005cfd07-9cc9-54bd-87a0-babf52c87a3f |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | 0224d50c-449c-57f8-977d-97f35edfac15 |  | note | Test Required - Installation Of Ducts / Thermal Backfill
label | ae3f0e83-6bee-5992-84fb-3fcedffece00 |  | note | Inspection By - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | b699f60e-64d1-523d-82d4-86c3e5d203ac |  | note | Task Timing Or Task Frequency - UG-7B
label | 25388878-448c-505b-9e2c-a42eaab672e7 |  | note | Acceptance Criteria - 2X 100mm, 10X150mm Heavy Duty Orange uPVC Ducts, Backfilled with Thermal backfill min. 100mm above top layer of ducts. MAG SLAB to be installed on Top of thermal backfill layer to cover entire width of cable trench. Install Tracer wire on each side of trench. Compaction test to be done with Scala at every 20m Interval for 3blows/100mm
label | 7eccb359-4dde-5141-ad01-0eca60236d2c |  | note | UCCL - H
text | ada3c21d-b955-5de4-af4d-491bdb1df01c |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Backfilling
label | 41d38bd7-34f4-5a13-8a58-c3e0ae9b3183 |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | e3542e10-5d1c-5f6c-9b63-39fd6e8fdbfa |  | note | Test Required - Visual Check/Photos
label | ab1cc125-6009-5a75-a0c8-a214dd66f95b |  | note | Inspection By - UCCL
label | cc3b2faa-1239-5931-9567-b000de1c6368 |  | note | Task Timing Or Task Frequency - UG-1
label | d1b95088-63b2-522c-9a7e-495b37c98028 |  | note | Acceptance Criteria - Minimum Cover from Finish Ground level to be as specified in IFC Drawing. Backfilled with approved material and compacted with small Plate Compactor in confined space or static roll with 4T Roller. Detachable Metal type Marking Tap to be installed 200mm apart across entire width of trench 250mm below finish ground level. Reinstate to match existing surface.
label | df9ae3f8-57ee-509c-8d6e-faaeebc1c25d |  | note | UCCL - H
text | ae568987-5ac8-5549-9f3d-badc07eb87a9 |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Backfilling
label | 826e60c3-1c8b-53ec-9f1d-2aae2bda54d0 |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | f7d663b7-61f4-5040-80d4-e991e0ad01d1 |  | note | Test Required - Visual Check/Photos
label | 2a4ca226-2d8c-5fb1-a358-b43d6b096956 |  | note | Inspection By - UCCL
label | 552b57b8-7332-54c8-9661-a55451cfa53b |  | note | Task Timing Or Task Frequency - UG-2
label | 841425cd-4f4f-5353-a867-cf79e98b274d |  | note | Acceptance Criteria - Minimum Cover from Finish Ground level to be as specified in IFC Drawing. Backfilled with approved material and compacted with small Plate Compactor in confined space or static roll with 4T Roller. Detachable Metalic type Marking Tap to be installed 200mm apart across entire width of trench 250mm below finish ground level. Reinstate to match existing surface.
label | 61435c09-9eba-59d5-8408-f60dbaa2b4fa |  | note | UCCL - H
text | 6c373177-bacd-5608-8b54-07286c5922b8 |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Backfilling
label | 7928edf3-4aab-5fbe-8b15-608bf8e3ec6c |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | e83c54fe-0859-580b-9864-2b1dcf65694a |  | note | Test Required - Visual Check/Photos
label | 089ec85f-5ca9-560e-8853-f623c588dc74 |  | note | Inspection By - UCCL
label | 2745b3cb-e06d-5e26-bd2d-4f770a0955fe |  | note | Task Timing Or Task Frequency - UG-3
label | 3b733ec4-ff56-587b-adf0-e9134d234a93 |  | note | Acceptance Criteria - Minimum Cover from Finish Ground level to be as specified in IFC Drawing. Backfilled with approved material and compacted with small Plate Compactor in confined space or static roll with 4T Roller. Detachable Metalic type Marking Tap to be installed 200mm apart across entire width of trench 250mm below finish ground level. Reinstate to match existing surface.
label | 0da7adcb-f97b-5885-8366-fcab8ff69e99 |  | note | UCCL - H
text | 9954c22c-97ff-5ad7-b2df-c139ef89016a |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Backfilling
label | b911be8b-a80f-5908-ba88-7a8de561b879 |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | f5602079-1988-57c4-8f9a-507bc3a2e858 |  | note | Test Required - Visual Check/Photos
label | 02d51a94-f537-593c-9a9e-1fdbd088739b |  | note | Inspection By - UCCL
label | 91569e26-1db2-5548-9428-595292239dd9 |  | note | Task Timing Or Task Frequency - UG-4A
label | ce9c1afb-d437-5875-b85d-918dceb8a1ae |  | note | Acceptance Criteria - Minimum Cover from Finish Ground level to be as specified in IFC Drawing. Backfilled with approved material and compacted with small Plate Compactor in confined space or static roll with 4T Roller. Detachable Metalic type Marking Tap to be installed 200mm apart across entire width of trench 250mm below finish ground level. Reinstate to match existing surface.
label | 0132f3f0-7834-545b-bb91-1f9b8630dd3d |  | note | UCCL - H
text | 3f1c6927-dafa-5d44-b153-c83ec26a2c7f |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Backfilling
label | 3c395d78-dcd4-5650-859b-1fe453a9b357 |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | b3a6f33e-63e0-5788-93a3-7b606fda3908 |  | note | Test Required - Visual Check/Photos
label | 03ca92fd-315d-50aa-bd49-a4a9f8d3f3eb |  | note | Inspection By - UCCL
label | f1048de3-a94d-592e-8fc5-e4820895d33b |  | note | Task Timing Or Task Frequency - UG-4B
label | 40120e67-7ff0-50cd-97f1-b0b06a98434a |  | note | Acceptance Criteria - Minimum Cover from Finish Ground level to be as specified in IFC Drawing. Backfilled with approved material and compacted with small Plate Compactor in confined space or static roll with 4T Roller. Detachable Metalic type Marking Tap to be installed 200mm apart across entire width of trench 250mm below finish ground level. Reinstate to match existing surface.
label | 9e21d536-ea9e-51a3-a2aa-0d58c33627cd |  | note | UCCL - H
text | 89bf2bdc-11cd-5dcc-9415-b8c8c452fce9 |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Backfilling
label | 1981fc8d-8ecb-5c13-934d-be15400af3f2 |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | a7979560-9421-5679-b5c0-cd692ec8aa8f |  | note | Test Required - Visual Check/Photos
label | f69a18cf-ea13-58d2-80bb-3933cc399fa6 |  | note | Inspection By - UCCL
label | 1f2bbaa5-162f-5cf9-b5f8-a0788cb71a71 |  | note | Task Timing Or Task Frequency - UG-5
label | 8e865c2d-ee1f-52c5-9ecc-5b9e6e62157e |  | note | Acceptance Criteria - Minimum Cover from Finish Ground level to be as specified in IFC Drawing. Backfilled with approved material and compacted with small Plate Compactor in confined space or static roll with 4T Roller. Detachable Metalic type Marking Tap to be installed 200mm apart across entire width of trench 250mm below finish ground level. Reinstate to match existing surface.
label | d315fd70-5860-5f04-ac78-f6b2836b1869 |  | note | UCCL - H
text | 11957a19-d67d-5076-94ae-b8c0d6391e7a |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Backfilling
label | d93b93bd-8c30-544c-b2b4-0c167fbc4d32 |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | 5bb50b9f-9c66-5d18-a260-f7b643e4af70 |  | note | Test Required - Visual Check/Photos
label | a6cbf59f-4a49-52da-b89b-c6df75875b73 |  | note | Inspection By - UCCL
label | efc58433-574d-56c9-ad35-6934398e3228 |  | note | Task Timing Or Task Frequency - UG-6
label | 598c235e-89a7-53a5-85f5-06065bb95445 |  | note | Acceptance Criteria - Minimum Cover from Finish Ground level to be as specified in IFC Drawing. Backfilled with approved material and compacted with small Plate Compactor in confined space or static roll with 4T Roller. Detachable Metalic type Marking Tap to be installed 200mm apart across entire width of trench 250mm below finish ground level. Reinstate to match existing surface.
label | d34792f3-36f6-543b-84cd-978459483e3d |  | note | UCCL - H
text | bdac2a49-96e2-5b7b-a1aa-b3263938002e |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Backfilling
label | ed049acc-4565-5fe0-9924-3c34d7a7a6c6 |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | 6c8140bb-75e6-5296-b3a3-1ee26fde4821 |  | note | Test Required - Visual Check/Photos
label | cfd7e509-cb7c-595f-9d2c-74efdd4d346d |  | note | Inspection By - UCCL
label | 367ca3e7-80d1-5c43-a65a-96a28e81e6f7 |  | note | Task Timing Or Task Frequency - UG-7A
label | 0c8e6503-f1f6-5321-8b1c-c9bbcaf48a07 |  | note | Acceptance Criteria - Minimum Cover from Finish Ground level to be as specified in IFC Drawing. Backfilled with approved material and compacted with small Plate Compactor in confined space or static roll with 4T Roller. Detachable Metalic type Marking Tap to be installed 200mm apart across entire width of trench 250mm below finish ground level. Reinstate to match existing surface.
label | 69a64e61-cfd9-5b60-88f4-c6d16f2bbcd0 |  | note | UCCL - H
text | 17bf6c35-a86c-55cd-9447-eb98b31e952a |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Backfilling
label | 203a1b54-1f65-595b-9c70-f9958a33330a |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0540, DET-0541, DET-0542, DET-0543
label | 6b584e06-e87d-5e5b-a32f-f9caefa41e60 |  | note | Test Required - Visual Check/Photos
label | ef6afa74-3522-54d1-8d7a-ecf87a76924e |  | note | Inspection By - UCCL
label | 2bf62702-1685-5524-a627-ee1d0038c57c |  | note | Task Timing Or Task Frequency - UG-7B
label | 1af886dc-82b5-5831-92f3-b08024fce07c |  | note | Acceptance Criteria - Minimum Cover from Finish Ground level to be as specified in IFC Drawing. Backfilled with approved material and compacted with small Plate Compactor in confined space or static roll with 4T Roller. Detachable Metalic type Marking Tap to be installed 200mm apart across entire width of trench 250mm below finish ground level. Reinstate to match existing surface.
label | dc198d04-6730-5899-8c85-4cf4cc91bdc5 |  | note | UCCL - H
text | 6496d369-a2a4-5ea0-98f4-7b3588b779e3 |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-group |  |  | section | Electrical Manholes
checkpoint-status |  |  | checkpoint | Setout
label | ec935717-ab1e-5f8e-9f87-b61fe8f47321 |  | note | Specification Reference - As per IFC Drawings and approved CAD files
label | 043bf5c0-32cb-578c-aec3-708efb09f62b |  | note | Test Required - Surveying
label | e63e1dbb-7a55-58d7-b9c6-1109fd2e25b0 |  | note | Inspection By - Surveyor
label | 738cb33b-64a6-52bc-b278-27f45cad2a8b |  | note | Task Timing Or Task Frequency - For set out of each Manhole
label | d532bdfb-4466-57bc-93fa-aa3057a0c782 |  | note | Acceptance Criteria - Horizontal Alignment to be within +/-100mm of trench position Vertical alignment to be within +/-50mm based on existing Ground levels
label | ee7089e6-bde9-5075-afff-3f8424afd5bb |  | note | UCCL - W
text | 98245ffa-0d9f-5f9a-934c-ebaca05b2262 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Excavation
label | fe867821-8e25-561b-b15f-8f09061a86a0 |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0542
label | 6b4187ec-0c02-5eff-b578-8504ca9b13de |  | note | Test Required - Visual Check/Photos
label | bed2e03f-a54e-57bd-991f-cea82182efbb |  | note | Inspection By - UCCL
label | 09667fea-a1aa-511e-9eb7-03d052fad90d |  | note | Task Timing Or Task Frequency - For each Electrical Manhole
label | d7a8f0fe-ed92-55e6-94d7-072aa13b7582 |  | note | Acceptance Criteria - Excavation Depth Correct to allow for all incoming ducts and drainage pipe. Allow for Min. 50mm of site concrete. No subgrade Testing Required.
label | cfb08c98-e806-5c28-9a9a-f34f75df33ec |  | note | UCCL - W
text | 5df87de8-c84f-508f-9612-fa94eeb841df |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Manhole Installation
label | bba9cd77-0411-5754-888b-b75f2e3317da |  | note | Specification Reference - TABG-JEC-0-000-ELE-DET-0543
label | fce2f22f-9563-5200-b33c-ac82f2d0dcfd |  | note | Test Required - Visual Check
label | 1125051f-d2bd-547a-be86-b752fd6b0b12 |  | note | Inspection By - UCCL
label | f36b674b-ba41-5b1a-b97a-95e40f856844 |  | note | Task Timing Or Task Frequency - Check for any damage prior and during Installation of Each manhole and ducts
label | 56152149-f937-5006-9a14-3b5f9b99b070 |  | note | Acceptance Criteria - Correct size manhole as specified in IFC Drawings. No visual Damage to manhole.Correct orientation. Please refer to specification reference for tolerance. Electrical Manhole installation Checksheet for each manhole. Refer to notes on TABG-JEC-0-000-ELE-DET-0543 (1). Novaflo only to be installed into lower side manholes (one side only).
label | 58ac48b0-7b5e-5039-af00-b8ee227f6133 |  | note | UCCL - W
text | 15fabc51-89cf-5936-8c56-87ee6ffb56bd |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Backfill
label | 3e8f9539-d536-5134-9546-676082dfbde8 |  | note | Specification Reference - Design / IFC Drawings
label | 656d5573-4d6a-54ee-b58c-f769f7008341 |  | note | Test Required - Visual Inspection
label | 50eadbbb-e6a5-5268-8ecd-3465f92d077e |  | note | Inspection By - Engineer
label | 43d2de36-7f76-58db-80a4-eeea1f44ae1d |  | note | Task Timing Or Task Frequency - For Each Manhole
label | 0e5c76c0-bebf-5d05-bb47-f1292237816f |  | note | Acceptance Criteria - Backfilling with site won material with small plate compactor in confined space and static roll with 4T Roller where applicable with max. of 300mm lift. Reinstate to match existing surface.
label | ae3c17e4-94fd-5425-9edc-532de34807fb |  | note | UCCL - W
text | 01adbbcc-45de-5658-a736-f521ce03f048 |  | textbox | Date Completed:
checkpoint-group |  |  | section | Duct Installation under Road Crossing and around other services
checkpoint-status |  |  | checkpoint | Duct Installation for Road Crossing
label | 73d7612b-6a4e-571a-aecb-d118e7f83eea |  | note | Specification Reference - IFC Drawings
label | 6957c5d0-45b5-5cd4-af0c-b07ce98e5b0c |  | note | Test Required - Visual/Photo
label | ed25da0b-588a-5c89-8f56-636fc8acc354 |  | note | Inspection By - UCCL/CEL
label | 0fe34ec6-596a-5dda-8783-41fc19cb72cd |  | note | Task Timing Or Task Frequency - UG-5 SGW Pump station
label | f02d3abf-97a2-5049-a6b9-45e9623c0b07 |  | note | Acceptance Criteria - 15Mpa Concrete cap to suit road crossing width. Concrete cap shall not be reinforced and shall be poured over the full trench for all the road crossing of the ducts.
label | 3767e34c-c1c0-5cbc-a18d-cc57f59047a6 |  | note | UCCL - W
text | ea303e2d-853e-57cd-8afd-df8f5344c695 |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Duct Installation for Road Crossing
label | d4fb7eed-9088-5922-ab99-d796b45b7561 |  | note | Specification Reference - IFC Drawings
label | 6a0d20d4-615b-5c3f-81c7-25ff1713f137 |  | note | Test Required - Visual/Photo
label | 294e1dfb-4f29-54c7-ac1c-22e9bd372602 |  | note | Inspection By - UCCL/CEL
label | 29ab0d54-b7ea-5abe-aeba-ceab3314ba86 |  | note | Task Timing Or Task Frequency - UG7B -SGW Pump station
label | 8d503b16-5651-5baf-aa13-67978c2b492a |  | note | Acceptance Criteria - 15Mpa Concrete cap to suit road crossing width. Concrete cap shall not be reinforced and shall be poured over the full trench for all the road crossing of the ducts.
label | 193ae290-228c-5f16-8bcc-cbb6254a9d35 |  | note | UCCL - W
text | d080ec66-f5be-5964-8ebe-e7ca92df138f |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Duct Installation for Road Crossing
label | 0edfb18d-ac97-51c5-96e9-ff5606a429e1 |  | note | Specification Reference - IFC Drawings
label | ad752248-ab56-5247-948f-64cf9fbb6764 |  | note | Test Required - Visual/Photo
label | 4bfe21e4-e677-55ea-8b49-37dfcbbc4785 |  | note | Inspection By - UCCL/CEL
label | c092c538-9c3c-5151-b8b5-04a2208ecccf |  | note | Task Timing Or Task Frequency - UG-1 Separator slab area (5 Locations)
label | 2ede0356-ab7f-55cd-937f-9fb27a0d6542 |  | note | Acceptance Criteria - 15Mpa Concrete cap to suit road crossing width. Concrete cap shall not be reinforced and shall be poured over the full trench for all the road crossing of the ducts.
text | 3d608e33-e36e-566c-8d6f-fc41c96b1e6d |  | textbox | Date Completed:
checkpoint-status |  |  | checkpoint | Duct Crossing Around other services
label | 41f702c9-c997-5226-8c18-75853ea0aa62 |  | note | Specification Reference - IFC Drawings
label | a0a11cf2-82d7-5836-b6e2-80cee948ddde |  | note | Test Required - Visual/Photo
label | 054a6f07-5c29-563a-bc9b-e859b72b6136 |  | note | Inspection By - UCCL/CEL
label | 62649fd0-01f2-58ee-952f-677c63f28ef8 |  | note | Task Timing Or Task Frequency - For each duct crossing around other services
label | 7e4b0b5c-17a9-5ab8-b025-cf931cf51182 |  | note | Acceptance Criteria - As per details section on TABG-JEC-0-000-ELE-DET-0541 (1)
label | 055b3fa4-24a8-552f-b04c-a9dd210811c4 |  | note | UCCL - W
text | b4bc6b8c-e3eb-57a5-a37c-7cdb248e4197 |  | textbox | Date Completed:
checkpoint-group |  |  | section | Post Construction
checkpoint-status |  |  | checkpoint | As Built & Final Design Documentation
label | 023499de-b277-5ed6-aa6d-c86e8f3c9d7b |  | note | Test Required - Surveying
label | 4771336c-6679-5fb2-8f5b-f2f1b7f9008d |  | note | Inspection By - UCCL
label | e9c3de4d-39fe-56ef-8209-32dd14ffecb5 |  | note | Task Timing Or Task Frequency - For each Trench line
label | 136207b3-a1f3-5ca0-a7fe-e505457fc2a6 |  | note | Acceptance Criteria - Confirmation From Engineer on as built records & redline mark ups
label | 926c20ec-4ef0-5281-9003-20c9143a4921 |  | note | UCCL - H
text | 824577a6-038b-5164-aa9f-ba5b3d160423 |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Completion Inspection inc. Construction Defects Report
label | 57369aaa-e259-5591-a5c6-497745f213c0 |  | note | Test Required - Completion inspection on the Each Duct Line by CEL
label | 2d539ea9-e944-5109-88df-9a5bb297318e |  | note | Inspection By - CEL/ UCCL
label | 50993522-831d-5a2d-b1d4-cd35c01693e6 |  | note | Task Timing Or Task Frequency - For each DuctLine
label | 7dea4826-9f19-5f59-862e-c8b5309d2bdc |  | note | Acceptance Criteria - Provided a completed construction defect report that that details any remedial measures taken, & snag lists closed out
label | 2c640238-4523-55d4-9138-4ecef272c33a |  | note | UCCL - H
text | 8300df11-8926-5cf2-bafc-31402c0e4f57 |  | textbox | Date Completed:
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checklist-flat | 89983eeb-40b8-4d9a-846b-86db75106d69 |  | checklist | Document: |  |  |  |  | Yes | Project Documentation | 9462476a-12bf-4d9e-a66b-8479879ee065
checkpoint-no-status | 78d25478-5723-4f8e-b4d8-3b7b8d9a0cd0 |  | checkpoint | Document Attached
checklist-sectioned |  |  | checklist | Concrete Inspection |  |  |  |  | Yes | Concrete Inspection | b8362b3b-9a0e-46be-bf56-d809efc4883c
checkpoint-group |  |  | section | Formwork
checkpoint-status |  |  | checkpoint | Adequately braced and supported
checkpoint-status |  |  | checkpoint | Grout tight
checkpoint-status |  |  | checkpoint | Correct dimensions
checkpoint-status |  |  | checkpoint | Cleaned and oiled
checkpoint-status |  |  | checkpoint | Formed surfaces straight
checkpoint-status |  |  | checkpoint | Major penetrations located
checkpoint-status |  |  | checkpoint | Embedded items located
checkpoint-status |  |  | checkpoint | Correct for specified surface finish
checkpoint-status |  |  | checkpoint | Adequate seating Pre Cast units
checkpoint-status |  |  | checkpoint | Permit to Load Obtained
checkpoint-group |  |  | section | Reinforcement
checkpoint-status |  |  | checkpoint | Reinforcement Content and size
checkpoint-status |  |  | checkpoint | Confirm correct grade markings
checkpoint-status |  |  | checkpoint | Placement, tolerance, clearance
checkpoint-status |  |  | checkpoint | Rigidity and cover
checkpoint-status |  |  | checkpoint | Clean steel
checkpoint-status |  |  | checkpoint | Lap location and lengths
checkpoint-status |  |  | checkpoint | Starters/dowels correctly located
checkpoint-group |  |  | section | Construction Joints
checkpoint-status |  |  | checkpoint | Location
checkpoint-status |  |  | checkpoint | Roughened
checkpoint-status |  |  | checkpoint | Clean
checkpoint-status |  |  | checkpoint | Water bar placed if specified
checkpoint-group |  |  | section | Post Pour
checkpoint-status |  |  | checkpoint | Correct mix ordered
checkpoint-status |  |  | checkpoint | Independent Survey – Check off critical survey points
checkpoint-status |  |  | checkpoint | Engineer’s Rep Notified
holdpoint |  |  | signoff | Pre-Pour Checked and Accepted
checkpoint-group |  |  | section | Wet Concrete Checks
checkpoint-status |  |  | checkpoint | Correct mix delivered
checkpoint-status |  |  | checkpoint | Slump/flow Target
checkpoint-status |  |  | checkpoint | Compliance Cylinders Taken
checkpoint-status |  |  | checkpoint | Site Cured Cylinders Taken
checkpoint-status |  |  | checkpoint | Concrete Vibrated
checkpoint-status |  |  | checkpoint | Mandrels drawn through all ducts to verify no leakage / disconnection
checkpoint-status |  |  | checkpoint | Finished Level: Finished to grout check / angle fillet worked to
checkpoint-status |  |  | checkpoint | Surface to required finish eg U2, U4
checkpoint-status |  |  | checkpoint | Retarder applied at end of the pour
checkpoint-status |  |  | checkpoint | Curing applied (specify type)
checkpoint-status |  |  | checkpoint | Concrete Supply Dockets collected
checkpoint-group |  |  | section | Post Concrete Inspection
checkpoint-status |  |  | checkpoint | Curing correctly carried out
checkpoint-status |  |  | checkpoint | Concrete Strength for Striking
checkpoint-status |  |  | checkpoint | Concrete Strength for backfilling
checkpoint-status |  |  | checkpoint | Preparation of Construction Joints Completed
checkpoint-status |  |  | checkpoint | Blow holes, tie bar holes filled
checkpoint-status |  |  | checkpoint | Inspection of surface/s & any authorised repairs have been completed
checkpoint-status |  |  | checkpoint | As-Built complete
checkpoint-group |  |  | section | Sign Off
checkpoint-status |  |  | checkpoint | Pre-Pour Checked and Accepted
text | 48513fa4-beca-5b1a-93a6-f5d5b57046d7 |  | textbox | Contractor Name
text | f39933d9-8d12-5f14-bfbb-b589e08b7fe7 |  | textbox | Date
text | 9c7a0efd-ef54-5039-b577-68d8b70ae14b |  | textbox | Engineer Name
text | d0332bcb-dd67-5dbb-ba9e-c5bf48927d5e |  | textbox | Date
checklist-sectioned |  |  | checklist | ITP No: 002 Foundations | itp |  |  |  | Yes | ITP No: 002 Foundations | bef37af0-9f29-4e3e-a64c-b5b1ded19bd1
checkpoint-group |  |  | section | Preliminary
checkpoint-status |  |  | checkpoint | Concrete Mix Design Approved
label | 65164fab-1aa4-5728-9e6a-11a8bd01fe0e |  | note | SPECIFICATION REFERENCE: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 88834bce-275b-5df5-a4e2-9b56788154d9 |  | note | TEST REQUIRED: Jacobs
label | cfea2cf4-2e4e-5502-8701-fbe098c05044 |  | note | INSPECTION BY: Engineer
label | f627f45c-36f5-53fb-b22a-ba04c26e21e8 |  | note | TASK TIMING OR TASK FREQUENCY: Formal request/RFI
label | 427eca07-2828-5354-a238-b818c1968ecf |  | note | ACCEPTANCE CRITERIA: Approved by Engineer
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Concrete 1.1
label | c55ccb04-5864-5a00-b6f4-649e9bdfe9b0 |  | note | SPECIFICATION REFERENCE: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 44563d38-a26a-5881-a164-b0045a0e3253 |  | note | TEST REQUIRED: Compressive Strength
label | fd7e5b24-3980-5875-b8e8-dfb5e47eaf4a |  | note | INSPECTION BY: Supplier
label | 2280b36d-aad1-5a2b-bbb3-da0007a9d292 |  | note | TASK TIMING OR TASK FREQUENCY: 1 Set of 3 tests for every 50m³ testing at the plant and 100m³ on site. Slump test on first 2 trucks from each plant. Then visual slump test for the pours over 20m³ and intermitted/random testing every 100m³.
label | 57efe228-8bb5-5a67-9c96-6cde621dac39 |  | note | ACCEPTANCE CRITERIA: Slump Test, Air Content Test, Compressive strength test results, shrinkage strain Accreditation/ Registration certificate from Laboratory
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Concrete 1.2
label | 3b7fa110-919d-5cd4-af6e-2bd7462eddc0 |  | note | SPECIFICATION REFERENCE: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 5cb4f689-8dba-52fa-b89b-827b8f49b650 |  | note | TEST REQUIRED: Slump Test
label | b077c7bf-ad1b-5de2-bb91-daa5eabdf656 |  | note | INSPECTION BY: Supplier
label | ce780e56-2a23-5704-a8dc-9423dbbf457f |  | note | TASK TIMING OR TASK FREQUENCY: 1 Set of 3 tests for every 50m³ testing at the plant and 100m³ on site. Slump test on first 2 trucks from each plant. Then visual slump test for the pours over 20m³ and intermitted/random testing every 100m³.
label | 9f53be20-da80-56bd-8e30-f1ea92c38bf8 |  | note | ACCEPTANCE CRITERIA: Slump Test, Air Content Test, Compressive strength test results, shrinkage strain Accreditation/ Registration certificate from Laboratory
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Concrete 1.3
label | 1256faf4-e208-5f6c-9eba-7ca322f4c2d9 |  | note | SPECIFICATION REFERENCE: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 2fdaa40a-06dd-505a-b4f7-c23f621eddcd |  | note | TEST REQUIRED: Air Content Test
label | b3fd2cab-2ef2-5b99-9558-505869a3f005 |  | note | INSPECTION BY: Supplier
label | 44a52a1a-cf61-537e-9510-c4e6b53369b7 |  | note | TASK TIMING OR TASK FREQUENCY: 1 Set of 3 tests for every 50m³ testing at the plant and 100m³ on site. Slump test on first 2 trucks from each plant. Then visual slump test for the pours over 20m³ and intermitted/random testing every 100m³.
label | aeae1bbe-09c3-55f9-93d5-6d7effccdfc6 |  | note | ACCEPTANCE CRITERIA: Slump Test, Air Content Test, Compressive strength test results, shrinkage strain Accreditation/ Registration certificate from Laboratory
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Concrete 1.4
label | 5dd40283-2785-578a-a0ff-eba9b37962c9 |  | note | SPECIFICATION REFERENCE: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | 6a2a6bf8-7227-5259-b773-2f3fd8535e16 |  | note | TEST REQUIRED: Shrinkage strain at 56 days
label | cb3b95ce-97aa-5f50-a347-9ae78be7fd98 |  | note | INSPECTION BY: Supplier
label | 750b0c43-e262-510c-b2c2-fd3d2dd4bb23 |  | note | TASK TIMING OR TASK FREQUENCY: 1 Set of 3 tests for every 50m³ testing at the plant and 100m³ on site. Slump test on first 2 trucks from each plant. Then visual slump test for the pours over 20m³ and intermitted/random testing every 100m³.
label | 7e0434bc-5e18-51aa-947c-5d538171ddc1 |  | note | ACCEPTANCE CRITERIA: Slump Test, Air Content Test, Compressive strength test results, shrinkage strain Accreditation/ Registration certificate from Laboratory
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Shop Drawings
label | 3b93a0d3-a928-5b4b-9169-5a1204cc6193 |  | note | SPECIFICATION REFERENCE: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification - 12.1.4
label | c94bb2d8-bd98-536a-b5f0-0d80c99f9abb |  | note | TEST REQUIRED: Approved shop drawings prior to fabrication
label | 4df9af90-0f6f-51b9-a050-1e25e3cdfce9 |  | note | INSPECTION BY: Engineer
label | 8a5aff3b-7080-5627-b3be-c04c0dae9934 |  | note | TASK TIMING OR TASK FREQUENCY: 10 Days before commencing fabrication
label | 53ffd583-ae89-574a-b723-94677046e162 |  | note | ACCEPTANCE CRITERIA: Approved by Engineer
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Supply of Reinforcement - Steel reinforcement compliance records
label | 2970f40d-8666-5957-aa71-33b51c65a874 |  | note | SPECIFICATION REFERENCE: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification - STEEL REINFORCEMENT COMPLIANCE 6.1.7
label | 959129e4-0f8f-5f13-9129-d6c727b10ea2 |  | note | TEST REQUIRED: Schedules shall be prepared by the supplier and reviewed/ accepted by CEL prior to fabrication.
label | da968d8a-f18c-59f8-8830-0b6a3d182acb |  | note | INSPECTION BY: Engineer
label | 1f90d2a5-9fb0-5a25-821b-e3166a7b12d2 |  | note | TASK TIMING OR TASK FREQUENCY: Prior to manufacturing any reinforcement
label | 4a7f1618-81b8-5a5f-a3e7-9f66162359a4 |  | note | ACCEPTANCE CRITERIA: Manufacturer´s Mill Certificate/Rebar schedule/Rebar summary sheet
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-group |  |  | section | Pre-construction site works
checkpoint-status |  |  | checkpoint | Ground Condition/Subgrade
label | e03512f6-aab2-571f-a283-a2cc0af668ea |  | note | SPECIFICATION REFERENCE: TABG-JEC-0-ULG-STR-DET-3104(1) Note 4
label | ac124840-7387-51c2-950c-ac93afa8bd85 |  | note | TEST REQUIRED: Geotechnical testing
label | 039b1617-6fe7-554f-8c0b-a56a0ab4e863 |  | note | INSPECTION BY: Contact
label | 5e438797-7f75-5f12-8137-4d433a26e349 |  | note | TASK TIMING OR TASK FREQUENCY: Before placement of any site concrete, Scala penetrometer testing, proof roll.
label | 2054dc26-55d4-5bb7-9f30-e258585435ad |  | note | ACCEPTANCE CRITERIA: SITE TO BE INSPECTED BY AN EXPERIENCED GEOTECHNICAL ENGINEER AND CONFIRM SUITABILITY FOR MINIMUM 100 kPa ULTIMATE BEARING CAPACITY.
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Trim Sub grade
label | f21ee709-111d-5f5c-91a1-1b71893b916d |  | note | SPECIFICATION REFERENCE: As per IFC Drawings and approved CAD files
label | 0b012f76-a695-53ae-bd05-118020ba278a |  | note | TEST REQUIRED: Survery plan
label | db5926ec-fb43-5e6d-a0cf-a21039c37d44 |  | note | INSPECTION BY: UCCL/Engineer
label | f2fcc4b0-7b20-578e-82f1-023e2ece2c7e |  | note | TASK TIMING OR TASK FREQUENCY: Before placement of any site concrete check sub grade profile
label | 0de4e5b0-6970-59fb-b2c2-47699e6f57a1 |  | note | ACCEPTANCE CRITERIA: Finished height for sub grade + 10/-50mm. Minimum thickness to be 50mm as per IFC Drawing. Target RL as per IFC Drawings.
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Site Concrete/binding
label | dd20fe31-83fc-5707-abc8-10079ecd3870 |  | note | SPECIFICATION REFERENCE: As per IFC Drawings and approved CAD files
label | 1ab391e6-e4ea-5af6-9d31-13fd09fde6c3 |  | note | TEST REQUIRED: Visual Inspection
label | ae8412a2-c357-5847-ab0d-4a9ec4d0750b |  | note | INSPECTION BY: UCCL/Engineer
label | 2c16af29-e076-5463-8240-5c40c40b26c0 |  | note | TASK TIMING OR TASK FREQUENCY: Thickness, minimum 50mm, consider 75mm depending on subgrade.
label | f21d67d4-726a-5188-be82-a7497360696c |  | note | ACCEPTANCE CRITERIA: Finished height for site concrete to be within +/- 10mm.Thickness, minimum 50mm, consider 75mm depending on subgrade.
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-group |  |  | section | Setout of Foundations
checkpoint-status |  |  | checkpoint | Setout Pour-1
label | e5aef230-8f20-56ec-8605-293a194c3aa6 |  | note | SPECIFICATION REFERENCE: As per IFC Drawings and approved CAD files
label | 23ab6981-4c8d-5398-920a-c23cb6d970c8 |  | note | TEST REQUIRED: Surveying as built/Visual Check
label | 768b87ae-95fe-52d8-8ae8-722d18e258d8 |  | note | INSPECTION BY: UCCL/Engineer
label | 0f6475ff-6f76-595f-9777-046edebc95c5 |  | note | TASK TIMING OR TASK FREQUENCY: For set out of each Foundation. After placement of Formwork. Top of Foundations to be sloped 1:200 to avoid ponding
label | 491981ea-2b18-5cd6-8d61-442cd0af86b7 |  | note | ACCEPTANCE CRITERIA: RL as specified in IFC Drawings
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Setout Pour-2
label | 2a440e75-89f0-50cb-95be-c3e3523dd43a |  | note | SPECIFICATION REFERENCE: As per IFC Drawings and approved CAD files
label | 4a2faa30-a477-57ea-83ad-ed621e07c4bc |  | note | TEST REQUIRED: Surveying as built/Visual Check
label | 1429595a-d937-50a5-afbe-1b89a3c943df |  | note | INSPECTION BY: UCCL/Engineer
label | e29a576e-4edd-5568-9770-dd5253b8cfd1 |  | note | TASK TIMING OR TASK FREQUENCY: For set out of each Foundation. After placement of Formwork. Top of Foundations to be sloped 1:200 to avoid ponding
label | 46cd7f1c-1d7d-5ce4-8159-939ce1b80c1d |  | note | ACCEPTANCE CRITERIA: RL as specified in IFC Drawings
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Setout Pour-3
label | 9e0db9b0-b2a3-5932-bc61-93df6554cfde |  | note | SPECIFICATION REFERENCE: As per IFC Drawings and approved CAD files
label | 1658778b-12ee-532e-a9a7-769d2fa6e4f2 |  | note | TEST REQUIRED: Surveying as built/Visual Check
label | 2dcb2012-3ee3-5dc8-8f6f-0477cd96b6f7 |  | note | INSPECTION BY: UCCL/Engineer
label | 258f084b-afcc-58f7-8e28-bcc480e39a2a |  | note | TASK TIMING OR TASK FREQUENCY: For set out of each Foundation. After placement of Formwork. Top of Foundations to be sloped 1:200 to avoid ponding
label | c4ebcd1a-744c-59cb-bcfd-2c9046f480ae |  | note | ACCEPTANCE CRITERIA: RL as specified in IFC Drawings
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Setout Pour-4
label | ecb06f0a-3f41-5b05-8c18-cae5b61dfb3f |  | note | SPECIFICATION REFERENCE: As per IFC Drawings and approved CAD files
label | 6ddf702c-ff70-5990-9001-42d6482045a7 |  | note | TEST REQUIRED: Surveying as built/Visual Check
label | b03adc61-f893-5b12-b38c-418fe17c83eb |  | note | INSPECTION BY: UCCL/Engineer
label | bb698251-8a42-57da-b549-39ca710053bb |  | note | TASK TIMING OR TASK FREQUENCY: For set out of each Foundation. After placement of Formwork. Top of Foundations to be sloped 1:200 to avoid ponding
label | 956e9efe-4484-59ed-94bc-0bce3d336f62 |  | note | ACCEPTANCE CRITERIA: RL as specified in IFC Drawings
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Setout Pour-5
label | cbd272be-d94d-507e-8442-e6abf908864b |  | note | SPECIFICATION REFERENCE: As per IFC Drawings and approved CAD files
label | 74bba541-8f20-54aa-813c-d887e361aa27 |  | note | TEST REQUIRED: Surveying as built/Visual Check
label | ffa8bdba-e022-5a07-9218-6b4e1ea9f311 |  | note | INSPECTION BY: UCCL/Engineer
label | 8a176f01-77d7-5697-add8-a23a79738d71 |  | note | TASK TIMING OR TASK FREQUENCY: For set out of each Foundation. After placement of Formwork. Top of Foundations to be sloped 1:200 to avoid ponding
label | 9289bd22-61a2-508b-9069-e6b60114078f |  | note | ACCEPTANCE CRITERIA: RL as specified in IFC Drawings
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Setout Pour-6
label | 777d46c2-9963-5e9a-af65-caa467b91f5c |  | note | SPECIFICATION REFERENCE: As per IFC Drawings and approved CAD files
label | 26bf10fc-c3c9-5a9e-9369-7606f0823dde |  | note | TEST REQUIRED: Surveying as built/Visual Check
label | 6a20b86e-f150-50ad-a5a9-80364a0f7855 |  | note | INSPECTION BY: UCCL/Engineer
label | 14a7d436-553f-57d5-8f0c-58bf5f81795b |  | note | TASK TIMING OR TASK FREQUENCY: For set out of each Foundation. After placement of Formwork. Top of Foundations to be sloped 1:200 to avoid ponding
label | d3b4763f-b683-5859-b25e-66a1d8092033 |  | note | ACCEPTANCE CRITERIA: RL as specified in IFC Drawings
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Setout Pour-7
label | 5c866a29-9df5-55ea-87d9-8e0bd5219b5b |  | note | SPECIFICATION REFERENCE: As per IFC Drawings and approved CAD files
label | 7c5c1a58-10ef-519a-8682-4053522df574 |  | note | TEST REQUIRED: Surveying as built/Visual Check
label | 1d5106af-b291-541d-9e19-1ccdd82a4f8b |  | note | INSPECTION BY: UCCL/Engineer
label | 285d41fe-0f87-5ad2-a9aa-ea43ac084f6c |  | note | TASK TIMING OR TASK FREQUENCY: For set out of each Foundation. After placement of Formwork. Top of Foundations to be sloped 1:200 to avoid ponding
label | a4def0ad-fcc5-5a6a-8884-4887965900f1 |  | note | ACCEPTANCE CRITERIA: RL as specified in IFC Drawings
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Setout Pour-8
label | 57c036f6-eba5-5530-b8ba-736c53f800d8 |  | note | SPECIFICATION REFERENCE: As per IFC Drawings and approved CAD files
label | 392dbbcd-de2a-5db9-afc7-ae1cbee136b7 |  | note | TEST REQUIRED: Surveying as built/Visual Check
label | bbf1d392-5d87-58a9-a248-ebcb34d783b5 |  | note | INSPECTION BY: UCCL/Engineer
label | 4a574431-b5ea-5f29-aa82-22d7d536b508 |  | note | TASK TIMING OR TASK FREQUENCY: For set out of each Foundation. After placement of Formwork. Top of Foundations to be sloped 1:200 to avoid ponding
label | d03fc99e-aad3-56d7-bea5-385e8e71c45d |  | note | ACCEPTANCE CRITERIA: RL as specified in IFC Drawings
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Setout Pour-9
label | 0b609169-aa60-573b-82be-b6c8cb449a1f |  | note | SPECIFICATION REFERENCE: As per IFC Drawings and approved CAD files
label | 9fa57b79-c991-5dc7-9682-76a87a37fc2f |  | note | TEST REQUIRED: Surveying as built/Visual Check
label | 8556fc14-61ac-5154-8a85-4286df4837fb |  | note | INSPECTION BY: UCCL/Engineer
label | e5ac400b-ea37-5152-aa13-481e8cdfd59a |  | note | TASK TIMING OR TASK FREQUENCY: For set out of each Foundation. After placement of Formwork. Top of Foundations to be sloped 1:200 to avoid ponding
label | 93a50898-bd9c-5be7-9984-65e72077f899 |  | note | ACCEPTANCE CRITERIA: RL as specified in IFC Drawings
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Setout Pour-10
label | 5b71c8de-febc-53e9-a2a8-a1604abe7ee2 |  | note | SPECIFICATION REFERENCE: As per IFC Drawings and approved CAD files
label | d12492c5-bc2d-5ece-bc57-3dd78b37c405 |  | note | TEST REQUIRED: Surveying as built/Visual Check
label | f73ebc8b-b886-5780-be25-d939011db555 |  | note | INSPECTION BY: UCCL/Engineer
label | c989ccae-37bd-505a-8be6-3e012525ef7d |  | note | TASK TIMING OR TASK FREQUENCY: For set out of each Foundation. After placement of Formwork. Top of Foundations to be sloped 1:200 to avoid ponding
label | 38d9ef05-9865-5d58-9448-86a67308abaf |  | note | ACCEPTANCE CRITERIA: RL as specified in IFC Drawings
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Setout Pour-11
label | 5a9d8842-1598-564b-86dd-66e8fee0227e |  | note | SPECIFICATION REFERENCE: As per IFC Drawings and approved CAD files
label | a6cde29e-46e0-52ec-984f-9d04b22c8c2e |  | note | TEST REQUIRED: Surveying as built/Visual Check
label | c48c9bfb-f9c9-5cd3-aa8f-cccc571a1d82 |  | note | INSPECTION BY: UCCL/Engineer
label | a3441cc0-77cf-5a10-aefa-b677bb1d5ce5 |  | note | TASK TIMING OR TASK FREQUENCY: For set out of each Foundation. After placement of Formwork. Top of Foundations to be sloped 1:200 to avoid ponding
label | e74424e6-c24f-53be-9b54-83c8844672eb |  | note | ACCEPTANCE CRITERIA: RL as specified in IFC Drawings
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Setout Pour-12
label | 4374ce97-311c-5ca5-b486-9db04f9bb2ec |  | note | SPECIFICATION REFERENCE: As per IFC Drawings and approved CAD files
label | 0b4801b6-8bc7-556b-aa32-4f83e183f31c |  | note | TEST REQUIRED: Surveying as built/Visual Check
label | ccecb552-1721-5289-9c03-358c5abd33d0 |  | note | INSPECTION BY: UCCL/Engineer
label | 416a4a57-9244-54bc-be7b-1f7f3d8aa268 |  | note | TASK TIMING OR TASK FREQUENCY: For set out of each Foundation. After placement of Formwork. Top of Foundations to be sloped 1:200 to avoid ponding
label | cc7b1c38-df23-5598-a1f1-6c4e45e5853b |  | note | ACCEPTANCE CRITERIA: RL as specified in IFC Drawings
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Setout Pour-13
label | 5f6b5aeb-5a0b-5142-a96c-285e10dfed43 |  | note | SPECIFICATION REFERENCE: As per IFC Drawings and approved CAD files
label | 033218ce-3800-55f6-81bd-a8432b480b98 |  | note | TEST REQUIRED: Surveying as built/Visual Check
label | 847d94de-5139-5da9-bc1c-b46f47204cae |  | note | INSPECTION BY: UCCL/Engineer
label | 96d54045-f6c9-5376-9953-c57ad10df41e |  | note | TASK TIMING OR TASK FREQUENCY: For set out of each Foundation. After placement of Formwork. Top of Foundations to be sloped 1:200 to avoid ponding
label | 7f7ca799-4f4b-5779-8966-f90e3ed66a8c |  | note | ACCEPTANCE CRITERIA: RL as specified in IFC Drawings
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-group |  |  | section | Pre Pour Inspections
checkpoint-status |  |  | checkpoint | Pre-pour Insepction Pour-1
label | 3e90f564-359b-5158-9cab-94f838d0e6d8 |  | note | SPECIFICATION REFERENCE: Design / IFC Drawings
label | d6026572-fc5c-5c18-9ebf-1fc458c2ddb7 |  | note | TEST REQUIRED: Visual Inspection
label | f4aeb28e-8586-5b25-866e-0e2cc436aeee |  | note | INSPECTION BY: Engineer
label | f205a764-24b3-56c3-ba30-3fe7d047ce40 |  | note | TASK TIMING OR TASK FREQUENCY: Pre pour inspection for each Pour or Foundation
label | 863a2131-ca71-59ee-9258-568d4ac0181b |  | note | ACCEPTANCE CRITERIA: Pre pour inspection check sheet
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Pre-pour Insepction Pour-2
label | 4b558900-cc2b-572b-97a2-3e6edcc89c06 |  | note | SPECIFICATION REFERENCE: Design / IFC Drawings
label | 3913bdbb-c518-5a29-bdd4-b4c21a54f530 |  | note | TEST REQUIRED: Visual Inspection
label | b03f6289-206c-51fd-b5d6-feb7caac6e27 |  | note | INSPECTION BY: Engineer
label | 4c775664-62e6-5209-9bf6-23287fc1522b |  | note | TASK TIMING OR TASK FREQUENCY: Pre pour inspection for each Pour or Foundation
label | ecd3c97f-9225-5537-a053-28d34fa522b5 |  | note | ACCEPTANCE CRITERIA: Pre pour inspection check sheet
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Pre-pour Insepction Pour-3
label | 9bf130e8-c0b8-5d8f-bacd-0ec25c171416 |  | note | SPECIFICATION REFERENCE: Design / IFC Drawings
label | 3e7d5529-2076-52bd-a0ad-1a4ef2abd0da |  | note | TEST REQUIRED: Visual Inspection
label | 41fed1bf-2cff-569f-935c-38482fdc8210 |  | note | INSPECTION BY: Engineer
label | 42e05416-a29e-57ce-a100-f1db5e669003 |  | note | TASK TIMING OR TASK FREQUENCY: Pre pour inspection for each Pour or Foundation
label | 846243e0-949c-58c0-a040-4cee1091f625 |  | note | ACCEPTANCE CRITERIA: Pre pour inspection check sheet
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Pre-pour Insepction Pour-4
label | ead29f99-1d10-5457-867a-a0dbd9d9a467 |  | note | SPECIFICATION REFERENCE: Design / IFC Drawings
label | d506b9fe-bbb7-52d3-877c-60d04df6113d |  | note | TEST REQUIRED: Visual Inspection
label | 80b3eac0-c0a4-5bbb-9b10-e5877f7639cf |  | note | INSPECTION BY: Engineer
label | 5ce7b165-1e7c-5237-8e71-1a689f2b42c0 |  | note | TASK TIMING OR TASK FREQUENCY: Pre pour inspection for each Pour or Foundation
label | 8e6d0dcb-11fe-52c8-bb0a-17ba7368eca3 |  | note | ACCEPTANCE CRITERIA: Pre pour inspection check sheet
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Pre-pour Insepction Pour-5
label | 53e27c29-500a-5a4e-8947-baa787a0b1ed |  | note | SPECIFICATION REFERENCE: Design / IFC Drawings
label | d3d9fa56-4d89-521a-a2e0-1d163411579e |  | note | TEST REQUIRED: Visual Inspection
label | c5fceb5f-56d9-58ea-8677-470e277206c9 |  | note | INSPECTION BY: Engineer
label | ec8fc36d-df9c-5cd0-9838-b16d4ccebb2c |  | note | TASK TIMING OR TASK FREQUENCY: Pre pour inspection for each Pour or Foundation
label | 4c8d900a-ae52-503f-bf1e-02ca3e632b1d |  | note | ACCEPTANCE CRITERIA: Pre pour inspection check sheet
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Pre-pour Insepction Pour-6
label | 476da45b-ad9e-5fa1-b4a7-f26d8dde79fb |  | note | SPECIFICATION REFERENCE: Design / IFC Drawings
label | e3275be2-d869-5545-b5ae-b403a318be92 |  | note | TEST REQUIRED: Visual Inspection
label | cf6c96d2-a74d-51c9-9eff-c2a9b99d5192 |  | note | INSPECTION BY: Engineer
label | 7fc1d0d5-dcfd-50e3-aba2-ce01ad1b1a78 |  | note | TASK TIMING OR TASK FREQUENCY: Pre pour inspection for each Pour or Foundation
label | b5c3249a-2e9a-588d-86d2-c9a6aaeca2fd |  | note | ACCEPTANCE CRITERIA: Pre pour inspection check sheet
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Pre-pour Insepction Pour-7
label | 5c98dd71-b964-5fa1-8ff1-ef2513ecffe9 |  | note | SPECIFICATION REFERENCE: Design / IFC Drawings
label | 000176d4-f2e1-58aa-ac23-fe5968e287ed |  | note | TEST REQUIRED: Visual Inspection
label | 48549a0d-0b9e-5554-8bdd-00f042cd9628 |  | note | INSPECTION BY: Engineer
label | 93e2c608-fec2-5d4c-902b-05861ba7ea5b |  | note | TASK TIMING OR TASK FREQUENCY: Pre pour inspection for each Pour or Foundation
label | 72b861e9-be71-59dd-9eb7-db7a6ba8f2aa |  | note | ACCEPTANCE CRITERIA: Pre pour inspection check sheet
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Pre-pour Insepction Pour-8
label | b2136ce5-df1b-5bff-9f0e-d23b0f839a72 |  | note | SPECIFICATION REFERENCE: Design / IFC Drawings
label | 841dad1f-22be-596a-9826-340f6ec69669 |  | note | TEST REQUIRED: Visual Inspection
label | afad2117-22c1-5fc7-bfa9-8be2296103d5 |  | note | INSPECTION BY: Engineer
label | 722fd7e2-ed87-5c30-9cb5-a3d228438944 |  | note | TASK TIMING OR TASK FREQUENCY: Pre pour inspection for each Pour or Foundation
label | ac888c10-d1f6-5dee-9947-3dba78f2b0b5 |  | note | ACCEPTANCE CRITERIA: Pre pour inspection check sheet
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Pre-pour Insepction Pour-9
label | 121d0639-b03a-5ed4-a24b-87ad15c2fb1d |  | note | SPECIFICATION REFERENCE: Design / IFC Drawings
label | 1efbf18b-35d9-5530-895f-8f888c6b5520 |  | note | TEST REQUIRED: Visual Inspection
label | 0ca18913-cafe-51cf-bd21-e73a1610d647 |  | note | INSPECTION BY: Engineer
label | 90a029d3-6e86-5b6c-8cf1-7e857a15d4d5 |  | note | TASK TIMING OR TASK FREQUENCY: Pre pour inspection for each Pour or Foundation
label | 1c59ba3c-ffed-53f2-88f6-8c3b25c46162 |  | note | ACCEPTANCE CRITERIA: Pre pour inspection check sheet
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Pre-pour Insepction Pour-10
label | 24818d02-239b-51a6-9688-4003b28c2819 |  | note | SPECIFICATION REFERENCE: Design / IFC Drawings
label | 9ae1a373-f73b-5f86-a67a-5408cbc15543 |  | note | TEST REQUIRED: Visual Inspection
label | 8d1b4b57-3857-59fb-839b-9673985ba74e |  | note | INSPECTION BY: Engineer
label | f9e0538e-fdb0-50aa-9d88-f4640cf2f38b |  | note | TASK TIMING OR TASK FREQUENCY: Pre pour inspection for each Pour or Foundation
label | ddd6ed73-cf95-5429-8faf-2fa17b019d2f |  | note | ACCEPTANCE CRITERIA: Pre pour inspection check sheet
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Pre-pour Insepction Pour-11
label | 292df658-5b05-5c89-81c3-e890b2784bc2 |  | note | SPECIFICATION REFERENCE: Design / IFC Drawings
label | 960527b0-4e67-56d5-9903-4072d4392840 |  | note | TEST REQUIRED: Visual Inspection
label | 30c1ca2a-8c1f-597a-bf6b-ef880e78413e |  | note | INSPECTION BY: Engineer
label | f3e526f7-53d0-59bd-80ee-0cd7c52b795a |  | note | TASK TIMING OR TASK FREQUENCY: Pre pour inspection for each Pour or Foundation
label | dfae2a6e-29f6-5392-a0de-14a64098b0a5 |  | note | ACCEPTANCE CRITERIA: Pre pour inspection check sheet
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Pre-pour Insepction Pour-12
label | 05d0dd30-e4fd-58d8-8b2a-63f8ab80bc9d |  | note | SPECIFICATION REFERENCE: Design / IFC Drawings
label | 57f48288-8964-5e41-a964-eae456cbe8fb |  | note | TEST REQUIRED: Visual Inspection
label | 8fbaec22-7219-5c84-96f8-6654347821a7 |  | note | INSPECTION BY: Engineer
label | 2da4cc6d-c87b-50d7-8e9b-0194585f3dde |  | note | TASK TIMING OR TASK FREQUENCY: Pre pour inspection for each Pour or Foundation
label | ff41ac2c-2a37-5304-98d3-0e069463cff2 |  | note | ACCEPTANCE CRITERIA: Pre pour inspection check sheet
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Pre-pour Insepction Pour-13
label | dbaea863-d387-5d81-bed7-bc68fc2baffb |  | note | SPECIFICATION REFERENCE: Design / IFC Drawings
label | ce201822-b7af-5d3b-9f72-90e7ccbdc30a |  | note | TEST REQUIRED: Visual Inspection
label | 2490b7d3-b633-5b22-8aca-f00b11198b18 |  | note | INSPECTION BY: Engineer
label | 558e56ef-a3c2-5883-a990-fb55d23cf817 |  | note | TASK TIMING OR TASK FREQUENCY: Pre pour inspection for each Pour or Foundation
label | 36782aa5-e768-575a-89b7-f86eaa9bc897 |  | note | ACCEPTANCE CRITERIA: Pre pour inspection check sheet
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-group |  |  | section | Embeded Items
checkpoint-status |  |  | checkpoint | Embeded Items For Pour-1
label | ba7c551b-cefc-5c4f-b3b2-47bd45f07b15 |  | note | SPECIFICATION REFERENCE: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification. ASNZS5131:2016/ table F3.3/ Item 1 Functional tolerance Class 1
label | b59283f3-a7c6-5d4b-9509-904b83e9fd22 |  | note | TEST REQUIRED: QA Documents and PS4, visual inspection
label | 26cad200-4ecd-5cdf-97ec-bad82664a8f5 |  | note | INSPECTION BY: Engineer/Surveyor
label | 82b846af-26d2-5436-8795-efebefccba64 |  | note | TASK TIMING OR TASK FREQUENCY: For each Embeded item
label | fd31ef95-7ce3-5992-9bb0-cc0b5cec13c4 |  | note | ACCEPTANCE CRITERIA: Embedded Items Install Tolerances Position in plan +/- 10mm Stanchion lengths have been standardized. Level tolerance +/- 20mm, as-built to inform levels for follow up fabrication works.
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Embeded Items For Pour-2
label | aa6f29cd-e5ea-530e-82a0-b815eb174290 |  | note | SPECIFICATION REFERENCE: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification. ASNZS5131:2016/ table F3.3/ Item 1 Functional tolerance Class 2
label | 38dbcaff-15bc-559b-a6a3-a039dbb7e23c |  | note | TEST REQUIRED: QA Documents and PS4, visual inspection
label | 79f4f45f-db5e-5c98-a5a7-d754a8176b9e |  | note | INSPECTION BY: Engineer/Surveyor
label | d56dfdde-5beb-5ec4-909b-6ae8a17beaa0 |  | note | TASK TIMING OR TASK FREQUENCY: For each Embeded item
label | 9fa604e4-259c-5eb7-9198-eafe502f9548 |  | note | ACCEPTANCE CRITERIA: Embedded Items Install Tolerances Position in plan +/- 10mm Stanchion lengths have been standardized. Level tolerance +/- 20mm, as-built to inform levels for follow up fabrication works.
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Embeded Items For Pour-3
label | b62f3f01-8559-51db-91b3-265f2ae8e504 |  | note | SPECIFICATION REFERENCE: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification. ASNZS5131:2016/ table F3.3/ Item 1 Functional tolerance Class 3
label | bb121016-2928-54c8-8f27-d2a8f48c46cb |  | note | TEST REQUIRED: QA Documents and PS4, visual inspection
label | ab25d952-eb0b-5c8e-8423-9ac2e8ab0385 |  | note | INSPECTION BY: Engineer/Surveyor
label | e19d07e5-91a9-5b29-bf5e-3ec74c9439b1 |  | note | TASK TIMING OR TASK FREQUENCY: For each Embeded item
label | 628f922b-70ee-5a13-a7de-cbf2601a4780 |  | note | ACCEPTANCE CRITERIA: Embedded Items Install Tolerances Position in plan +/- 10mm Stanchion lengths have been standardized. Level tolerance +/- 20mm, as-built to inform levels for follow up fabrication works.
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Embeded Items For Pour-4
label | 1e8f914f-240e-5bc8-a996-d1c6a8677c5f |  | note | SPECIFICATION REFERENCE: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification. ASNZS5131:2016/ table F3.3/ Item 1 Functional tolerance Class 4
label | 88416eb8-8bbb-593b-ad66-4440003f2c72 |  | note | TEST REQUIRED: QA Documents and PS4, visual inspection
label | 466481ba-5e8f-508b-98e8-261a213d4e99 |  | note | INSPECTION BY: Engineer/Surveyor
label | 4fb4b3c5-23aa-5c1e-8caa-922fe05f6a8c |  | note | TASK TIMING OR TASK FREQUENCY: For each Embeded item
label | 5b828a9e-3d3b-5848-978d-bc5d51d39f9c |  | note | ACCEPTANCE CRITERIA: Embedded Items Install Tolerances Position in plan +/- 10mm Stanchion lengths have been standardized. Level tolerance +/- 20mm, as-built to inform levels for follow up fabrication works.
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Embeded Items For Pour-5
label | 5386d156-9053-59b4-982a-6bf9a780d75c |  | note | SPECIFICATION REFERENCE: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification. ASNZS5131:2016/ table F3.3/ Item 1 Functional tolerance Class 5
label | fa895b45-64b8-5dc1-a664-714ff796d07d |  | note | TEST REQUIRED: QA Documents and PS4, visual inspection
label | 3c8dd448-f5ed-5fee-9171-d6af6e20f81d |  | note | INSPECTION BY: Engineer/Surveyor
label | bd477b09-d728-5e76-bc8a-bc85ead98688 |  | note | TASK TIMING OR TASK FREQUENCY: For each Embeded item
label | 0e61cfdc-2dba-5223-9ac1-faffca84c017 |  | note | ACCEPTANCE CRITERIA: Embedded Items Install Tolerances Position in plan +/- 10mm Stanchion lengths have been standardized. Level tolerance +/- 20mm, as-built to inform levels for follow up fabrication works.
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Embeded Items For Pour-6
label | 6bd84a87-a8f5-5068-8d30-85d6e973a5b7 |  | note | SPECIFICATION REFERENCE: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification. ASNZS5131:2016/ table F3.3/ Item 1 Functional tolerance Class 6
label | 00f63567-4d3d-54d9-8fbf-d23c1d0976dd |  | note | TEST REQUIRED: QA Documents and PS4, visual inspection
label | 2fcb8a45-01b6-5336-b6e1-f93772a8e6d1 |  | note | INSPECTION BY: Engineer/Surveyor
label | 0b4ad170-bc92-52a3-84c5-c87fe1732bac |  | note | TASK TIMING OR TASK FREQUENCY: For each Embeded item
label | 87af46cb-88c9-5303-817a-a89b4a442e80 |  | note | ACCEPTANCE CRITERIA: Embedded Items Install Tolerances Position in plan +/- 10mm Stanchion lengths have been standardized. Level tolerance +/- 20mm, as-built to inform levels for follow up fabrication works.
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Embeded Items For Pour-7
label | 17ef834f-1895-5019-a08d-1e1ddf486f25 |  | note | SPECIFICATION REFERENCE: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification. ASNZS5131:2016/ table F3.3/ Item 1 Functional tolerance Class 7
label | 71c3ff2c-6420-5e76-89c1-c1c8db891f7d |  | note | TEST REQUIRED: QA Documents and PS4, visual inspection
label | ce389bb3-52ba-511d-bfe7-4d833a0e6f75 |  | note | INSPECTION BY: Engineer/Surveyor
label | ba06a310-71eb-57cf-89bb-ee6529a97f38 |  | note | TASK TIMING OR TASK FREQUENCY: For each Embeded item
label | 7670fc39-e4a7-588d-b4c8-1450ad1dbad0 |  | note | ACCEPTANCE CRITERIA: Embedded Items Install Tolerances Position in plan +/- 10mm Stanchion lengths have been standardized. Level tolerance +/- 20mm, as-built to inform levels for follow up fabrication works.
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Embeded Items For Pour-8
label | d96bb6b4-17c2-5356-9931-204d9e68b35c |  | note | SPECIFICATION REFERENCE: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification. ASNZS5131:2016/ table F3.3/ Item 1 Functional tolerance Class 8
label | 84416ec9-250f-535f-b539-cb42c8715247 |  | note | TEST REQUIRED: QA Documents and PS4, visual inspection
label | 5cef9a85-33df-5d81-bc42-391b7fe262c8 |  | note | INSPECTION BY: Engineer/Surveyor
label | 3f21676f-2986-58ad-8de6-73d21a7c7607 |  | note | TASK TIMING OR TASK FREQUENCY: For each Embeded item
label | 77ed392b-9434-5339-88f8-0288fd8f20c0 |  | note | ACCEPTANCE CRITERIA: Embedded Items Install Tolerances Position in plan +/- 10mm Stanchion lengths have been standardized. Level tolerance +/- 20mm, as-built to inform levels for follow up fabrication works.
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Embeded Items For Pour-9
label | 1448ef5a-4c07-596f-98cd-8857ed58f8f3 |  | note | SPECIFICATION REFERENCE: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification. ASNZS5131:2016/ table F3.3/ Item 1 Functional tolerance Class 9
label | 99ec8a78-31ac-5abc-817f-81475ce6f777 |  | note | TEST REQUIRED: QA Documents and PS4, visual inspection
label | 3b384be5-2a8d-5ec2-9144-286e05bb81f8 |  | note | INSPECTION BY: Engineer/Surveyor
label | 8ac5dc97-36d4-53d8-9a52-388766330b0c |  | note | TASK TIMING OR TASK FREQUENCY: For each Embeded item
label | 47809677-2f86-573f-9902-9251454e3063 |  | note | ACCEPTANCE CRITERIA: Embedded Items Install Tolerances Position in plan +/- 10mm Stanchion lengths have been standardized. Level tolerance +/- 20mm, as-built to inform levels for follow up fabrication works.
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Embeded Items For Pour-10
label | edeee5fc-1e2b-520c-8291-20db16d2a06e |  | note | SPECIFICATION REFERENCE: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification. ASNZS5131:2016/ table F3.3/ Item 1 Functional tolerance Class 10
label | 205f2979-62da-50e0-961e-145364edf53a |  | note | TEST REQUIRED: QA Documents and PS4, visual inspection
label | cfcc3746-6753-5800-ab46-4123ab695df7 |  | note | INSPECTION BY: Engineer/Surveyor
label | 826c030a-21c0-50eb-92cc-03b27e510fe9 |  | note | TASK TIMING OR TASK FREQUENCY: For each Embeded item
label | 3e05d057-1ae4-5e06-a3b0-e2258f7678e9 |  | note | ACCEPTANCE CRITERIA: Embedded Items Install Tolerances Position in plan +/- 10mm Stanchion lengths have been standardized. Level tolerance +/- 20mm, as-built to inform levels for follow up fabrication works.
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Embeded Items For Pour-11
label | 57e333bf-4115-59fd-b1ed-12b6da1af508 |  | note | SPECIFICATION REFERENCE: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification. ASNZS5131:2016/ table F3.3/ Item 1 Functional tolerance Class 11
label | 353ccad2-72f1-55dd-a82d-f08201338bab |  | note | TEST REQUIRED: QA Documents and PS4, visual inspection
label | 5dfc2c24-86d7-5980-8b27-86c5d65034e8 |  | note | INSPECTION BY: Engineer/Surveyor
label | f9b4377f-6509-5e32-bd2c-64a6b13e4c3f |  | note | TASK TIMING OR TASK FREQUENCY: For each Embeded item
label | ed0e4ddb-55db-54fb-add4-7612e61639f9 |  | note | ACCEPTANCE CRITERIA: Embedded Items Install Tolerances Position in plan +/- 10mm Stanchion lengths have been standardized. Level tolerance +/- 20mm, as-built to inform levels for follow up fabrication works.
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Embeded Items For Pour-12
label | e846dbf1-abaa-55bc-a220-7e626b884814 |  | note | SPECIFICATION REFERENCE: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification. ASNZS5131:2016/ table F3.3/ Item 1 Functional tolerance Class 12
label | a8b4e016-9ad2-5dd5-9ec7-6a803a6fd3c0 |  | note | TEST REQUIRED: QA Documents and PS4, visual inspection
label | 2c832bfa-ba0e-59c2-afed-340f9043cc66 |  | note | INSPECTION BY: Engineer/Surveyor
label | de9fb41b-5c91-528e-937c-acccb1e251c9 |  | note | TASK TIMING OR TASK FREQUENCY: For each Embeded item
label | 6c60d3e7-133d-5b6f-96b1-42b5339916a0 |  | note | ACCEPTANCE CRITERIA: Embedded Items Install Tolerances Position in plan +/- 10mm Stanchion lengths have been standardized. Level tolerance +/- 20mm, as-built to inform levels for follow up fabrication works.
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Embeded Items For Pour-13
label | 63551d8c-a659-54f0-87cf-4a73de13ccc7 |  | note | SPECIFICATION REFERENCE: TABG-JEC-0-000-STR-SPC-7500-B Structural Specification. ASNZS5131:2016/ table F3.3/ Item 1 Functional tolerance Class 13
label | 5ace6127-ce5d-552d-8300-451aded06d85 |  | note | TEST REQUIRED: QA Documents and PS4, visual inspection
label | a8ba49dd-dd66-5208-ba17-2cd5597b6198 |  | note | INSPECTION BY: Engineer/Surveyor
label | fcf0fd0f-f206-5adb-aca9-3548934f6b62 |  | note | TASK TIMING OR TASK FREQUENCY: For each Embeded item
label | c50ccb31-22ab-5a35-b778-81fdf670d034 |  | note | ACCEPTANCE CRITERIA: Embedded Items Install Tolerances Position in plan +/- 10mm Stanchion lengths have been standardized. Level tolerance +/- 20mm, as-built to inform levels for follow up fabrication works.
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-group |  |  | section | Backfilling of Foundations
checkpoint-status |  |  | checkpoint | Backfill
label | edc8fc0a-973e-5cd5-bc6f-af5d78249ce3 |  | note | SPECIFICATION REFERENCE: Design / IFC Drawings
label | 61e985bb-70a6-5d46-9862-d6319572373d |  | note | TEST REQUIRED: Visual Inspection
label | d10deb03-7d20-5356-87f7-d10bf3cc63d0 |  | note | INSPECTION BY: Enginner
label | a21c342d-41ed-5b8d-b7e4-bcb77740a055 |  | note | TASK TIMING OR TASK FREQUENCY:
label | 33eea054-589d-5c0f-8b2f-577d5e083346 |  | note | ACCEPTANCE CRITERIA: Plate compact backfill material around foundations
checkpoint-group |  |  | section | Post Construction
checkpoint-status |  |  | checkpoint | As Built & Final Design Documentation
label | adcb15a2-3a44-5696-9514-da7d73a93819 |  | note | TEST REQUIRED: Surveying
label | 7cf28a3f-e0a2-5adf-9a2f-fac60eb18c7f |  | note | INSPECTION BY: UCCL
label | 13ec2c67-cb41-54c6-97ea-4decce93c872 |  | note | TASK TIMING OR TASK FREQUENCY: For each Pour
label | 18c56bdc-68d1-5589-af20-6c614ff05da4 |  | note | ACCEPTANCE CRITERIA: Confirmation From Engineer on as built records & redline mark ups
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Completion Inspection inc. Construction Defects Report
label | d08de670-d82e-5944-80ac-fe76f39f96ee |  | note | TEST REQUIRED: Completion inspection on the structure by CEL
label | 251965e1-747e-5a6f-aeca-1394b0467da7 |  | note | INSPECTION BY: CEL/ UCCL
label | 3349579c-7f17-5d7e-a45f-64a4ef575ef9 |  | note | TASK TIMING OR TASK FREQUENCY: For each structure
label | f1805920-8ea4-519c-8731-2aaec9bf5571 |  | note | ACCEPTANCE CRITERIA: Provided a completed construction defect report that that details any remedial measure taken, snag lists closed out
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checklist-sectioned |  |  | checklist | ITP - Piling | itp |  |  |  | Yes | ITP - Piling | e51be483-0e91-4e50-a429-b3fd19473b93
checkpoint-group |  |  | section | Preliminary
checkpoint-status |  |  | checkpoint | Acceptable Method Statement
label | 27860f24-c564-51da-92f1-9e671b39104e |  | note | Specification Reference: TABG-JEC-0-000-STR- SPC-0004(B) Bored Pile Specification and IFC Drawings
label | aca5eda0-426b-57d9-a383-150f4315353d |  | note | Task Timing or Task Frequency: Once Prior to commencement of piling
label | 7465a2ec-f734-50e1-9b34-9896e42964e5 |  | note | Acceptance Criteria: Approved Method statement document
label | f5ac7d84-1d53-5044-aac1-4dbe3705bbe4 |  | note | CLL: H
label | 2e6b0e0d-05dd-5aa5-bf64-bc0f557ba31c |  | note | UCLL: R
label | e8489425-2510-5527-9b64-9be9967219b2 |  | note | Client: R/A
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Concrete Design Mix Verification
label | 722f1d83-87a9-59fe-965d-fc446972a460 |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-0004(B) Bored Pile Specification
label | 42fd79c9-27df-517b-9202-06a4fd80d603 |  | note | Task Timing or Task Frequency: Once Prior to commencement of piling
label | 3a1d7c59-5d4e-5d3d-994b-db0c2e76c44c |  | note | Acceptance Criteria: Approved by Engineer
label | 7b186afe-aefe-56fd-93c3-15263be63ea5 |  | note | CLL: H
label | 39f69211-a91c-5286-a9d7-068d21969432 |  | note | UCLL: R
label | ea955312-d5d8-57e2-b452-36caa895b3f1 |  | note | Client: R/A
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Supply of Reinforcement - Steel reinforcement compliance records
label | 8e05913f-acfb-5248-98da-41d37bd8620b |  | note | Specification Reference: TABG-JEC-0-000-STR-SPC-0004(B) Bored Pile Specification
label | d8e3f372-4485-5640-88f7-b607332c13db |  | note | Test Required: Schedules shall be prepared by the supplier and reviewed
label | 7ad32846-669c-5251-8586-4ad9611794e6 |  | note | Inspection By: Engineer
label | 887c6c0e-65d2-512a-bfe6-b593ca49c9a9 |  | note | Task Timing or Task Frequency: Prior to manufacturing any reinforcement
label | 40b79a73-957b-582d-848a-da5a059f0a8f |  | note | Acceptance Criteria: Manufacturer´s Mill Certificate/Rebar schedule/Rebar summary sheet
label | 251919bd-1fc8-5d5e-ae3e-173b4fdfd39f |  | note | CLL: H
label | 62a074a4-a662-5e55-8ae4-f30f353a2bed |  | note | UCLL: R
label | eda41ae4-2bfc-5b6c-9528-8ef54e8750ad |  | note | Client: R
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-group |  |  | section | Pile Boring
checkpoint-status |  |  | checkpoint | Pile Location
label | 2ba31798-1315-591f-872f-993ecd0a0ce6 |  | note | Specification Reference: Jacobs Technical requirements: For Bored Piles
label | 3e8baaff-3d0d-503b-ae0c-f65187c106cb |  | note | Test Required: Survey record
label | 981ea484-1cab-5e36-b0f2-dd40648e43f0 |  | note | Inspection By: Surveyor
label | 651ea24e-9c33-5d91-bf86-92330f2138fb |  | note | Task Timing or Task Frequency: Every Pile
label | 47711e60-6971-5ff6-8c34-c38404527802 |  | note | Acceptance Criteria: Hz +/-75mm Vt +/- 25mm
label | eb84a298-a113-5be5-8b81-4307b32667c0 |  | note | CLL: H/V
label | 33d8739a-9df5-5cd8-9af7-3c128974221d |  | note | UCLL: R
label | 75985160-131e-536a-87c4-730e912ddda4 |  | note | Client: R
checkpoint-status |  |  | checkpoint | Drill Tool Diameter
label | a730cf72-d650-543d-922f-287d8760b458 |  | note | Specification Reference: Visual
label | d660645e-5abd-5004-b1d9-d34ce3973e16 |  | note | Test Required: QAC Pile Card
label | dbf5920c-899f-5d34-90f1-77e13233e137 |  | note | Inspection By: CLL
label | 6b168b9d-9b30-53b2-8143-b4a467794962 |  | note | Task Timing or Task Frequency: Start of project
label | b07e2379-f3b1-5dee-9493-2cfba522983f |  | note | Acceptance Criteria: Design
label | 861e5e86-e63c-5c86-a044-87042a2b32bf |  | note | CLL: H
label | 200a2762-a4ea-5a66-8a42-feab703dcde5 |  | note | UCLL: R
label | 2d2ce740-14fb-5ab4-ab44-28787afa3904 |  | note | Client: R
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Verticality
label | 94f46270-0ed0-55ec-986c-8809536e37e8 |  | note | Specification Reference: Jacobs Technical requirements: For Bored Piles
label | 33ec3aaa-4b5f-5491-8dec-2ab4983ebfe6 |  | note | Test Required: QAC Pile Card
label | 4d40943c-6ae3-572f-b429-85f6e5127f61 |  | note | Inspection By: CLL
label | 9cb3ea51-90df-5a82-b9f3-09b99a02ecd6 |  | note | Task Timing or Task Frequency: As per QAC requirements
label | 36dcd653-c1f4-5acb-8a3c-150b04931cf7 |  | note | Acceptance Criteria: Vertical alignment <1:75 from design
label | a34232af-4a6b-5a86-9b29-1554f25a9fcc |  | note | CLL: R
label | 53c1d2d9-01be-5d8c-a09a-8b9ddbbedf68 |  | note | UCLL: W
label | 18e47085-7686-5138-b0c6-84b5aea52350 |  | note | Client: R
checkpoint-status |  |  | checkpoint | Casing Inspection
label | 264fbe7b-053c-5912-ad4f-5bb679534458 |  | note | Specification Reference:
label | 50aa03de-ddd9-5179-9949-450cfc24b3cb |  | note | Test Required: QAC Pile Card
label | 56fee3b7-3645-5b6d-aadf-b36d02d89f00 |  | note | Inspection By: CLL
label | 7ec7aabd-190e-5d32-b431-478228815bba |  | note | Task Timing or Task Frequency: Start of project
label | e8df2940-365e-52cf-a58e-f7d851b52418 |  | note | Acceptance Criteria: Visual
label | fcad353e-d0b1-5246-814e-c1df1a0d207e |  | note | CLL: H
label | c2507c1f-bd54-5e91-88eb-9d685b810ea4 |  | note | UCLL: W
label | f86f0660-1d5f-5221-866f-6d6c25a0bc3f |  | note | Client: R
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Bore size
label | 1c25fea7-a3ec-59f9-a6b0-9b15e0e62edf |  | note | Specification Reference: Jacobs Technical requirements: For Bored Piles
label | a65a71ad-2238-546b-aee9-08d945167ec4 |  | note | Test Required: QAC Pile Card
label | 3820a820-bf93-5b22-9048-bd2f1b7f473e |  | note | Inspection By: CLL
label | 02b456c0-93a1-55e9-8929-e419a9cfa5cf |  | note | Acceptance Criteria: ≥ specified diameter
label | 7d38f14b-fea2-526a-b04b-f2a3c54ea3cd |  | note | CLL: H
label | 3cdb99fb-dd96-5797-b4b0-b9f09840b254 |  | note | UCLL: W
label | b416af43-1e4f-5acd-bb94-bf4cce78b861 |  | note | Client: R
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-group |  |  | section | Concrete Placement
checkpoint-status |  |  | checkpoint | Verify Concrete Mix
label | e550dcf6-b66f-58e6-b592-0d7daeb00957 |  | note | Specification Reference: Jacobs Structural Specification
label | 08cbfba3-1902-550d-83aa-e320fe759165 |  | note | Test Required: Concrete Ticket
label | 95082c50-99b4-5e3a-ba06-2d96c0389cc6 |  | note | Inspection By: CLL
label | 8a360466-88e7-5fbb-99cb-0a68fe48debb |  | note | Task Timing or Task Frequency: Each delivery
label | 442cd011-97e4-5801-bfb3-d5851d51ab71 |  | note | Acceptance Criteria: Approved Mix Design
label | df23e776-a5cf-5934-ab5e-879c4523814e |  | note | CLL: H
label | 37af08cf-ba12-505c-b7b8-48f065c2c44a |  | note | UCLL: W
label | c185102a-3e45-5984-984a-41ccc3bba0b9 |  | note | Client: W
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Concrete level
label | e9e4fabd-7006-5d12-9f2c-dccb7ba09870 |  | note | Specification Reference: Jacobs Structural Specification
label | 72dcd4a0-08f6-56bd-a71e-1e5696f90521 |  | note | Test Required: QAC Pile Card
label | 78c4089d-e1f2-524a-9489-890e1828e63f |  | note | Inspection By: CLL
label | 4dcade30-3232-5dd4-bc7c-e5179756f671 |  | note | Task Timing or Task Frequency: Every Pile, United Civil at commencement of project on the first pile/piles
label | 4b7de410-ca38-5a8e-98f9-e6967aa965ba |  | note | Acceptance Criteria: Design +50mm
label | 105e007d-fb28-512e-b5cf-81a63ad5f2e7 |  | note | CLL: H
label | 9defffc5-3bda-565f-b5b7-dde2848ed0c2 |  | note | UCLL: W
label | d0beaa93-09f8-590f-8858-8c18b1fe96eb |  | note | Client: W
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Concrete pouring
label | 34f0dea2-604a-51e5-9e7f-20430ccc7b28 |  | note | Specification Reference: Jacobs Technical requirements: For Bored Piles Jacobs Structural Specification
label | 3d41175a-148e-597b-8f18-a95d58d632dd |  | note | Test Required: QAC Pile Card
label | f3a835c2-eaa6-5f31-85d7-47f66d3bf1d4 |  | note | Inspection By: CLL
label | d5f5bace-c02c-58cb-804d-50b281a4298d |  | note | Task Timing or Task Frequency: Every Pile, United Civil at commencement of project on the first pile/piles
label | b9981263-ebf1-5bd6-a77b-709fe955c7b8 |  | note | Acceptance Criteria: Tremie as required
label | b5f2d431-386c-540a-9fa9-8aa107d69dcf |  | note | UCLL: R
label | 098f7947-6d57-51cd-be8d-29fc18434532 |  | note | Client: R
checkpoint-status |  |  | checkpoint | Compressive Strength Sampling
label | 7e77c1dd-b30c-5a6e-a7ec-a0fd64514473 |  | note | Specification Reference: OTR
label | 3442fb2c-1dd5-5f0c-8e10-37f53f267284 |  | note | Test Required: Lab.Test Record
label | 2a85585c-7af5-5556-a000-73b79cfa9222 |  | note | Inspection By: IANZ Accredited Lab
label | 03cdd1c9-4ff4-5500-920e-36c29f523e7a |  | note | Task Timing or Task Frequency: As per NZS 3104
label | d2f993da-e3d1-5198-8b66-bd4b182b51a2 |  | note | Acceptance Criteria: 28 day - 30MPa
label | d82deaba-2908-56f1-a87e-dbe9d73ea13d |  | note | CLL: R
label | bdac80c9-1b7d-5090-834c-e8847a143bee |  | note | UCLL: R
label | 8f0c900e-1550-5552-86fa-b3e4da220b8a |  | note | Client: R
checkpoint-status |  |  | checkpoint | Compressive Strength Sampling (1)
label | 13f3e9b8-f55e-5959-a3f9-a16cda941f65 |  | note | Specification Reference: NZS 3104 Jacobs Structural Specification
label | 709683c0-38a7-53b6-ad90-cf04e0e221d9 |  | note | Test Required: Lab. Test Record
label | 5f843341-ac20-5412-9cbe-da61e245f93a |  | note | Inspection By: IANZ Accredited Lab
label | f5e55155-d943-5f8f-b7db-589deb317f15 |  | note | Task Timing or Task Frequency: Daily on-site testing for each concrete pour for each 50 m3 or pt. thereof
label | a8c8d722-6bcb-5b4c-b86d-0e20ac7942d8 |  | note | Acceptance Criteria: 28 Day - 30MPa
label | 99f53767-5a55-5eac-8ff5-64ae03e27e82 |  | note | CLL: H
label | fc3e2b2e-c6d5-5ef6-89e9-2f83cd681d0d |  | note | UCLL: R
label | b23c8234-ab66-53aa-b324-912c52a901ae |  | note | Client: R
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Slump/spread test
label | f55cfc4c-fa45-577c-b2a9-001ed93e0050 |  | note | Specification Reference: Jacobs Structural Specification NZS 3109
label | 1971937c-43f8-55ef-94eb-ddf18b7cdab1 |  | note | Test Required: QAC Pile Card
label | 98855ebf-ebf3-5a79-96ae-c5309f2d9458 |  | note | Inspection By: IANZ Accredited Lab
label | 6ecc1509-0051-5716-a6fe-2b1f9c6b9f29 |  | note | Task Timing or Task Frequency: At same time as on-site compressive test sampling
label | 2c40642b-8c1e-597e-8e81-195c07feb7d7 |  | note | Acceptance Criteria: TBC
label | f621db81-5c93-558c-a140-3ee05496ae1d |  | note | CLL: H
label | 847628ff-fe89-5aef-844f-6a17d3188ec3 |  | note | UCLL: R
label | 04c4731b-8ce9-528b-9521-f460507cd109 |  | note | Client: R
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-group |  |  | section | Post-Construction Testing
checkpoint-status |  |  | checkpoint | Pile Dynamic Analysis
checkpoint-status |  |  | checkpoint | Pile Integrity Testing
checkpoint-group |  |  | section | Post Construction
checkpoint-status |  |  | checkpoint | As Built & Final Design Documentation
label | 75a4fa84-326d-5b17-ac0e-112f76129ef5 |  | note | Test Required: Surveying
label | 1260f883-c6c4-5da8-a59d-bd39a429465f |  | note | Inspection By: UCCL
label | c84422bf-836c-5ef9-8052-1f9d342756ca |  | note | Task Timing or Task Frequency: For each Pour
label | 3d902c29-d867-53da-b4a0-46218646a7c0 |  | note | Acceptance Criteria: Confirmation From Engineer on as built records & redline mark ups
label | 733a69d2-6398-5bd9-8a6d-66639a4a427f |  | note | UCLL: H
label | 9e9a92f8-369b-5038-8652-cb07c758fc19 |  | note | Client: R
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checkpoint-status |  |  | checkpoint | Completion Inspection inc. Construction Defects Report
label | 994a2c13-1dc9-5352-ad9b-c2740a9530b8 |  | note | Test Required: Completion inspection on the structure by CEL
label | bc41d6ca-bcc6-5d86-a6a2-1617dfdbde62 |  | note | Inspection By: CEL/ UCCL
label | 021f5a52-6365-598c-992c-ea5caeb303f6 |  | note | Task Timing or Task Frequency: For each structure
label | 7404da66-44d1-5961-95c7-12d49c99f5a5 |  | note | Acceptance Criteria: Provided a completed construction defect report that that details any remedial measure taken, snag lists closed out
label | 141f2497-4b54-551b-8359-0db535d34af0 |  | note | UCLL: H
holdpoint |  |  | signoff | HOLD POINT AUTHORITY
checklist-sectioned |  |  | checklist | ITP - Process Drains | itp |  |  |  | Yes | ITP - Process Drains | f4f1c566-337f-4528-9483-625ed1dad24b
checkpoint-group |  |  | section | Preliminary
checkpoint-status |  |  | checkpoint | Material Supply - Precast Concrete U Channels & Lids
label | 64f805a4-38f0-5786-af1b-f58801f74dd2 |  | note | Specification Reference - TABG-JEC-0-000-STR-SPC-7500-B Structural Specification
label | d52873a0-b59f-5576-a18f-5763bcf217ff |  | note | Test Required - Producer statement
label | a63196bb-2ef9-5fdc-9105-d4f4c0434dd0 |  | note | Inspection By - UCCL
label | f7d5e7ed-e254-5cdf-bd7d-9504dd15e07d |  | note | Task Timing Or Task Frequency - Prior to Installation
checkpoint-status |  |  | checkpoint | Supply of Reinforcement - Steel reinforcement compliance records (stitches & bases)
label | 3287278e-5dc8-57ba-9872-b09a56c6914e |  | note | Specification Reference - TABG-JEC-0-000-STR-SPC-7500-B Structural Specification - STEEL REINFORCEMENT COMPLIANCE 6.1.7
label | 74e810c3-c225-59e7-9fd6-3f52a57318b1 |  | note | Test Required - Schedules shall be prepared by the supplier and reviewed/ accepted by CEL prior to fabrication.
label | 5b43e071-b36f-5b3b-9ca6-d69b3fb1f213 |  | note | Inspection By - UCCL
label | 74272bf6-0390-5fc5-8218-94cfd07a2f49 |  | note | Task Timing Or Task Frequency - Each batch of reinforcing supplied
checkpoint-status |  |  | checkpoint | Supply of steel grates
label | 0f7c06eb-81d9-53bb-a6cb-cc1ecfa08123 |  | note | Specification Reference - TABG-JEC-0-000-STR-SPC-7500-B Structural Specification - 18.3.4 Steelwork being galvanized
label | 66fc54c9-e798-51f0-8205-7f604ee61a06 |  | note | Test Required - Galvanizing certs
label | ce2fcdda-a09d-550e-985d-57ce7b01db62 |  | note | Inspection By - UCCL
label | 8839faca-1051-5909-a1aa-4075a8a53063 |  | note | Task Timing Or Task Frequency - For all grating supplied
checkpoint-group |  |  | section | Process Drain - Construction
checkpoint-status |  |  | checkpoint | Setout of trench
label | ab243eab-09fc-51df-acf3-233c773b9ee7 |  | note | Specification Reference - As per IFC Drawings and approved CAD files
label | 07a34f84-99c0-5d19-a3b2-2f14ea19dafd |  | note | Test Required - Surveying
label | aa1fa9a8-89dd-587a-a1a3-ff2906223add |  | note | Inspection By - Surveyor
label | cf1d5bb6-a066-52df-8621-0fc255eb15cc |  | note | Task Timing Or Task Frequency - For set out of each trench line.
checkpoint-status |  |  | checkpoint | Excavation/ Subgrade
label | 0ab1134c-c9a8-58c9-8e35-7030bc0a6e82 |  | note | Specification Reference - As per IFC Drawings
label | 83a40313-a93d-5c21-9633-d3ddbfe9b36b |  | note | Test Required - Scala tests
label | c8bf2a50-9755-5839-a404-423879efbb15 |  | note | Inspection By - UCCL
label | b5236fc2-9a21-573d-a1ff-6dbc34655922 |  | note | Task Timing Or Task Frequency - 1 test every 50m on each line of process drain to be installed
checkpoint-status |  |  | checkpoint | Bedding, Site Concrete
label | 19c709a5-7342-5430-8d54-0a7a3f14a62a |  | note | Specification Reference - TABG-JEC-0-000-GCV-DET-0032
label | baa0a212-d749-5f44-98ab-a32d8524b3fd |  | note | Test Required - Refer Cross sections
label | 2c6d2a59-0846-5b87-a9c3-5e6444d435d9 |  | note | Inspection By - UCCL
label | 6ca77263-4223-5f3a-969e-6b0a6a7c8780 |  | note | Task Timing Or Task Frequency - Beneath all U Channels
checkpoint-status |  |  | checkpoint | Installation of U Channels
label | 7977ca25-5bf9-58e3-8294-b73910af51ee |  | note | Specification Reference - TABG-JEC-0-000-GCV-DET-0032
label | 006380c9-4f87-5753-8bbe-4efb6e907133 |  | note | Test Required - Pre-pour survey Concrete compressive strength reports
label | e653938b-7cdd-5a60-b179-2dc7c3051d3f |  | note | Inspection By - UCCL
label | 86711431-c118-5694-a373-a21df28b2bba |  | note | Task Timing Or Task Frequency - Prior to pouring the base and stitchs of any section of channel
checkpoint-status |  |  | checkpoint | In-situ Joints
label | 513f833a-e594-5355-b90f-2b9e55a56587 |  | note | Specification Reference - TABG-JEC-0-000-GCV-DET-0032 GA Shop drawings
label | 7f86006f-9ccc-5b47-9146-39e3b14c6a09 |  | note | Test Required - Visual Inspection Concrete compressive strength reports
label | 0b20357f-0fe4-57c2-a2ba-2ccbcb817671 |  | note | Inspection By - UCCL
label | ca521c50-7b7b-5520-8246-a78875d77aec |  | note | Task Timing Or Task Frequency - Each Stitch
checkpoint-status |  |  | checkpoint | Invert Pour
label | 353cd0b3-3d55-5ecf-8e34-fbd7a45825a3 |  | note | Specification Reference - TABG-JEC-0-000-GCV-DET-0032 GA Shop drawings
label | 726768a0-709b-5bca-a22f-fac38f453df4 |  | note | Test Required - Visual Inspection, Concrete compressive strength reports
label | 7ef62ed7-d408-509a-a297-819e7af79139 |  | note | Inspection By - UCCL
label | b15fc6ae-dfba-5f5e-9107-f872870e5a85 |  | note | Task Timing Or Task Frequency - Each Line of process drain invert
checkpoint-status |  |  | checkpoint | Joint Sealant
label | 9d41c6d2-c6c2-5b0e-ae92-e21a9a56eb0f |  | note | Specification Reference - TABG-JEC-0-000-GCV-DET-0032 GA Shop drawings
label | ad428299-2df7-5d7c-8753-73ebbfffca44 |  | note | Test Required - Visual Inspection
label | 5eaf1203-cdc1-51ca-ba96-72d69ddc830b |  | note | Inspection By - UCCL
label | c2dd502d-a79f-5f70-9e0d-16f0003047c4 |  | note | Task Timing Or Task Frequency - Each crack control joint
checkpoint-status |  |  | checkpoint | Compaction/Backfill of channels
label | 802dc305-479c-5fc5-a586-9910411c5600 |  | note | Specification Reference - TABG-JEC-0-000-GCV-SPC-0002-B_-CIVIL AND GEOTECHNICAL PROJECT SP Section 7.10.7
label | b3b30203-64a5-5ffc-810b-3177d0f7b16b |  | note | Test Required - Track rolling with excavator
label | 43e1368a-7e84-5d91-96d9-efae49e2fb19 |  | note | Inspection By - UCCL
label | b402e73f-9cfe-5155-936b-9dde83c7c922 |  | note | Task Timing Or Task Frequency - All process drain lines
checkpoint-status |  |  | checkpoint | Embedded items
label | 4b24c2c9-ca2a-571b-8d8f-78f0dfd56677 |  | note | Specification Reference - TABG-JEC-0-ULG-STR-DET-3165 - Detail 2
label | 7196982d-b3e8-59c7-ad1c-d644a3773a7c |  | note | Test Required - Visual Inspection
label | 341a2f1d-7647-5610-a637-053f272f75a1 |  | note | Inspection By - UCCL
label | 8bedefbd-8780-5bd7-8f68-03e9c2eae291 |  | note | Task Timing Or Task Frequency - Pipes connecting to the rock muffler sumps
checkpoint-status |  |  | checkpoint | Lid & Grate installation
label | a36277f3-0fb7-57f4-b23a-107ecfc1b253 |  | note | Specification Reference - TABG-JEC-0-000-GCV-DET-0032 GA Shop drawings
label | 5aeb3f30-bc6b-5bee-9e11-d1d6ac927913 |  | note | Test Required - Visual Inspection
label | b0929fce-ebe7-5826-8c20-6084d8103287 |  | note | Inspection By - UCCL
label | af642034-d516-5af6-be68-f26b5a91eb6a |  | note | Task Timing Or Task Frequency - All concrete lids & steel grates
checkpoint-group |  |  | section | Post Construction
checkpoint-status |  |  | checkpoint | As Built & Final Design Documentation
label | c0fbc4bf-de16-5758-b41e-be1569620c52 |  | note | Test Required - Surveying
label | bfa685f2-045b-5256-bfe8-3cae17291833 |  | note | Inspection By - UCCL
label | 7addd8a4-c5ff-59c4-81de-5060c83a67a4 |  | note | Task Timing Or Task Frequency - For each PD Line
checkpoint-status |  |  | checkpoint | Completion Inspection inc. Construction Defects Report
label | 3a9cdfe6-7818-5690-b534-deb57cdd8cba |  | note | Test Required - Completion inspection on the Each PD Line by CEL
label | 9c320de1-3864-5a0f-84ed-23cf5f32a7fe |  | note | Inspection By - CEL/ UCCL
label | d09f2737-3e29-5212-800f-b3e38e606f49 |  | note | Task Timing Or Task Frequency - For each PD Line