## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
d283b807-9e86-5a16-aeaf-e1270fc28892 | checklist | ITP-0001 - DI Watermain | itp | ITP-0001 - DI Watermain
2ac8716a-63b3-52cf-b624-07c24c0cd6c9 | section | SECTION 3 - RECEIVING INSPECTIONS
2d6469ff-22e7-5477-8cef-d23cbae25acd | checkpoint | 3.1 - Material Delivery
95f0052a-c399-5b13-b0b9-382fd441a454 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
70dfd956-df25-5b7f-86f0-7193b5662c5f | note | Acceptance Criteria - DI Pipes shall be DN150 PN35 with cement mortar or concrete lining
dcb55c98-9f9d-58ec-ade2-b287fbeeb0f0 | note | ○ Material and fittings are approved as per contract specification
1e329314-d334-5eac-ac9e-6cb29ff28813 | note | Verifying Document - Photos, delivery docket, MDD results for backfill materials
6a900a08-cf3a-5a34-986b-8d6abbd14ea0 | note | Frequency - On Delivery
8fc40037-93e4-5baf-b841-9b67d77c2c6d | note | Inspection Type (Visual, other) - Visual
807e8f18-403e-57d4-aa8b-df95aa6912b4 | note | Inspection: Key - C
8f6dbf2f-9f4d-514f-ae80-57151c1d03ae | checkpoint | 3.2 - Set out
299af1f6-b465-5cf7-837b-e19ce4fc81d1 | note | Inspection Point: Quality Control Activity - Allignment set out completed by an approved surveyor marked allignment
314918e2-3f45-55aa-8f18-6e5e59f44ed0 | note | Acceptance Criteria - Set out matches drawings, 2D data and linework provided or aggreed with the Engineer
e44535bb-5a5b-5708-8ccc-9e5e4c02dbbe | note | Verifying Document - Survey marks, photos
cb3c9eea-9691-54df-b7ba-490d3f53f66c | note | Frequency - Prior to commencement of works
3bfa345e-a230-5232-aa4e-aff9d673994b | note | Inspection Type (Visual, other) - Visual, Instrumental
9433c7f8-1e69-50c6-9616-f12667fdc477 | note | Inspection: Key - H
57e25cdc-0d38-5a66-a6ee-bd14e8463cf5 | signoff | HOLD POINT
1d1078e0-1bb1-56f7-948a-752012ad998c | section | SECTION 4 - IN-PROCESS INSPECTIONS
c5f206b2-b8d9-55e2-a96f-c1168acbd237 | checkpoint | 4.1 - Trench Excavation
59010ff7-a58b-5930-a62f-f7f1aee9fefc | note | Inspection Point: Quality Control Activity - Excavate to acheive required depth to invert as per drawing C4500
7b767845-458a-5cf4-9389-5d9975f8ab65 | note | ○ Floor of trench to be even across width and length
f027339a-c927-5cae-a105-e737961ad5c9 | note | Acceptance Criteria - Allow 100mm for bedding
48b68b52-d794-5a42-b9be-298f7bb284fa | note | ○ Allow for minimum cover of 750mm. Max cover not exceeding 1000mm unless shown on Drawings C4500
81016198-c266-5a3e-aefb-51cf2e8133a4 | note | Verifying Document - Photos
fa9aff56-159a-53fb-a2a3-8cbfa9603454 | note | Frequency - During Installation
4d5a8c12-b117-5105-aea3-4f3537b97130 | note | Inspection Type (Visual, other) - Visual
245cff37-160f-5a3a-892d-c2664137d75f | note | Inspection: Key - V
5f723e23-2a78-544e-8477-4ca06f9af449 | checkpoint | 4.2 - Foundation
857be670-bc35-536b-a536-03b584ae17ed | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
bce46be0-68f3-5dca-9796-bf7345159e9f | note | Acceptance Criteria - minimum of 2 blows per 100mm
1e8e82ea-d609-5ab8-acbf-c589247e8cba | note | Verifying Document - test results
2b85e972-d27a-5e78-ad4f-7dc08f0d5ee3 | note | Frequency - During installation, per 20m
b149e75b-9ad3-5a32-9894-e58a4acdfae3 | note | Inspection Type (Visual, other) - Visual, On site test
69645629-13c6-51f9-8c76-3ea0f4ba9fc9 | note | Inspection: Key - H
a2836e07-5fe4-5bc6-a345-bf727e1f1bd5 | signoff | HOLD POINT
e6457720-9f34-5eb3-aa27-51d3ca705faa | checkpoint | 4.3 - Ductile Iron Pipe Installation
27a1ac53-6186-56a6-b519-35fb8e1c8e7a | note | Inspection Point: Quality Control Activity - Pipes installed and positioned as per design
c4695230-3e9e-52d6-9063-dfc8677fdfaa | note | Acceptance Criteria - Pipe not damaged during installation
dcab95bf-dea1-550d-9902-18556550594c | note | ○ Pipe is centrally located within trench
f7bcbd19-1d01-557d-9316-879d969b6514 | note | ○ Pipe levels are within tolerance and according to the drawings
93e01d6b-2cde-5cc8-b34d-cd87c14b9e4c | note | Verifying Document - Photos, Survey of position for asbuilt
19863c04-fad6-59cc-bce6-0e5f7ad6ae83 | note | Frequency - During installation
6bb84f5f-54d1-5950-84d3-7eb8bd47d653 | note | Inspection Type (Visual, other) - Visual
0ae62b89-b361-51b9-ba5a-211bc7b40731 | note | Inspection: Key - V
c7f45453-571b-5df5-a1b1-776de92911f8 | checkpoint | 4.4 - Embedment zone
809c1018-e052-592c-8094-c6940702520d | note | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
3a8be8d3-5271-5443-8885-e836871f838c | note | Acceptance Criteria - Min 100mm bedding
436329b5-94f9-59e1-8dc8-818d7c7cb4b4 | note | ○ 100mm overlay
4cd20966-44a6-569d-93f2-71b0efca2daa | note | Verifying Document - Photos
5584e74a-6509-5ee8-9cea-73acbd196731 | note | Frequency - During Installation
62aaf457-6c46-5554-9926-7e38143346ac | note | Inspection Type (Visual, other) - Visual
fa488abc-db7f-5f8b-8e62-9fe565493efc | note | Inspection: Key - V
8115e6c2-209d-5b8f-9a62-4e0d4d447f75 | checkpoint | 4.5 - Backfill and Compact
daaaf144-0ceb-539a-8599-9ae01570e671 | note | Inspection Point: Quality Control Activity - Backfill material shall be AP65
8c67a3f8-1833-50d7-8f4c-f72d9f195f93 | note | ○ Backfill in 200mm layers of compacted material
025b65db-01cf-5584-8039-85fa20e47d3f | note | ○ Compaction testing one test every two layers as required
34c7cce5-59c1-54f8-837a-34ae28ffd96c | note | ○ Conductive signal strip to be laid at 300mm above pipe
474037b9-3d34-5285-82c0-e42f0771aeae | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
32e0dff3-54b2-5883-944c-d5b33858cfc2 | note | Verifying Document - Photos, Compaction test results
dbc37c94-5497-55f6-a47a-7b11fe4236ae | note | Frequency - During Installation, compaction testing per 50m of pipeline
c6157455-9d54-53de-9422-3ae10fb80541 | note | Inspection Type (Visual, other) - Visual, On Site test
43763bde-2eee-599c-87cb-3f1c815a649a | note | Inspection: Key - H
9c7bc350-6804-5db1-b5e2-6bbb0cb3509e | signoff | HOLD POINT
26b44d4a-841a-50a8-b965-36c95addc184 | section | SECTION 5 - FINAL INSPECTION AND HANDOVER
77a507b9-8f55-5853-8325-9fb24d7a9aab | checkpoint | 5.1 - Pressure Testing (non-PE pipeline)
57ead7f5-36b5-593e-9441-93539912cf78 | note | Inspection Point: Quality Control Activity - Non PE pipelines to be tested in accordance with specifications
b62d67ac-924b-56d9-b8d0-88474c05ea4a | note | Acceptance Criteria - Specification WM 4.6.1: No Thrust block failures, No visible leaks, Do not exceed make-up water limit.
f4b5f43d-7068-547f-a2b9-021a2f91888c | note | Verifying Document - Test Records
3cff9625-4950-5871-a68d-f4e816b21ece | note | Frequency - Before commisioning
cdc40938-3c80-5010-94ad-97c0058da5ad | note | Inspection Type (Visual, other) - On-Site Test
d968d8cb-2885-5a1e-bcaf-d01096beba67 | note | Inspection: Key - H
6efd2c09-69d8-5423-bc0a-ab701a1ea708 | signoff | HOLD POINT
cefa0890-ed04-5eda-b653-0dbb76cb65b3 | checkpoint | 5.2 - Disinfection
4a784473-5f0a-5c40-9386-b5aed470a608 | note | Inspection Point: Quality Control Activity - Disinfection to be completed in accordance with specifications
d3be427f-204c-584b-aef1-07069bd4f5b7 | note | Acceptance Criteria - Specification WM 4.11:
716f865d-16f4-52ff-9840-cede1d671e85 | note | Verifying Document - Test Records
a7d1aec7-09c8-50cb-baf6-987c379f0dad | note | Frequency - Before commisioning
34f71a4f-7a08-5861-96da-ccac84ee8382 | note | Inspection Type (Visual, other) - On-Site Test
6fdf1c8c-1d03-5aa7-8875-29064814b7c2 | note | Inspection: Key - H
83fcf59c-f164-5a1c-ae3b-615bbc32805c | signoff | HOLD POINT
44a3c72c-6f8e-5cd4-956b-cf0bc13db118 | checkpoint | 5.3 - As-Built
23f9b5c9-96b0-573e-b1fc-7fe29078b8cc | note | Acceptance Criteria - Engineer Approval
f7fa94e0-15a2-56ec-900b-6ede2571580c | note | Verifying Document - QA records
51c92772-3f69-59c9-a227-d29c46abbc7b | note | Frequency - At completion
28e83814-cc29-5f0d-8ea1-2be2402fecf5 | note | Inspection: Key - H
aabb3efa-02d2-5ac5-bd5a-664b688b5bf4 | signoff | HOLD POINT
d6d5c3a8-cad4-5fcb-9083-d2756fafd90e | checklist | ITP-0002 - PE Watermain | itp | ITP-0002 - PE Watermain
2ac8716a-63b3-52cf-b624-07c24c0cd6c9 | section | SECTION 3 - RECEIVING INSPECTIONS
2d6469ff-22e7-5477-8cef-d23cbae25acd | checkpoint | 3.1 - Material Delivery
2db0b0ce-8e5c-5fbe-93c8-ac0e778e3993 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
2fd06242-83c9-568c-9e57-3058d29bd0a7 | note | Acceptance Criteria - Pipes shall be DN63 PN16 PE80
8a530a5b-b19d-5b80-a024-b6a0a3107801 | note | ○ Material and fittings are approved as per contract specification
41036e47-785f-5a27-863b-8b426772dbf4 | note | Verifying Document - Photos,delivery docket, MDD results for backfill materials
fdb7957b-1d37-58c0-a66d-bafe66ae53fa | note | Frequency - On Delivery
1767c647-cc30-5c2e-8660-a6ab563654ff | note | Inspection Type (Visual, other) - Visual
a13e224d-dd93-5322-8734-9af4a4037369 | note | Inspection: Key - C
8f6dbf2f-9f4d-514f-ae80-57151c1d03ae | checkpoint | 3.2 - Set out
02cfc7b8-03d2-505a-a322-0eaf3645cf93 | note | Inspection Point: Quality Control Activity - Allignment set out completed by an approved surveyor marked allignment
4e841cb8-1c5f-5108-8458-12fe12a4187c | note | Acceptance Criteria - Set out matches drawings, 2D data and linework provided or aggreed with the Engineer
659acb46-0359-5c53-9dd0-9f650ea6a039 | note | Verifying Document - Survey marks, photos
3f62f40b-f52a-5f30-ac8c-a5459c532fde | note | Frequency - Prior to commencement of works
fbaab756-18a9-583b-be7f-558fd1e0a12b | note | Inspection Type (Visual, other) - Visual, Instrumental
497ae945-d0d1-5bc5-97c5-e153337d57da | note | Inspection: Key - H
57e25cdc-0d38-5a66-a6ee-bd14e8463cf5 | signoff | HOLD POINT
1d1078e0-1bb1-56f7-948a-752012ad998c | section | SECTION 4 - IN-PROCESS INSPECTIONS
c5f206b2-b8d9-55e2-a96f-c1168acbd237 | checkpoint | 4.1 - Trench Excavation
0e61c345-756e-5b6a-880f-ea58638ca6e4 | note | Inspection Point: Quality Control Activity - Excavate to acheive required depth to invert as per drawing C4500
c1e6df37-3058-50df-9a08-e80d142f2cd8 | note | ○ Floor of trench to be even across width and length
cea94ee6-ec87-5ab5-a2b9-fdc4d191a6df | note | Acceptance Criteria - Allow 100mm for bedding
6f04a03c-6ed7-53f7-9515-f1a6b3a561de | note | ○ Allow for minimum cover of 750mm. Max cover not exceeding 1000mm unless shown on Drawings C4500
61c232e1-4be1-55ca-a956-f06ea936a3c1 | note | Verifying Document - Photos
4251ad0f-a1a5-5ce3-bc01-df379f5125b4 | note | Frequency - During Installation
3759decc-3445-5c6c-a501-1234b1685534 | note | Inspection Type (Visual, other) - Visual
eb7e49ed-4f12-570c-9fa1-dde834716dbf | note | Inspection: Key - V
5f723e23-2a78-544e-8477-4ca06f9af449 | checkpoint | 4.2 - Foundation
ad5eb550-15dc-56cf-ace7-ab9a959a30f5 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
61ccfc23-29cc-551b-b0ad-c99158fc1679 | note | Acceptance Criteria - minimum of 2 blows per 100mm
38b92c67-1b58-5259-9164-83fd0c1d9cd0 | note | Verifying Document - test results
636e9912-a1ec-5d7e-a283-bcccc04da6df | note | Frequency - During installation, per 20m
72aa5685-db82-5c87-848f-90f2f58b2f86 | note | Inspection Type (Visual, other) - Visual, On site test
72d3e610-6bf4-5f9d-8f0b-c0714cc59497 | note | Inspection: Key - H
a2836e07-5fe4-5bc6-a345-bf727e1f1bd5 | signoff | HOLD POINT
32149c64-cb1a-5c4a-a136-4dcb2ba6786e | checkpoint | 4.3 - Pipe Installation
28c9ca0a-f8cc-5a59-9cb5-2cc5009916fc | note | Inspection Point: Quality Control Activity - Pipes installed and positioned as per design
77affdb4-367f-5448-bb0a-ce3f82baea4e | note | Acceptance Criteria - Pipe not damaged during installation
801c4c87-d32c-55f5-b98e-38ed7551e50e | note | ○ Pipe is centrally located within trench
8a37136d-6e12-59e3-87eb-0b96df871a55 | note | ○ Pipe levels are within tolerance and according to the drawings
ec1537b4-baf7-541b-ae01-35e230dd7b19 | note | Verifying Document - Photos, weld records (if required), Survey of position for asbuilt
d914efd2-344e-5f29-b0ac-643a116cb1d2 | note | Frequency - During installation
0d892a48-e70a-5a4f-ae68-d4ba83a99eb3 | note | Inspection Type (Visual, other) - Visual
17d84d09-354c-57fd-9460-425db729d5f5 | note | Inspection: Key - V
c7f45453-571b-5df5-a1b1-776de92911f8 | checkpoint | 4.4 - Embedment zone
14662422-d3ab-5a21-9f78-c1b5fb118de8 | note | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
5b6f5399-560a-5b3f-b398-8770fe3088c3 | note | Acceptance Criteria - Min 100mm bedding
4cfcc987-3a20-5b9a-ab89-6f10fa9e251b | note | ○ 100mm overlay
13553891-0ce7-59f7-905f-f0f4e45f9c12 | note | Verifying Document - Photos
b777e6ad-f4e2-551b-9780-4747ddb5f39d | note | Frequency - During Installation
369c27a6-6265-5c04-8c8c-a17f09a6aca1 | note | Inspection Type (Visual, other) - Visual
b1a317ae-c537-5434-8d9a-1d168d1c0e96 | note | Inspection: Key - V
8115e6c2-209d-5b8f-9a62-4e0d4d447f75 | checkpoint | 4.5 - Backfill and Compact
c4ed0ba1-45cd-5f87-8bb3-a94300e5252c | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
58d78ea6-92a5-55e3-aa6b-5fdf5c91c0fa | note | ○ Compaction testing one test every two layers as required
1bbadaa9-d47c-52a7-abd6-5ab1b3e4dec3 | note | ○ Conductive signal strip to be laid at 300mm above pipe
90381076-357d-5bcd-9ee2-36d58687dedc | note | Acceptance Criteria - Passing compaction results - 95% MDD backfill - basecourse
c5049d5f-1bb7-5dbb-8328-190ea949f82d | note | Verifying Document - Photos, Compaction test results
3baf512e-9911-52c9-a9d1-bdcfe7f5cbd8 | note | Frequency - During Installation, compaction testing per 50m of pipeline
c612634a-2179-55f9-91c8-3d02e8d3c816 | note | Inspection Type (Visual, other) - Visual, On Site test
8b5d4dc5-63e7-5441-a5b1-90c8de84d468 | note | Inspection: Key - H
9c7bc350-6804-5db1-b5e2-6bbb0cb3509e | signoff | HOLD POINT
26b44d4a-841a-50a8-b965-36c95addc184 | section | SECTION 5 - FINAL INSPECTION AND HANDOVER
77c12021-91ac-5601-a90a-1992eaf2663e | checkpoint | 5.1 - Pressure Testing (PE pipeline)
78f58bde-a020-5fab-840f-9364074a50cc | note | Inspection Point: Quality Control Activity - PE pipelines to be tested in accordance with specifications
ea419330-966f-526e-b149-d37a363f0816 | note | Acceptance Criteria - Specification WM 4.7.5: No Thrust block failures, No visible leaks, Do not exceed make-up water limit
d31629db-bf4d-5c9c-83b7-9aa4b43dcf26 | note | Verifying Document - Test Records
444a8ca3-e6b1-581a-9461-77721794adcf | note | Frequency - Before commissioning
dfab7f7f-dfc7-5e06-8561-e54abde1ac1e | note | Inspection Type (Visual, other) - On-Site Test
c2779745-08bd-5ff9-8f8f-3621200b77db | note | Inspection: Key - H
9945034a-7c36-5f74-b7ea-ad856ffd612e | signoff | HOLD POINT
cefa0890-ed04-5eda-b653-0dbb76cb65b3 | checkpoint | 5.2 - Disinfection
31ebd585-0600-5105-a55b-2efd3787d67d | note | Inspection Point: Quality Control Activity - Disinfection to be completed in accordance with specifications
2bbfa808-d004-5f10-8a6a-31c5bedfb862 | note | Acceptance Criteria - Specification WM 4.11:
2abac563-d9f5-5145-bf24-61cd054ac670 | note | Verifying Document - Test Records
8b17f466-8d64-5152-9282-1658bc07d7de | note | Frequency - Before commissioning
c3590ca3-9c03-56a8-a50d-ca3b707cae79 | note | Inspection Type (Visual, other) - On-Site Test
1e13bf72-aa7c-5db8-8dcf-de1c896152d5 | note | Inspection: Key - H
83fcf59c-f164-5a1c-ae3b-615bbc32805c | signoff | HOLD POINT
44a3c72c-6f8e-5cd4-956b-cf0bc13db118 | checkpoint | 5.3 - As-Built
9a06dea4-21a5-59c5-8a35-4e8a1d37d7fe | note | Acceptance Criteria - Engineer Approval
854cd6d9-9402-5cb7-a6b8-60693d45e3bb | note | Verifying Document - QA records
d2df897d-a9a9-5d38-abc9-e9df67d3be24 | note | Frequency - At completion
e8e231ce-2b20-5bb7-b87d-863efc08f0e3 | note | Inspection: Key - H
aabb3efa-02d2-5ac5-bd5a-664b688b5bf4 | signoff | HOLD POINT
9a0fb5ab-7027-5147-8881-e49d02734a0e | checklist | ITP-0003 - Ducting | itp | ITP-0003 - Ducting
2ac8716a-63b3-52cf-b624-07c24c0cd6c9 | section | SECTION 3 - RECEIVING INSPECTIONS
2d6469ff-22e7-5477-8cef-d23cbae25acd | checkpoint | 3.1 - Material Delivery
8d902c4c-affa-553e-9f08-490e6074f82d | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
cf5edf52-5433-5344-905e-168289730e73 | note | Acceptance Criteria - Items are approved as per contract specification or as agreed by the engineer
07112d89-e4fb-5f9b-8cd2-45b02ce7fd54 | note | ○ DCC approved
8120143a-a2fd-5c99-97e9-fa8f5dc84740 | note | Verifying Document - Photos, delivery docket, MDD results for backfill materials (if required)
48af411d-411d-5d79-994f-ea06e949c798 | note | Frequency - On Delivery
51064610-ff9c-5dd1-8d53-210c81058b6f | note | Inspection Type (Visual, other) - Visual
91a0b025-3ca9-5e95-b207-8deed9e4b330 | note | Inspection: Key - C
8f6dbf2f-9f4d-514f-ae80-57151c1d03ae | checkpoint | 3.2 - Set out
ae066ef9-0984-5cd8-a226-1fc349b21f53 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
29a471bc-026e-50ef-bfdd-82a1f17be599 | note | Acceptance Criteria - Allignment set out matches drawings, 2D data and linework provided or aggreed with the Engineer
d03b60bd-7a6a-5b8a-8f2a-261c3bb411e1 | note | Verifying Document - Survey marks, photos
8115acc6-0430-526a-bcd2-b522390e4e72 | note | Frequency - Prior to commencement of works
5a6f757d-64bf-50f1-b34e-b4a64b39b801 | note | Inspection Type (Visual, other) - Visual, Instrumental
da13be71-93e6-5c68-9559-99a4695e54ac | note | Inspection: Key - H
57e25cdc-0d38-5a66-a6ee-bd14e8463cf5 | signoff | HOLD POINT
1d1078e0-1bb1-56f7-948a-752012ad998c | section | SECTION 4 - IN-PROCESS INSPECTIONS
c5f206b2-b8d9-55e2-a96f-c1168acbd237 | checkpoint | 4.1 - Trench Excavation
a2397ccb-6c99-525b-a9c5-b77cfec8b051 | note | Inspection Point: Quality Control Activity - Excavate to achieve required depth as per Drawing C4600,C4500
ebace46e-95ae-5388-8b10-adda14a6199d | note | ○ Floor of trench to be even across width and length
8b0f67a7-d71c-5c93-9f07-078b21ad0f88 | note | Acceptance Criteria - Allow 100mm for bedding
00c359b0-3f65-53fc-abcb-f815b8c6eec6 | note | ○ Allow for minimum cover of 600mm.
5f50eb37-df33-5a14-b10f-cbf3d6104142 | note | Verifying Document - Photos
02ae92e1-e99d-592d-b198-7379398e529b | note | Frequency - During Installation
f4505258-4ef3-5dd1-8377-5e73e51ca6ac | note | Inspection Type (Visual, other) - Visual
81c8f8e2-28db-58c2-8f50-781bc18966f2 | note | Inspection: Key - V
5f723e23-2a78-544e-8477-4ca06f9af449 | checkpoint | 4.2 - Foundation
7c4cb71d-a4ba-52d9-ace5-d5d5ef95ecc1 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
e0953abd-7b7a-5a52-826b-9e5353cf1095 | note | Acceptance Criteria - minimum of 2 blows per 100mm
0b64e85b-26ac-5da8-82ff-a10d18c9758c | note | Verifying Document - test results
5e476bbe-174e-5db4-8a61-817c23738ced | note | Frequency - During installation, per 20m
89391e0a-cd85-5ee2-a490-c202c0328502 | note | Inspection Type (Visual, other) - Visual, On site test
1d9e19ed-acc9-5672-9229-1126fbfc2a3c | note | Inspection: Key - H
a2836e07-5fe4-5bc6-a345-bf727e1f1bd5 | signoff | HOLD POINT
2b0fcc0d-5cfb-529f-a549-eabde7247c83 | checkpoint | 4.3 - Install Duct
d3140c32-17e8-519c-8d33-1bf7e6de6e55 | note | Inspection Point: Quality Control Activity - Ducting installed and positioned as per design
7c056b31-b6c5-517c-9d15-c274c7de8440 | note | Acceptance Criteria - Duct not damaged during installation
1accd5ae-0db7-59b9-ba98-629af29a31c4 | note | ○ Minimum of 150mm horizontal and vertical clearence from other services or as specified on Drawings C4600, C4500
a5bc5895-9ab6-5634-a130-3e5d30dd835f | note | Verifying Document - Photos, Survey of position for asbuilt, weld records (if required)
313b1e98-e95e-577d-a6fe-68886d893217 | note | Frequency - During installation
5b80d755-722e-5988-9dd0-c84e17d1ad16 | note | Inspection Type (Visual, other) - Visual
decf6a22-76b6-5ccd-8261-2ee0f90b82d0 | note | Inspection: Key - V
c7f45453-571b-5df5-a1b1-776de92911f8 | checkpoint | 4.4 - Embedment zone
f76f3a6c-a88d-54ef-9698-d9cdae1da0d1 | note | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
59a6202a-5885-5d77-849a-34dbe244afc5 | note | Acceptance Criteria - Min 100mm bedding
fc25305e-7973-546a-b8e1-a0f45f8b2303 | note | ○ 100mm overlay
4c335cb2-e8ef-5997-ae01-12952b650974 | note | Verifying Document - Photos
fe7ddae4-2304-52d4-aea7-85e2fa9796f8 | note | Frequency - During Installation
436864b6-e3e0-5ae9-8a61-ce30229de621 | note | Inspection Type (Visual, other) - Visual, measurement check
b8c9868d-7396-5851-a703-0eefd4b14fb1 | note | Inspection: Key - V
8115e6c2-209d-5b8f-9a62-4e0d4d447f75 | checkpoint | 4.5 - Backfill and Compact
6f28239d-0725-58b0-9012-60710954e9a3 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
bc2bfa89-42ac-5ab9-b44b-c749bdcbc8bc | note | ○ Compaction testing one test every two layers as required
4f37897e-2756-5699-aa29-e1da630280d6 | note | ○ Conductive signal strip to be laid at 300mm above duct
b6d636d5-f794-5b49-b270-bfee37df99ee | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
224ee362-8bfc-57ae-9d94-e9608d14e307 | note | Verifying Document - Photos, Compaction test results
7d9f6647-3a2f-5542-83a4-8ede136a128b | note | Frequency - During Installation, compaction testing per 50m of pipeline
529d52b2-3d85-56ab-a4b3-e9b03517687e | note | Inspection Type (Visual, other) - Visual, On Site test
a77e93be-b2af-5473-91ba-e40b7b14b420 | note | Inspection: Key - H
9c7bc350-6804-5db1-b5e2-6bbb0cb3509e | signoff | HOLD POINT
26b44d4a-841a-50a8-b965-36c95addc184 | section | SECTION 5 - FINAL INSPECTION AND HANDOVER
7b1fe29d-ac29-5823-87f6-f58f354f91f9 | checkpoint | 5.1 - As built
9d816568-a130-5295-b70d-6ef281625964 | note | Acceptance Criteria - Engineer Approval
6f746184-a1ff-5f91-bca3-b1dd4a4d46b5 | note | Verifying Document - QA records
c9f0114c-dd6e-509a-bdde-4dedb0b9b521 | note | Frequency - At completion
61e8da25-482b-5c7a-96a2-b5aa94691a7a | note | Inspection: Key - H
179b224a-28a7-596d-86fb-b0a02402a162 | signoff | HOLD POINT