## Table 1
BESS Alinta Wagerup Peaking Power Station Field Inspection Checklist – Electrical trenching Document Number: RR-SEPD-BESS-FIC-003
Document Information
| Checklist title |  |  | Earthworks
| Checklist No |  |  | RR-SEPD-BESS-FIC-003
Lot Description
| Revision no. |  |  | 0
Revision Date (DD/MM/YYYY)
| Description of Changes |  |  | First Issue
Document Review
Prepared by:
| Responsibility |  | Name |  |  | Signature |  | Date (DD/MM/YYYY)
| Drafted by (Engineer) |  | Juan Orozco |  |  |  |  | 2024-07-10
| Reviewed by (Supervisor) |  | Craig Stein |  |  |  |  | 2024-07-10
| Approved by (Manager) |  | Artur Krupinski |  |  |  |  | 2024-08-10
Document No: RR-SEPD-BESS-FIC-001 ¦ Revision: 00
Pg.1
Part 1 – Preliminaries (photos where applicable)
| Inspection/Test item |  |  |  | Acceptance Criteria | Specifications/Drawings Reference | (Yes/No/NA) | Initial & Date
[8 empty] | ROBAR | SEPD
| 1.1 | Review of approved construction drawings and specifications |  |  | All drawings and specifications approved and up to date | WBS-SS-CI-SPC-006
| 1.2 | Verification of permits |  |  | All relevant permits (GDA/GDP) in place | GDA/GDP
| 1.3 | Site access and safety preparation |  |  | Site access cleared and made safe | WBS-SS-CI-SPC-006
| 1.4 | Safety inductions and toolbox talks |  |  | All personnel inducted; safety briefings completed | Induction record
| 1.5 | Environmental controls in place |  |  | Dust, noise, and sediment barriers installed and functioning | SEPD environmental requirements
| 1.6 | Utility identification |  |  | All utilities marked as per drawings | Project as-built drawings
Part 2 – Set-out and excavation (photos where applicable)
| 2.1 | Site set-out verification |  |  | Set-out verified and matches IFC drawings | Site IFC Drawings
| 2.2 | Accurate dimensions |  |  | Width, depth, and alignment match design drawings | WBS-SS-EL-DRG-3005
Part 3 – Excavation (photos where applicable)
| 3.1 | Dimensions maintained |  |  | Depth and width meet design specifications | WBS-SS-CI-SPC-006 WBS-SS-EL-DRG-3005
| 3.2 | Stockpiling of excavated material |  |  | Material stockpiled properly, no contamination | WBS-SS-CI-SPC-006
| 3.3 | Stability of trench |  |  | No loose soil or collapses; protective measures in place if trench is over 1.5m | WBS-SS-CI-SPC-006
| 3.4 | Subbase inspection |  |  | Subgrade verified, compacted and stable | Geotechnical report
| 3.5 | Subbase compaction testing |  |  | Compaction results meet project criteria. 1 test every 40 linear meters and 1 every two layers. | AS 1289 geotechnical report
Part 4 – Fill material and compaction (photos where applicable)
| 4.1 | Backfill material |  |  | Approved material used for backfill | WBS-SS-CI-SPC-0006
| 4.1 | Imported fill material testing |  |  | Material complies with particle size, moisture content, MMDD | WBS-SS-CI-SPC-0006 Test material results
| 4.2 | Fill placement in 150mm layers |  |  | Layers placed in maximum 200mm (loose) thickness | WBS-SS-CI-SPC-0006
| 4.3 | Compaction testing |  |  | Compaction >92% MMDD for general fill | AS 1289 Compaction test results
| 4.4 | Level and grading check |  |  | Levels and grading match design tolerances (+/- 20mm) | WBS-SS-CI-SPC-0006, Survey Report
Document No: RR-SEPD-BESS-FIC-001 ¦ Revision: 00
Pg.2
Part 5 – Environmental and erosion controls (photos where applicable)
| Inspection Acceptance |  |  |  | Acceptance Criteria | Specifications/Drawings Reference | (Yes/No/NA) | Initial & Date
| 5.1 | Dust control measures |  |  | Dust suppression methods in place and effective | SEPD Environmental Plan
| 5.2 | Erosion and sediment control measures |  |  | Sediment barriers, silt fences, and basins installed and maintained | WBS-SS-CI-SPC-0006
| 5.3 | Site drainage |  |  | Temporary drainage in place to control stormwater and prevent site flooding | Drainage Plan Site Inspection
Part 6 – Final inspections and acceptance (photos where applicable)
| Inspection Acceptance |  |  |  | Acceptance Criteria | Specifications/Drawings Reference | (Yes/No/NA) | Initial & Date
| 6.1 | Final surface inspection |  |  | Surface is stable, free from defects, and meets design criteria | Site inspection Proof roll
| 6.2 | As-built survey verification |  |  | As-built levels and layout match design | As-Built Drawings Survey Report
| 6.3 | Removal of temporary works |  |  | All temporary structures, barriers, and access points removed | Site inspection
| 6.4 | Final inspection sign-off |  |  | All earthworks activities completed and accepted | WBS-SS-CI-SPC-0006
Document Sign-off
Prepared by:
| Responsibility |  | Name |  |  | Signature |  | Date (DD/MM/YYYY)
ROBAR (Engineer)
SEPD (Engineer)
Document No: RR-SEPD-BESS-FIC-001 ¦ Revision: 00
Pg.3