## Table 1
Inspection & Test Plan Electrical Trenching
| Project Scope: Electrical trenching | [18 empty] | Ref: RR-SEPD-BESS-ITP-003
| Project: BESS Alinta Wagerup Peaking Power Station | [18 empty] | Revision: 00
ITP Description: Electrical trenching
Work Pack number: RR-SEPD-CI-SOW-003-01
Client: SEPD
| Prepared By: | [6 empty] | Sign & Date: 20/11/2024 |  |  | Reviewed & Approved By: | [8 empty] | Sign & Date: 20/11/2024
| Juan Orozco – Project Engineer | [9 empty] | Ronan Egan – Project Manager
| Reviewed & Approved By: | [6 empty] | Sign & Date: 20/11/2024 |  |  | Reviewed & Approved By: | [8 empty] | Sign & Date: 20/11/2024
| Artur Krupinski - Project Controls | [9 empty] | Craig Stein – Site Supervisor
RR-SEPD-BESS-ITP-003-00 Page 1 of 8
Inspection & Test Plan Electrical Trenching
Definitions
| Hold Point |  | A point beyond which a work process must not proceed without the nominated authority’s express authorization.
| Witness Point |  | A point in a work process where the Contractor must give prior notice to the nominated authority and the option of attendance may be exercised by the nominated authority.
| Responsibility | [5 empty] | Method |  |  |  | Frequency | [6 empty] | Verification Requirement
| SUP | Supervisor |  |  |  |  | I | Inspection |  |  | PW |  | Prior to works |  |  |  |  | HP |  |  | Hold Point
| SE | Site Engineer |  |  |  |  | R | Review |  |  | PL |  | Per lot |  |  |  |  | WP |  |  | Witness Point
| PE | Project Engineer |  |  |  |  | S | Survey | [9 empty] | M |  |  | Milestone
| SPE | Senior Project Engineer |  |  |  |  | T | Test | [9 empty] | V |  |  | Verification
| PM | Project Manager | [15 empty] | NA |  |  | Not Available
| SV | Surveyor
| QM | Quality Manager
| QR | Quality Representative
| ER | Environmental Representative
| IV | Independent Verifier
RR-SEPD-BESS-ITP-003-00 Page 2 of 8
Inspection & Test Plan Electrical Trenching
| Contractor Name |  |  |  |  | ROBAR Rentals | [12 empty] | RR-SEPD-BESS-ITP-003-00
| Responsible Engineer |  |  |  |  | Juan Orozco | [12 empty] | RR-SEPD-CI-SOW-001-01
| Responsible Supervisor |  |  |  |  | Craig Stein
Location
Description
| Item no. | Inspection/Test Point |  |  | Responsibility | Specification Reference |  |  | Conformance Criteria Summary |  |  | Method |  | Frequency |  | Hold/Witness Point Requirements | [6 empty] | Records or Checklist Document Number
[16 empty] | ROBAR | SEPD |  |  |  |  | Client
Section 1: Preliminaries & Permits
| 1.1 | Pre-Excavation Site Inspection |  |  | SE/PE | WBS-SS-CI- SPC-0006 |  |  | Work area is clear, utilities and exclusion zones are clearly marked, permits are approved. |  |  | R |  | PW |  | V | NA |  |  |  |  | NA | IFC Drawings
| 1.2 | Permit approval (GDA/GDP) |  |  | SE/PE | WBS-SS-CI- SPC-0006 |  |  | Approved excavation permit (GDP) prior to commencing works |  |  | R |  | PW |  | HP | HP |  |  |  |  | NA | RR-SEPD-CI- SOW-002-01
| 1.3 | Site set-out |  |  | SE/PE | WBS-SS-CI- SPC-0006 |  |  | Verify levels, site boundaries, and physical bounds per IFC drawings |  |  | R |  | PW |  | V | NA |  |  |  |  | NA | IFC Drawings
| 1.4 | Sediment control plan |  |  | SE/PE | WBS-SS-PM- PLN-0024 WAE230103- 03-003 TM Rev0 |  |  | Sediment control measures in place |  |  | R |  | PW |  | V | NA |  |  |  |  | NA | SEPD environment- al plan
| 1.5 | Dust control plan |  |  | SE/PE | PP3 section 1.5 and section 4.1 |  |  | Dust control measures in place |  |  | R |  | PW |  | V | NA |  |  |  |  | NA | SEPD environment- al plan
Section 2: Materials
| 2.1 | Import fill material inspection |  |  | SE/PE | WBS-SS-CI- SPC-0006 |  |  | Material certificate and test report for particle size distribution, moisture content, MMDD |  |  | R |  | PW |  | V | V |  |  |  |  | NA | Material certificates
| 2.2 | Verify suitable foundation material (compaction >92% MMDD) |  |  | SE/PE | WBS-SS-CI- SPC-0006 |  |  | Geotechnical test results showing compliance |  |  | R |  | PW |  | HP | HP |  |  |  |  | NA | Test results
Section 3: Electrical trenching
| 3.1 | Excavation to subgrade – verify lines, depth and dimensions |  |  | SE/PE | WBS-SS-CI- SPC-0006 |  |  | Compliance with design drawings and subgrade preparation |  |  | I |  | PL |  | V | V |  |  |  |  | NA | IFC Drawings
| 3.2 | Stockpiling of excavated material – manage and segregate by type |  |  | SE/PE | WBS-SS-CI- 0006 |  |  | Material stockpiled appropriately, no cross contamination |  |  | I |  | PL |  | V | V |  |  |  |  | NA | SEPD environment- al plan
| 3.3 | Base preparation |  |  | SE/PE | WBS-SS-CI- 0006 |  |  | Base is level, compacted, and free of debris; compaction meets project specs. |  |  | I |  | PL |  | V | V |  |  |  |  | NA
| 3.4 | Initial backfilling and compaction |  |  | SE/PE | WBS-SS-CI- 0006 |  |  | Backfill material compacted in 150mm layers to required thickness Material shall be placed to a depth of 150mm above the collars of pipes or conduits, 300mm above pipes and 600mm above culverts |  |  | I |  | PL |  | V | V |  |  |  |  | NA | WBS-SS-CI- ITP-920049
| 3.5 | Compaction density ratio for backfill |  |  | SE/PE | WBS-SS-CI- SPC-0006 |  |  | Compaction test report showing >92% MMDD every 40 linear meters and every 2 layers WBS-SS-CI-ITP-920049 |  |  | T |  | PL |  | HP | HP |  |  |  |  | NA | Test results
| 3.6 | As-built survey pick-up |  |  | SE/PE | WBS-SS-CI- SPC-0006 PPR |  |  | Survey records and as-built drawings |  |  | S |  | PL |  | V | V |  |  |  |  | NA | As-built drawings
Section 4: Final Inspection
| 4.1 | Finish level compliance with design drawings |  |  | SE/PE | WBS-SS-CI- SPC-0006 |  |  | As-built drawings |  |  | S |  | PL |  | V | V |  |  |  |  | NA | WBS-SS-CI- ITP-920049
| 4.2 | Final Inspection Checklist (FIC) completion |  |  | SE/PE | WBS-SS-CI- SPC-0006 |  |  | Signed FIC |  |  | R |  | PL |  | V | V |  |  |  |  | NA | WBS-SS-CI- ITP-920049
Document sign-off
Close-out
| Company |  |  | Name | [5 empty] | Position |  |  |  |  | Signature |  |  | Date (DD/MM/YYYY)
ROBAR
SEPD
RR-SEPD-BESS-ITP-003-00 Page 8 of 8