## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | Inverter Foundations | itp |  |  |  |  | ITP - Inverter Foundations
section | Preconstruction
checkpoint | Design
label | Issued For Construction Drawings MSF-EN-CIV-DRG-910
checkpoint | Survey & Setout
label | Issued For Construction Drawings MSF-EN-CIV-DRG-910
section | Material Procurement
checkpoint | Structural Steel
label | Issued For Construction Drawings
label | Manufacturers Documentation
label | Inspection Records
label | All reinforcing bars shall be Grade 300E to AS/NZS 4671 as shown in IFC Drawings NZS3109/3112
label | All reinforcing and formwork to comply with IFC drawings
checkpoint | Concrete
label | Concrete shall be 30MPa Minimum Strength for precast elements
section | Construction
checkpoint | Excavation of Foundation
label | Issued for Construction Drawings
label | Remove topsoil back to subgrade material and place in suitable storage location with silt controls
label | Foundation excavated to line and level shown in IFC Drawings
label | Scalar Penetrometer test results recorded on Checksheet
checkpoint | Compacted Harfill under Inverter Foundations
label | Issued for Construction Drawings
label | 200x800 Compacted Hardfill Pad under footings
label | Results Recorded on Clegg Hammer Checksheet
checkpoint | Concrete
label | Lines, levels and dimension as per Issued for Construction Drawings MSF-EN-CIV-DRG-910
label | Concrete to be min 30MPa at 28 days
label | Test cylinders taken
label | Dimensions to match IFC Drawings with tolerance of +/- 1mm
label | 50mm minimum cover to steel
label | Prepour Inspection Record completed prior to pouring
checkpoint | Placement of Concrete Elements
label | Lines and levels as per Issued for Construction Drawings
label | Use drypack for installation of inverter if required with min thickness of 20mm
label | Middle block must be setup for container to sit fully on level and true
label | The outside blocks shall be set lower than the centre block
checkpoint | Backfill
label | Issued for Construction Drawings
label | Sand Backfill to be watered and compacted in by mechanical means to provide backfill and support around the foundations without voids or areas of non-compaction
section | Close-Out
checkpoint | Asbuilt Recording
label | Asuilt records supplied of inverter foundations in place
checkpoint | Non-Conformance-Reports
label | Non-Conformances Closed Out
checkpoint | Handover
label | At completion of works QA/QC Pack is handed to client
label | Client Verifies Work has been completed correctly and all quality documents are in order
holdpoint | HOLD POINT