## matrix
Matrix Name | Dimension | Name | Type / Data Field | Tag 1 | Tag 2
Plans
| Scope |  |  | Plans
Rows
|  | Overall | dynamic | Site QA | Plans | Overall
|  | Basement | dynamic | Site QA | Plans | Basement
|  | Ground | dynamic | Site QA | Plans | Ground
|  | Ground/Mezzanine | dynamic | Site QA | Plans | Ground/Mezzanine
|  | Level 1 | dynamic | Site QA | Plans | Level 1
|  | Level 2 | dynamic | Site QA | Plans | Level 2
|  | Level 3 | dynamic | Site QA | Plans | Level 3
|  | Level 4 | dynamic | Site QA | Plans | Level 4
|  | Level 5 | dynamic | Site QA | Plans | Level 5
|  | Level 6 | dynamic | Site QA | Plans | Level 6
|  | Level 7 | dynamic | Site QA | Plans | Level 7
|  | Level 8 | dynamic | Site QA | Plans | Level 8
|  | Level 9 | dynamic | Site QA | Plans | Level 9
|  | Level 10 | dynamic | Site QA | Plans | Level 10
|  | Level 11 | dynamic | Site QA | Plans | Level 11
|  | Level 12 | dynamic | Site QA | Plans | Level 12
|  | Roof | dynamic | Site QA | Plans | Roof
Columns
|  | Document / Photo Attached |  | Attach Document / Upload Photo here
|  | Upload Doc |  | Upload Doc
Undergrounds Overall Progress
| Scope |  |  | Undergrounds
Rows
|  | Undergrounds | dynamic | Site QA | Undergrounds
Columns
|  | Inspect conduit material to check that it meets material specifications |  | Inspect conduit material to check that it meets material specifications
|  | Check conduit alignment as per plans |  | Check conduit alignment as per plans
|  | Set out marked, & all services located |  | Set out marked, and all services located
|  | Erect pedetrian barricading as per plan |  | Erect pedetrian barricading as per plan
|  | Check excavation depth against proposed road level |  | Check excavation depth against proposed road level
|  | Excavate to the trench as per plan |  | Excavate to the trench as per plan
|  | Place specified bedding material in trench |  | Place specified bedding material in trench
|  | Placement of conduit of specified size in accordance with specifications/drawings |  | Placement of conduit of specified size in accordance with specifications/drawings
|  | Backfill over conduit to 300mm |  | Backfill over conduit to 300mm
|  | Install cover slabs over conduit |  | Install cover slabs over conduit
|  | Ensure area is left clean |  | Ensure area is left clean
|  | Photos |  | Photos
Inslab Conduits Overall Progress
| Scope |  |  | Inslab Conduits
Rows
|  | Core | dynamic | Site QA | Inslab Conduits | Core
|  | Floors - Basement | dynamic | Site QA | Inslab Conduits | Floors | Basement
|  | Floors - Ground | dynamic | Site QA | Inslab Conduits | Floors | Ground
|  | Floors - Ground/Mezzanine | dynamic | Site QA | Inslab Conduits | Floors | Ground/Mezzanine
|  | Floors - Level 1 | dynamic | Site QA | Inslab Conduits | Floors | Level 1
|  | Floors - Level 2 | dynamic | Site QA | Inslab Conduits | Floors | Level 2
|  | Floors - Level 3 | dynamic | Site QA | Inslab Conduits | Floors | Level 3
|  | Floors - Level 4 | dynamic | Site QA | Inslab Conduits | Floors | Level 4
|  | Floors - Level 5 | dynamic | Site QA | Inslab Conduits | Floors | Level 5
|  | Floors - Level 6 | dynamic | Site QA | Inslab Conduits | Floors | Level 6
|  | Floors - Level 7 | dynamic | Site QA | Inslab Conduits | Floors | Level 7
|  | Floors - Level 8 | dynamic | Site QA | Inslab Conduits | Floors | Level 8
|  | Floors - Level 9 | dynamic | Site QA | Inslab Conduits | Floors | Level 9
|  | Floors - Level 10 | dynamic | Site QA | Inslab Conduits | Floors | Level 10
|  | Floors - Level 11 | dynamic | Site QA | Inslab Conduits | Floors | Level 11
|  | Floors - Level 12 | dynamic | Site QA | Inslab Conduits | Floors | Level 12
|  | Floors - Roof | dynamic | Site QA | Inslab Conduits | Floors | Roof
Columns
|  | Determine origin & destination |  | Determine origin and destination
|  | Check clear of other services, penetrations & form work stripping etc |  | Check clear of other services, penetrations and form work stripping etc
|  | Check cable size to verify conduit size |  | Check cable size to verify conduit size
|  | Mark out positions of junction boxes & penerations where necessary |  | Mark out positions of junction boxes and penerations where necessary
|  | Install bar chairs where necessary |  | Install bar chairs where necessary
|  | Install junction boxes & penetrations where necessary |  | Install junction boxes and penetrations where necessary
|  | Install junction boxes & conduits glue |  | Install junction boxes and conduits glue
|  | Tie conduits securely at all joints & midpoints |  | Tie conduits securely at all joints and midpoints
|  | Ensure all conduits are 50mm above deck |  | Ensure all conduits are 50mm above deck
|  | Install conduits in stair 1 |  | Install conduits in stair 1
|  | Install conduits in stair 2 |  | Install conduits in stair 2
|  | Temp Board penetrations to floor below installed (50mm for submains, 25mm for Evac) |  | Temp Board penetrations to floor below installed (50mm for submains, 25mm for Evac)
|  | All Temp lighting conduits installed |  | All Temp lighting conduits installed
|  | Penos through Core wall installed |  | Penos through Core wall installed
|  | Mark up drawing of conduit runs, Penos |  | Mark up drawing of conduit runs, Penos
|  | Check clear of other services, penetrations etc |  | Check clear of other services, penetrations etc
|  | Check if expansion joints are required |  | Check if expansion joints are required
|  | 50mm temp conduit installed from Control DB to temp board |  | 50mm temp conduit installed from Control DB to temp board
|  | Rio Turned up at riser to earth slab |  | Rio Turned up at riser to earth slab
|  | Ensure floor boxes & conduits into the FB are secured & photos of each one are uploaded |  | Ensure floor boxes and conduits into the FB are secured and photos of each one are uploaded
|  | Mark up drawing of conduit runs, Penos, Floor Boxes Etc. |  | Mark up drawing of conduit runs, Penos, Floor Boxes Etc.
|  | Take photos of conduit & cups installed |  | Take photos of conduit and cups installed
|  | Check Cable tray penatration boxes are installed correctly & take photos |  | Check Cable tray penatration boxes are installed correctly and take photos
|  | Observe conduits when concrete is being poured |  | Observe conduits when concrete is being poured
|  | Conduit installed to roll over capping beam & roll down to B1 Control DB |  | Conduit installed to roll over capping beam and roll down to B1 Control DB
|  | Conduit installed to roll over capping beam supply 2 x Alimak from Temp MSB |  | Conduit installed to roll over capping beam supply 2 x Alimak from Temp MSB
|  | Ensure area is left clean |  | Ensure area is left clean
|  | Photos |  | Photos
Temps Overall Progress
| Scope |  |  | Temps
Rows
|  | Temp Board Register | grouping | Temp Board Register
|  | Temp Board Register |  | Site QA | Temps | Temp Board Register
|  | Temp Board RCD Test Results - 2024 | dynamic | Site QA | Temps | Temp Board RCD Test Results | 2024
|  | Temp Board RCD Test Results - 2025 | dynamic | Site QA | Temps | Temp Board RCD Test Results | 2025
|  | Temp Boards Installation - Basement | dynamic | Site QA | Temps | Temp Boards Installation | Basement
|  | Temp Boards Installation - Ground | dynamic | Site QA | Temps | Temp Boards Installation | Ground
|  | Temp Boards Installation - Ground/Mezzanine | dynamic | Site QA | Temps | Temp Boards Installation | Ground/Mezzanine
|  | Temp Boards Installation - Gantry Lunch sheds | dynamic | Site QA | Temps | Temp Boards Installation | Gantry Lunch sheds
|  | Temp Boards Installation - Level 1 | dynamic | Site QA | Temps | Temp Boards Installation | Level 1
|  | Temp Boards Installation - Level 2 | dynamic | Site QA | Temps | Temp Boards Installation | Level 2
|  | Temp Boards Installation - Level 3 | dynamic | Site QA | Temps | Temp Boards Installation | Level 3
|  | Temp Boards Installation - Level 4 | dynamic | Site QA | Temps | Temp Boards Installation | Level 4
|  | Temp Boards Installation - Level 5 | dynamic | Site QA | Temps | Temp Boards Installation | Level 5
|  | Temp Boards Installation - Level 6 | dynamic | Site QA | Temps | Temp Boards Installation | Level 6
|  | Temp Boards Installation - Level 7 | dynamic | Site QA | Temps | Temp Boards Installation | Level 7
|  | Temp Boards Installation - Level 8 | dynamic | Site QA | Temps | Temp Boards Installation | Level 8
|  | Temp Boards Installation - Level 9 | dynamic | Site QA | Temps | Temp Boards Installation | Level 9
|  | Temp Boards Installation - Level 10 | dynamic | Site QA | Temps | Temp Boards Installation | Level 10
|  | Temp Boards Installation - Level 11 | dynamic | Site QA | Temps | Temp Boards Installation | Level 11
|  | Temp Boards Installation - Level 12 | dynamic | Site QA | Temps | Temp Boards Installation | Level 12
|  | Temp Boards Installation - Roof | dynamic | Site QA | Temps | Temp Boards Installation | Roof
|  | Temp Boards Installation - Jump Form | dynamic | Site QA | Temps | Temp Boards Installation | Jump Form
|  | Temp Lighting - Basement | dynamic | Site QA | Temps | Temp Lighting | Basement
|  | Temp Lighting - Ground | dynamic | Site QA | Temps | Temp Lighting | Ground
|  | Temp Lighting - Mezzanine | dynamic | Site QA | Temps | Temp Lighting | Mezzanine
|  | Temp Lighting - Level 1 | dynamic | Site QA | Temps | Temp Lighting | Level 1
|  | Temp Lighting - Level 2 | dynamic | Site QA | Temps | Temp Lighting | Level 2
|  | Temp Lighting - Level 3 | dynamic | Site QA | Temps | Temp Lighting | Level 3
|  | Temp Lighting - Level 4 | dynamic | Site QA | Temps | Temp Lighting | Level 4
|  | Temp Lighting - Level 5 | dynamic | Site QA | Temps | Temp Lighting | Level 5
|  | Temp Lighting - Level 6 | dynamic | Site QA | Temps | Temp Lighting | Level 6
|  | Temp Lighting - Level 7 | dynamic | Site QA | Temps | Temp Lighting | Level 7
|  | Temp Lighting - Level 8 | dynamic | Site QA | Temps | Temp Lighting | Level 8
|  | Temp Lighting - Level 9 | dynamic | Site QA | Temps | Temp Lighting | Level 9
|  | Temp Lighting - Level 10 | dynamic | Site QA | Temps | Temp Lighting | Level 10
|  | Temp Lighting - Level 11 | dynamic | Site QA | Temps | Temp Lighting | Level 11
|  | Temp Lighting - Level 12 | dynamic | Site QA | Temps | Temp Lighting | Level 12
|  | Temp Lighting - Level roof | dynamic | Site QA | Temps | Temp Lighting | Level roof
|  | Temp Lighting - Jump Form | dynamic | Site QA | Temps | Temp Lighting | Jump Form
|  | Temp Boards Removal - Basement | dynamic | Site QA | Temps | Temp Boards Removal | Basement
|  | Temp Boards Removal - Ground | dynamic | Site QA | Temps | Temp Boards Removal | Ground
|  | Temp Boards Removal - Ground/Mezzanine | dynamic | Site QA | Temps | Temp Boards Removal | Ground/Mezzanine
|  | Temp Boards Removal - Gantry Lunch sheds | dynamic | Site QA | Temps | Temp Boards Removal | Gantry Lunch sheds
|  | Temp Boards Removal - Level 1 | dynamic | Site QA | Temps | Temp Boards Removal | Level 1
|  | Temp Boards Removal - Level 2 | dynamic | Site QA | Temps | Temp Boards Removal | Level 2
|  | Temp Boards Removal - Level 3 | dynamic | Site QA | Temps | Temp Boards Removal | Level 3
|  | Temp Boards Removal - Level 4 | dynamic | Site QA | Temps | Temp Boards Removal | Level 4
|  | Temp Boards Removal - Level 5 | dynamic | Site QA | Temps | Temp Boards Removal | Level 5
|  | Temp Boards Removal - Level 6 | dynamic | Site QA | Temps | Temp Boards Removal | Level 6
|  | Temp Boards Removal - Level 7 | dynamic | Site QA | Temps | Temp Boards Removal | Level 7
|  | Temp Boards Removal - Level 8 | dynamic | Site QA | Temps | Temp Boards Removal | Level 8
|  | Temp Boards Removal - Level 9 | dynamic | Site QA | Temps | Temp Boards Removal | Level 9
|  | Temp Boards Removal - Level 10 | dynamic | Site QA | Temps | Temp Boards Removal | Level 10
|  | Temp Boards Removal - Level 11 | dynamic | Site QA | Temps | Temp Boards Removal | Level 11
|  | Temp Boards Removal - Level 12 | dynamic | Site QA | Temps | Temp Boards Removal | Level 12
|  | Temp Boards Removal - Roof | dynamic | Site QA | Temps | Temp Boards Removal | Roof
|  | Temp Boards Removal - Jump Form | dynamic | Site QA | Temps | Temp Boards Removal | Jump Form
Columns
|  | Document / Photo attached |  | Attach Document / Upload Photo here
|  | Upload Doc |  | Upload Doc
|  | Area accessible & ready |  | Area accessible & ready
|  | Locate & fix into position, bolt temporary board down with at least 2 fixings |  | Locate & fix into position, bolt temporary board down with at least 2 fixings
|  | Install submains cabling as appropriate eg: glands/tray/duct |  | Install submains cabling as appropriate eg: glands/tray/duct
|  | Install lugs & terminate |  | Install lugs and terminate
|  | Any cables not terminated prior to energisation must be removed from cubicle at origin & have ends covered in heat shrink |  | Any cables not terminated prior to energisation must be removed from cubicle at origin and have ends covered in heat shrink. At destination cables must be covered in heat shrink and be contrained in a junction box
|  | Ensure pole filler is covering any openings |  | Ensure pole filler is covering any openings
|  | Ensure all cable entry holes not used are plugged up |  | Ensure all cable entry holes not used are plugged up
|  | Label temp board with unique temp board number |  | Label temp board with unique temp board number
|  | Clearly identify services with labels |  | Clearly identify services with labels
|  | When ready to energise proceed in accordance with energisation procedure |  | When ready to energise proceed in accordance with energisation procedure
|  | Energise & record results on Vast RCD test sheet |  | Energise & record results on Vast RCD test sheet
|  | Put on appropriate colour 3 x monthly testing tag |  | Put on appropriate colour 3 x monthly testing tag
|  | Install A3 laminated sign on face of temp board with floor plan & where the board is fed from |  | Install A3 laminated sign on face of temp board with floor plan and where the board is fed from
|  | Update Temporary Power Board register & save to project folder/design control/temp const. |  | Update Temporary Power Board register & save to project folder/design control/temp const.
|  | Install emergency light is installed above or on Temporary board & tagged. |  | Install emergency light is installed above or on Temporary board and tagged.
|  | Lodge non prescribed certificate of electrical safety |  | Lodge non prescribed certificate of electrical safety
|  | RCBO'S must be fully tested initially & then tested every month with results recorded & c/b’s labelled |  | RCBO'S must be fully tested initially and then tested every month with results recorded and c/b’s labelled
|  | Refer to temporary wiring setout plan |  | Refer to temporary wiring setout plan
|  | CABLING MUST BE SUPPORTED & PROTECTED FROM DAMAGE. CONSTRUCTION WIRING TAPE MUST BE FITTED AT EVERY 5 METRES. |  | CABLING MUST BE SUPPORTED AND PROTECTED FROM DAMAGE. CONSTRUCTION WIRING TAPE MUST BE FITTED AT EVERY 5 METRES. TEMPORARY WIRING MUST NOT BE INSTALLED WITH PERMANENT CABLING
|  | Fit off plug base & or powerpoint/isolator |  | Fit off plug base and or powerpoint/isolator
|  | Install light fitting, exit/emg, power |  | Install light fitting, exit/emg, power
|  | Ensure all stairs are Emergency lights only |  | Ensure all stairs are Emergency lights only
|  | Ensure exits are installed as needed at exit points & are visable |  | Ensure exits are installed as needed at exit points and are visable
|  | Terminate cable to temp board. Ensure temp board is isolated! Test Test Test |  | Terminate cable to temp board. Ensure temp board is isolated! Test Test Test
|  | Test & commission |  | Test & commission
|  | Temp lights installed & energised after pour before stripping |  | Temp lights installed and energised after pour before stripping
|  | Flood lights installed |  | Flood lights installed
|  | Rest of templights installed & energised after stripping |  | Rest of templights installed and energised after stripping
|  | Determine what the temporary board is controlling & confirm what action is required before board can be decommissioned. |  | Determine what the temporary board is controlling and confirm what action is required before board can be decommissioned.
|  | De-commission form issued to builder, 48 hours notice to be given |  | De-commission form issued to builder, 48 hours notice to be given
|  | Sign off builders checklist |  | Sign off builders checklist
|  | Safety Committee Inspection |  | Safety Committee Inspection
|  | Final approval to be given by builder |  | Final approval to be given by builder
|  | Perform voltage test to ensure power supply has been isolated |  | Perform voltage test to ensure power supply has been isolated
|  | Disconnect supply cables |  | Disconnect supply cables
|  | Fire sealing of penetrations |  | Fire sealing of penetrations
|  | Remove temporary board |  | Remove temporary board
|  | Update temporary power board register |  | Update temporary power board register
|  | Ensure area is left clean |  | Ensure area is left clean
|  | Photos |  | Photos
Mains & Sub-Mains Overall Progress
| Scope |  |  | Mains & Sub-Mains
Rows
|  | Basement | dynamic | Site QA | Mains & Sub-Mains | Basement
|  | Ground | dynamic | Site QA | Mains & Sub-Mains | Ground
|  | Ground/Mezzanine | dynamic | Site QA | Mains & Sub-Mains | Ground/Mezzanine
|  | Level 1 | dynamic | Site QA | Mains & Sub-Mains | Level 1
|  | Level 2 | dynamic | Site QA | Mains & Sub-Mains | Level 2
|  | Level 3 | dynamic | Site QA | Mains & Sub-Mains | Level 3
|  | Level 4 | dynamic | Site QA | Mains & Sub-Mains | Level 4
|  | Level 5 | dynamic | Site QA | Mains & Sub-Mains | Level 5
|  | Level 6 | dynamic | Site QA | Mains & Sub-Mains | Level 6
|  | Level 7 | dynamic | Site QA | Mains & Sub-Mains | Level 7
|  | Level 8 | dynamic | Site QA | Mains & Sub-Mains | Level 8
|  | Level 9 | dynamic | Site QA | Mains & Sub-Mains | Level 9
|  | Level 10 | dynamic | Site QA | Mains & Sub-Mains | Level 10
|  | Level 11 | dynamic | Site QA | Mains & Sub-Mains | Level 11
|  | Level 12 | dynamic | Site QA | Mains & Sub-Mains | Level 12
Columns
|  | Determine cable run (start & end, cable tray position etc) |  | Determine cable run (start and end, cable tray position etc)
|  | Measure cable runs with appropriate accurate measuring instrument eg: tape measure, wheel, rope in conduit |  | Measure cable runs with appropriate accurate measuring instrument eg: tape measure, wheel, rope in conduit
|  | Confirm length of cable |  | Confirm length of cable
|  | Confirm cable size, type etc. |  | Confirm cable size, type etc.
|  | Install cable in applicable method eg: cable stands, electric winch, pulleys etc |  | Install cable in applicable method eg: cable stands, electric winch, pulleys etc
|  | Any cable not terminated immediately must have the end taped covering the bare copper |  | Any cable not terminated immediately must have the end taped covering the bare copper
|  | Trefoil (refer to details on back for all options) cables & tie cables to support system |  | Trefoil (refer to details on back for all options) cables and tie cables to support system
|  | Ensure fire rated cable installed with stainless steel cable ties |  | Ensure fire rated cable installed with stainless steel cable ties
|  | Check cable requirements for cable identification & install |  | Check cable requirements for cable identification and install
|  | Ensure Cables are CLEARLY labelled at both ends |  | Ensure Cables are CLEARLY labelled at both ends
|  | Ensure area is left clean |  | Ensure area is left clean
|  | Photos |  | Photos
Switchboards Overall Progress
| Scope |  |  | Switchboards
Rows
|  | Basement | dynamic | Site QA | Switchboards | Basement
|  | Ground | dynamic | Site QA | Switchboards | Ground
|  | Ground/Mezzanine | dynamic | Site QA | Switchboards | Ground/Mezzanine
|  | Level 1 | dynamic | Site QA | Switchboards | Level 1
|  | Level 2 | dynamic | Site QA | Switchboards | Level 2
|  | Level 3 | dynamic | Site QA | Switchboards | Level 3
|  | Level 4 | dynamic | Site QA | Switchboards | Level 4
|  | Level 5 | dynamic | Site QA | Switchboards | Level 5
|  | Level 6 | dynamic | Site QA | Switchboards | Level 6
|  | Level 7 | dynamic | Site QA | Switchboards | Level 7
|  | Level 8 | dynamic | Site QA | Switchboards | Level 8
|  | Level 9 | dynamic | Site QA | Switchboards | Level 9
|  | Level 10 | dynamic | Site QA | Switchboards | Level 10
|  | Level 11 | dynamic | Site QA | Switchboards | Level 11
|  | Level 12 | dynamic | Site QA | Switchboards | Level 12
Columns
|  | DELIVERY CHECK FOR DAMAGE, PAINT FINISH, DIMENSIONS & DOORS AGAINST APPROVED SHOP DRAWING |  | DELIVERY CHECK FOR DAMAGE, PAINT FINISH, DIMENSIONS AND DOORS AGAINST APPROVED SHOP DRAWING
|  | CONFIRM SWITCHBOARD LABEL & LOCATION |  | CONFIRM SWITCHBOARD LABEL & LOCATION
|  | LOCATE & FIX INTO POSITION |  | LOCATE & FIX INTO POSITION
|  | INSTALL SUBMAINS CABLING AS APPROPRIATE EG. GLANDS, TRAY, DUCT |  | INSTALL SUBMAINS CABLING AS APPROPRIATE EG. GLANDS, TRAY, DUCT
|  | INSTALL LUGS & TERMINATE ONCE INSULATION RESISTANCE & POLARITY TESTS HAVE BEEN CONDUCTED |  | INSTALL LUGS AND TERMINATE ONCE INSULATION RESISTANCE AND POLARITY TESTS HAVE BEEN CONDUCTED
|  | ANY CABLES NOT TERMINATED PRIOR TO ENERGISATION MUST BE REMOVED FROM CUBICLE AT ORIGIN & HAVE ENDS COVERED IN HEATSHRINK |  | ANY CABLES NOT TERMINATED PRIOR TO ENERGISATION MUST BE REMOVED FROM CUBICLE AT ORIGIN AND HAVE ENDS COVERED IN HEATSHRINK. AT DESTINATION CABLES MUST BE COVERED IN HEATSHRINK AND BE CONTAINED IN A JUNCTION BOX
|  | CLEAN & VACUUM |  | CLEAN & VACUUM
|  | ORGANISE INPECTION BY INSPECTOR. LODGE PRESCRIBED / NON PRESCRIBED (AS APPLICABLE) CERTIFICATE OF ELECTRICAL SAFETY (IF REQUIRED). |  | ORGANISE INPECTION BY INSPECTOR. LODGE PRESCRIBED / NON PRESCRIBED (AS APPLICABLE) CERTIFICATE OF ELECTRICAL SAFETY (IF REQUIRED).
|  | CLEARLY IDENTIFY SERVICES |  | CLEARLY IDENTIFY SERVICES
|  | WHEN READY TO ENERGISE PROCEED IN ACCORDANCE WITH ENERGISATION PROCEDURE |  | WHEN READY TO ENERGISE PROCEED IN ACCORDANCE WITH ENERGISATION PROCEDURE
|  | ENERGIZE & RECORD RESULTS |  | ENERGIZE & RECORD RESULTS
|  | CHECK SWITCHBOARD AS INSTALLED MATCHES SHOP DRAWING. IF NECCESARY MODIFY SHOP DRAWING TO MATCH INSTALLED & RETURN TO OFFICE |  | CHECK SWITCHBOARD AS INSTALLED MATCHES SHOP DRAWING. IF NECCESARY MODIFY SHOP DRAWING TO MATCH INSTALLED & RETURN TO OFFICE
|  | CLEAN SWITCHBOARD CUPBOARD |  | CLEAN SWITCHBOARD CUPBOARD
|  | INSTALL SUB CIRCUIT CABLING IN ACCORDANCE WITH DB SCHEDULE & TERMINATE |  | INSTALL SUB CIRCUIT CABLING IN ACCORDANCE WITH DB SCHEDULE AND TERMINATE. if circuit not complete at the other end, it must not be terminated BUT PLACED IN A JUNCTION BOX AT FIELD END AND IN CONNECTORS AT dISTRIBUTION BOARD END.
|  | CLEAN & VACUUM |  | CLEAN & VACUUM
|  | RECORD RELEVANT INFORMATION & ANY CHANGES ON DB SCHEDULE. & RETURN TO ADMINISTRATOR/OFFICE FOR COMMISSIONING TEAM |  | RECORD RELEVANT INFORMATION AND ANY CHANGES ON DB SCHEDULE. AND RETURN TO ADMINISTRATOR/OFFICE FOR COMMISSIONING TEAM
|  | Ensure area is left clean |  | Ensure area is left clean
|  | Photos |  | Photos
Rough In Overall Progress
| Scope |  |  | Rough In
Rows
|  | Basement | dynamic | Site QA | Rough In | Basement
|  | Ground | dynamic | Site QA | Rough In | Ground
|  | External | dynamic | Site QA | Rough In | External
|  | Ground/Mezzanine | dynamic | Site QA | Rough In | Ground/Mezzanine
|  | Level 1 | dynamic | Site QA | Rough In | Level 1
|  | Level 2 | dynamic | Site QA | Rough In | Level 2
|  | Level 3 | dynamic | Site QA | Rough In | Level 3
|  | Level 4 | dynamic | Site QA | Rough In | Level 4
|  | Level 5 | dynamic | Site QA | Rough In | Level 5
|  | Level 6 | dynamic | Site QA | Rough In | Level 6
|  | Level 7 | dynamic | Site QA | Rough In | Level 7
|  | Level 8 | dynamic | Site QA | Rough In | Level 8
|  | Level 9 | dynamic | Site QA | Rough In | Level 9
|  | Level 10 | dynamic | Site QA | Rough In | Level 10
|  | Level 11 | dynamic | Site QA | Rough In | Level 11
|  | Level 12 | dynamic | Site QA | Rough In | Level 12
|  | Roof | dynamic | Site QA | Rough In | Roof
Columns
|  | Area clear, tidy & accessible |  | Area clear, tidy and accessible
|  | CO-ORDINATE WITH OTHER SERVICES (CHECK FOR ANY CLASHES) |  | CO-ORDINATE WITH OTHER SERVICES (CHECK FOR ANY CLASHES)
|  | CONFIRM SIZE OF CABLE TRAY |  | CONFIRM SIZE OF CABLE TRAY
|  | INSTALL FIXINGS & SUPPORTS AS NEEDED |  | INSTALL FIXINGS AND SUPPORTS AS NEEDED
|  | ENSURE FIRE RATED SECTIONS OF TRAY USE UNISTRUT, HOLD DOWN BRAKETS & NO MORE THAN 1500MM APART |  | ENSURE FIRE RATED SECTIONS OF TRAY USE UNISTRUT, HOLD DOWN BRAKETS & NO MORE THAN 1500MM APART
|  | INSTALL CABLE TRAY |  | INSTALL CABLE TRAY
|  | COMPLETE SKETCH/MARK UP DRAWING FOR FUTURE AS BUILTS |  | COMPLETE SKETCH/MARK UP DRAWING FOR FUTURE AS BUILTS
|  | Rough in all lighting feeds & label on plan |  | Rough in all lighting feeds and label on plan
|  | Rough in of all lighting circuits- inc Emg/Exits & sensors |  | Rough in of all lighting circuits- inc Emg/Exits and sensors
|  | Rough in of all external lights |  | Rough in of all external lights
|  | Mark all lighting cable runs on plan |  | Mark all lighting cable runs on plan
|  | Rough in all power feeds & label on plan |  | Rough in all power feeds and label on plan
|  | Rough in of all power circuits |  | Rough in of all power circuits
|  | Mark all power cable runs on plan |  | Mark all power cable runs on plan
|  | Check for clashes with other services |  | Check for clashes with other services
|  | Assess all relevent drawings to ensure cables are in appropriate location. |  | Assess all relevent drawings to ensure cables are in appropriate location.
|  | Intstall Earth tags (If applicable) |  | Intstall Earth tags (If applicable)
|  | Ensure all Quick Connects, 413s & J boxes are fit off (if applicable) |  | Ensure all Quick Connects, 413s & J boxes are fit off (if applicable)
|  | Ensure Cables are CLEARLY labelled at both ends |  | Ensure Cables are CLEARLY labelled at both ends
|  | Ensure all cables are neat, taped to studs & Easily Accessible for cut out |  | Ensure all cables are neat, taped to studs & Easily Accessible for cut out
|  | Make sure any junctions are left in an accessible area & clearly marked on relevent plans/uploaded to conqa |  | Make sure any junctions are left in an accessible area and clearly marked on relevent plans/uploaded to conqa
|  | Go over area & make sure it is 100% |  | Go over area and make sure it is 100%
|  | Power plans are uploaded with location of feeds & cable run |  | Power plans are uploaded with location of feeds and cable run
|  | Lighting plans are uploaded with location of feeds & cable run including dali route. |  | Lighting plans are uploaded with location of feeds and cable run including dali route.
|  | Photos of all walls & ceilings |  | Photos of all walls and ceilings
|  | INSTALL CABLE SUPPORT OR CONDUIT WHERE REQUIRED. |  | INSTALL CABLE SUPPORT OR CONDUIT WHERE REQUIRED.
|  | VERIFY CORRECT CABLE TYPE. |  | VERIFY CORRECT CABLE TYPE.
|  | REFER TO APPROVED DRAWINGS FOR CABLE NUMBERING SEQUENCE RELEVANT TO FINAL FIT OFF SEQUENCE & RECORD |  | REFER TO APPROVED DRAWINGS FOR CABLE NUMBERING SEQUENCE RELEVANT TO FINAL FIT OFF SEQUENCE & RECORD
|  | INSTALL CABLE WITHIN OR ON CABLE SUPPORT SYSTEMS MAINTAINING MIN SEGREGATIONS |  | INSTALL CABLE WITHIN OR ON CABLE SUPPORT SYSTEMS MAINTAINING MIN SEGREGATIONS, ENSURE VELCRO CABLE TIES ARE USED AS PER SPECIFICATION
|  | ROUGH IN ALL CAMERAS |  | ROUGH IN ALL CAMERAS
|  | ROUGH IN ALL CABLES TO DOORS, AUTODOORS, DURESS BUTTONS, BREAK GLASS ETC. |  | ROUGH IN ALL CABLES TO DOORS, AUTODOORS, DURESS BUTTONS, BREAK GLASS ETC.
|  | FORM CABLES INTO RELEVANT FIT-OFF GROUPS AT THE CABINET END. |  | FORM CABLES INTO RELEVANT FIT-OFF GROUPS AT THE CABINET END.
|  | Plan lighting control route in conjunction with supervisor. |  | Plan lighting control route in conjunction with supervisor.
|  | Rough in lighting control cable to all sensors & switches. |  | Rough in lighting control cable to all sensors and switches.
|  | All lighting control must be roughed in point to point, daisy chain style (no star points, two cables at each point only). |  | All lighting control must be roughed in point to point, daisy chain style (no star points, two cables at each point only).
|  | Lighting control route must be drawn clearly & precisely on dedicated plan |  | Lighting control route must be drawn clearly and precisely on dedicated plan, if there is a change or revision, a new plan must be created and superseded written on old plan.
|  | Upload lighting control plan to Conqa, use this spot as a place to upload any & all plan/revision of this drawing. |  | Upload lighting control plan to Conqa, use this spot as a place to upload any and all plan/revision of this drawing.
|  | Rough in of all booster cables applicable to the lighting control system (1.5mm2 twin active) |  | Rough in of all booster cables applicable to the lighting control system (1.5mm2 twin active)
|  | Ensure all cables are clearly labled & are to the appropriate length. |  | Ensure all cables are clearly labled and are to the appropriate length.
|  | Rough in of 2 x LT/ Emg/sensors |  | Rough in of 2 x LT/ Emg/sensors
|  | Rough in of Exit (Ground level Only) |  | Rough in of Exit (Ground level Only)
|  | Lighting plans are uploaded with location of feeds & cable run |  | Lighting plans are uploaded with location of feeds and cable run
|  | Ensure area is left clean |  | Ensure area is left clean
|  | Photos |  | Photos
Cut Out Overall Progress
| Scope |  |  | Cut Out
Rows
|  | Basement | dynamic | Site QA | Cut Out | Basement
|  | Ground | dynamic | Site QA | Cut Out | Ground
|  | Ground/Mezzanine | dynamic | Site QA | Cut Out | Ground/Mezzanine
|  | Level 1 | dynamic | Site QA | Cut Out | Level 1
|  | Level 2 | dynamic | Site QA | Cut Out | Level 2
|  | Level 3 | dynamic | Site QA | Cut Out | Level 3
|  | Level 4 | dynamic | Site QA | Cut Out | Level 4
|  | Level 5 | dynamic | Site QA | Cut Out | Level 5
|  | Level 6 | dynamic | Site QA | Cut Out | Level 6
|  | Level 7 | dynamic | Site QA | Cut Out | Level 7
|  | Level 8 | dynamic | Site QA | Cut Out | Level 8
|  | Level 9 | dynamic | Site QA | Cut Out | Level 9
|  | Level 10 | dynamic | Site QA | Cut Out | Level 10
|  | Level 11 | dynamic | Site QA | Cut Out | Level 11
|  | Level 12 | dynamic | Site QA | Cut Out | Level 12
|  | Roof | grouping | Roof
|  | Roof |  | Site QA | Cut Out | Roof
Columns
|  | Confirm sizes off all fittings prior to cut out |  | Confirm sizes off all fittings prior to cut out
|  | Cut out for all sensors, EX/EMG & light fittings |  | Cut out for all sensors, EX/EMG and light fittings
|  | Consult supervisor before cutting a patch of is a mistake is made |  | Consult supervisor before cutting a patch of is a mistake is made
|  | Cut out items on joinery to the joinery plans |  | Cut out items on joinery to the joinery plans
|  | Cut out switches |  | Cut out switches
|  | Cut out GPO's |  | Cut out GPO's
|  | Cut out any CCTV cameras |  | Cut out any CCTV cameras
|  | Ensure Electric Strike cable is inside the pressed metal frame cut out |  | Ensure Electric Strike cable is inside the pressed metal frame cut out
|  | Cut out bathrooms & other wet areas to relevent wet area plans |  | Cut out bathrooms and other wet areas to relevent wet area plans
|  | Locate all cables |  | Locate all cables
|  | Install Fire Boxes & hit all 4 tabs in |  | Install Fire Boxes and hit all 4 tabs in
|  | Fire caulk ( if applicable ) |  | Fire caulk ( if applicable )
|  | FIT OFF ALL 413'S + QC'S |  | FIT OFF ALL 413'S + QC'S
|  | Ensure area is left clean |  | Ensure area is left clean
|  | Photos |  | Photos
Fit Off Overall Progress
| Scope |  |  | Fit Off
Rows
|  | Basement | dynamic | Site QA | Fit Off | Basement
|  | Ground | dynamic | Site QA | Fit Off | Ground
|  | Ground/Mezzanine | dynamic | Site QA | Fit Off | Ground/Mezzanine
|  | Level 1 | dynamic | Site QA | Fit Off | Level 1
|  | Level 2 | dynamic | Site QA | Fit Off | Level 2
|  | Level 3 | dynamic | Site QA | Fit Off | Level 3
|  | Level 4 | dynamic | Site QA | Fit Off | Level 4
|  | Level 5 | dynamic | Site QA | Fit Off | Level 5
|  | Level 6 | dynamic | Site QA | Fit Off | Level 6
|  | Level 7 | dynamic | Site QA | Fit Off | Level 7
|  | Level 8 | dynamic | Site QA | Fit Off | Level 8
|  | Level 9 | dynamic | Site QA | Fit Off | Level 9
|  | Level 10 | dynamic | Site QA | Fit Off | Level 10
|  | Level 11 | dynamic | Site QA | Fit Off | Level 11
|  | Level 12 | dynamic | Site QA | Fit Off | Level 12
|  | Roof | grouping | Roof
|  | Roof |  | Site QA | Fit Off | Roof
Columns
|  | CHECK DRAWINGS FOR QUANTITY, BRAND TYPE & COLOUR |  | CHECK DRAWINGS FOR QUANTITY, BRAND TYPE AND COLOUR
|  | LOCATION/COMPLIANCE WET AREAS, HAZARDS ETC. MOUNTING HEIGHTS, |  | LOCATION/COMPLIANCE WET AREAS, HAZARDS ETC. MOUNTING HEIGHTS,
|  | FIT OFF & FIX SWITCHES, EACH CIRCUIT MUST BE FITTED OFF COMPLETELY. |  | FIT OFF AND FIX SWITCHES, EACH CIRCUIT MUST BE FITTED OFF COMPLETELY.
|  | FIT OFF & FIX GPO’S, EACH CIRCUIT MUST BE FITTED OFF COMPLETELY. |  | FIT OFF AND FIX GPO’S, EACH CIRCUIT MUST BE FITTED OFF COMPLETELY.
|  | COVER PLATES (IF REQUIRED) |  | COVER PLATES (IF REQUIRED)
|  | INSTALL LABEL (IF A SPECIFIED REQUIREMENT) |  | INSTALL LABEL (IF A SPECIFIED REQUIREMENT)
|  | DELIVERY CHECK FOR DAMAGE & CORRECT QUANTITIES |  | DELIVERY CHECK FOR DAMAGE AND CORRECT QUANTITIES
|  | LOCATIONS CO ORDINATE WITH OTHER SERVICES |  | LOCATIONS CO ORDINATE WITH OTHER SERVICES
|  | MARKING OUT IF REQUIRED - REFER TO REFLECTED CEILING PLAN FOR SET OUT |  | MARKING OUT IF REQUIRED - REFER TO REFLECTED CEILING PLAN FOR SET OUT
|  | PLUG IN OR FIT OFF LIGHT / PLUG BASE |  | PLUG IN OR FIT OFF LIGHT / PLUG BASE
|  | INSTALL LIGHT FITTING (Take note of Mounting heights, locations etc) |  | INSTALL LIGHT FITTING (Take note of Mounting heights, locations etc)
|  | INSTALL LAMPS & DIFFUSER |  | INSTALL LAMPS AND DIFFUSER
|  | CLEAN FITTING, LAMP DIFFUSER |  | CLEAN FITTING, LAMP DIFFUSER
|  | Ensure Electric Strike cable is inside the pressed metal frame cut out |  | Ensure Electric Strike cable is inside the pressed metal frame cut out
|  | Locate all Cables |  | Locate all Cables
|  | Install Firebox’s |  | Install Firebox’s
|  | Area clear, tidy & accessible |  | Area clear, tidy and accessible
|  | Dediacte one person to be in charge of lighting control fitoff. |  | Dediacte one person to be in charge of lighting control fitoff.
|  | Always use the correct tools to fitoff the lighting control equiptment |  | Always use the correct tools to fitoff the lighting control equiptment
|  | Fitoff all sensors |  | Fitoff all sensors
|  | Fit off all switches |  | Fit off all switches
|  | Stick barcode of sensor/switch onto the designated plan in the location of the sensor/switch |  | Stick barcode of sensor/switch onto the designated plan in the location of the sensor/switch
|  | Make sure all installed items are clean & undamaged. |  | Make sure all installed items are clean and undamaged.
|  | COMPLETE WALL OR CEILING CUT OUT WHERE REQUIRED |  | COMPLETE WALL OR CEILING CUT OUT WHERE REQUIRED
|  | TEST & ENSURE SUB CIRCUIT CABLING IS NOT LIVE PRIOR TO FIT OFF |  | TEST & ENSURE SUB CIRCUIT CABLING IS NOT LIVE PRIOR TO FIT OFF
|  | TERMINATE CABLE TO OUTLET OR PLUG BASE, CHECK CORRECT CONNECTIONS & FIX TO SURFACE |  | TERMINATE CABLE TO OUTLET OR PLUG BASE, CHECK CORRECT CONNECTIONS AND FIX TO SURFACE, IF CIRCUIT CAN NOT BE FULLY TERMINATED A JUNCTION BOX MUST BE INSTALLED WHERE REQUIRED
|  | CLEAN AREA AS REQUIRED |  | CLEAN AREA AS REQUIRED
|  | RECORD ANY RELEVANT INFORMATION ON DRAWINGS. |  | RECORD ANY RELEVANT INFORMATION ON DRAWINGS.
|  | COORDINATE LOCATIONS WITH OTHER SERVICES |  | COORDINATE LOCATIONS WITH OTHER SERVICES
|  | MARKING OUT (IF REQUIRED) REFER TO DRAWINGS FOR LOCATIONS |  | MARKING OUT (IF REQUIRED) REFER TO DRAWINGS FOR LOCATIONS
|  | PLUG IN OR FIT OFF LIGHT, FIT OFF DATA CABLE IF REQUIRED |  | PLUG IN OR FIT OFF LIGHT, FIT OFF DATA CABLE IF REQUIRED
|  | INSTALL LAMP & DIFFUSER & CLEAN FITTING |  | INSTALL LAMP & DIFFUSER AND CLEAN FITTING
|  | INSTALL EMERGENCY BARCODE TO FITTING & TO DRAWINGS (IF REQUIRED) OR, |  | INSTALL EMERGENCY BARCODE TO FITTING AND TO DRAWINGS (IF REQUIRED) OR,
|  | NUMBER FITTINGS AS PER VAST SHOP DRAWINGS. |  | NUMBER FITTINGS AS PER VAST SHOP DRAWINGS.
|  | UPDATE ANY CHANGES FOR AS BUILTS |  | UPDATE ANY CHANGES FOR AS BUILTS
|  | COMPLETE LOG BOOK |  | COMPLETE LOG BOOK
|  | COMPLETE INITIAL 2 HOUR TEST |  | COMPLETE INITIAL 2 HOUR TEST
|  | RECORD RESULTS |  | RECORD RESULTS
|  | VISUAL CHECK ENSURING CABLE TO BE FITTED OFF IN CORRECT POSITION. |  | VISUAL CHECK ENSURING CABLE TO BE FITTED OFF IN CORRECT POSITION.
|  | SELECTION OF CORRECT TOOL TO BE USED FOR TERMINATION TYPE. |  | SELECTION OF CORRECT TOOL TO BE USED FOR TERMINATION TYPE.
|  | ENSURE CABLES ARE STRIPPED NO MORE THAN THE SPECIFIED DISTANCE |  | ENSURE CABLES ARE STRIPPED NO MORE THAN THE SPECIFIED DISTANCE. CHECK TERMINATIONS AT COMPLETION FOR COLOUR CODE AND SEQUENCE.
|  | ATTACH WRAP AROUND LABEL TO CABLE NO MORE THAN 60MM FROM THE JACK |  | ATTACH WRAP AROUND LABEL TO CABLE NO MORE THAN 60MM FROM THE JACK. ENSURING CORRECT NUMBER SEQUENCE.
|  | DRESS CABLES TO FINAL LOCATION. ENSURE VELCRO STRAPS FOR CAT 6 CABLING |  | DRESS CABLES TO FINAL LOCATION. ENSURE VELCRO STRAPS FOR CAT 6 CABLING
|  | INSTALL JACK INTO WORKSTATION OR WALL OUTLET. |  | INSTALL JACK INTO WORKSTATION OR WALL OUTLET.
|  | INSTALL PATCH PANEL INTO CABINET LOOM CABLES TO THE BACK OF THE PATCH PANEL |  | INSTALL PATCH PANEL INTO CABINET LOOM CABLES TO THE BACK OF THE PATCH PANEL. TIE INTO POSITION USING VELCRO STRIP AND/OR CABLE TIES SUPPLIED.
|  | PATCH OUTLETS TO HARDWARE DEVICES WHERE APPLICABLE & CHECK FOR CORRECT OPERATION. |  | PATCH OUTLETS TO HARDWARE DEVICES WHERE APPLICABLE AND CHECK FOR CORRECT OPERATION.
|  | LABEL OUTLET ENSURING CORRECT NUMBER SEQUENCE |  | LABEL OUTLET ENSURING CORRECT NUMBER SEQUENCE
|  | COMPLETE CERTIFICATION AS REQUIRED |  | COMPLETE CERTIFICATION AS REQUIRED
|  | Ensure danger tags have up to date contact & isolation details |  | Ensure danger tags have up to date contact & isolation details
|  | LOCK OFF & TAG circuits that require isolation (Ensure key is with supervisor) |  | LOCK OFF & TAG circuits that require isolation (Ensure key is with supervisor)
|  | Test circuits to ensure they are isolated |  | Test circuits to ensure they are isolated
|  | Fit off all Lights |  | Fit off all Lights
|  | Fit off of 4 pin plug |  | Fit off of 4 pin plug
|  | Fit off all Sensors & SET TIME TO MINIMUM |  | Fit off all Sensors and SET TIME TO MINIMUM
|  | Fit off all EX/EMG’s |  | Fit off all EX/EMG’s
|  | Label all EX/EMG’s as per plan number |  | Label all EX/EMG’s as per plan number
|  | Fit off all GPOs |  | Fit off all GPOs
|  | Fit off of all isolators (signs, hand dryers, hws) |  | Fit off of all isolators (signs, hand dryers, hws)
|  | Ensure all fit off has been ticked off on plans once completed |  | Ensure all fit off has been ticked off on plans once completed
|  | WET AREAS to be above 300 from FFL- UNDER 40L SINK to be 150mm/400mm rule- OVER 40L SINK to be 500mm/1000mm rule |  | WET AREAS to be above 300 from FFL- UNDER 40L SINK to be 150mm/400mm rule- OVER 40L SINK to be 500mm/1000mm rule
|  | FIT OFF & FIX SWITCHES |  | FIT OFF AND FIX SWITCHES
|  | FIT OFF & FIX GPO’S |  | FIT OFF AND FIX GPO’S
|  | FIT OFF FINAL APPLIANCES WITH PHOTOS |  | FIT OFF FINAL APPLIANCES WITH PHOTOS
|  | INSTALL LIGHT FITTING |  | INSTALL LIGHT FITTING
|  | Ensure area is left clean |  | Ensure area is left clean
|  | Photos |  | Photos
Commissioning Overall Progress
| Scope |  |  | Commissioning
Rows
|  | Mains - Basement | dynamic | Site QA | Commissioning | Mains | Basement
|  | Mains - Ground | dynamic | Site QA | Commissioning | Mains | Ground
|  | Mains - Ground/Mezzanine | dynamic | Site QA | Commissioning | Mains | Ground/Mezzanine
|  | Mains - Level 1 | dynamic | Site QA | Commissioning | Mains | Level 1
|  | Mains - Level 2 | dynamic | Site QA | Commissioning | Mains | Level 2
|  | Mains - Level 3 | dynamic | Site QA | Commissioning | Mains | Level 3
|  | Mains - Level 4 | dynamic | Site QA | Commissioning | Mains | Level 4
|  | Mains - Level 5 | dynamic | Site QA | Commissioning | Mains | Level 5
|  | Mains - Level 6 | dynamic | Site QA | Commissioning | Mains | Level 6
|  | Mains - Level 7 | dynamic | Site QA | Commissioning | Mains | Level 7
|  | Mains - Level 8 | dynamic | Site QA | Commissioning | Mains | Level 8
|  | Mains - Level 9 | dynamic | Site QA | Commissioning | Mains | Level 9
|  | Mains - Level 10 | dynamic | Site QA | Commissioning | Mains | Level 10
|  | Mains - Level 11 | dynamic | Site QA | Commissioning | Mains | Level 11
|  | Mains - Level 12 | dynamic | Site QA | Commissioning | Mains | Level 12
|  | Field - Basement | dynamic | Site QA | Commissioning | Field | Basement
|  | Field - Ground | dynamic | Site QA | Commissioning | Field | Ground
|  | Field - Ground/Mezzanine | dynamic | Site QA | Commissioning | Field | Ground/Mezzanine
|  | Field - Level 1 | dynamic | Site QA | Commissioning | Field | Level 1
|  | Field - Level 2 | dynamic | Site QA | Commissioning | Field | Level 2
|  | Field - Level 3 | dynamic | Site QA | Commissioning | Field | Level 3
|  | Field - Level 4 | dynamic | Site QA | Commissioning | Field | Level 4
|  | Field - Level 5 | dynamic | Site QA | Commissioning | Field | Level 5
|  | Field - Level 6 | dynamic | Site QA | Commissioning | Field | Level 6
|  | Field - Level 7 | dynamic | Site QA | Commissioning | Field | Level 7
|  | Field - Level 8 | dynamic | Site QA | Commissioning | Field | Level 8
|  | Field - Level 9 | dynamic | Site QA | Commissioning | Field | Level 9
|  | Field - Level 10 | dynamic | Site QA | Commissioning | Field | Level 10
|  | Field - Level 11 | dynamic | Site QA | Commissioning | Field | Level 11
|  | Field - Level 12 | dynamic | Site QA | Commissioning | Field | Level 12
|  | Roof | grouping | Roof
|  | Roof |  | Site QA | Commissioning | Field | Roof
Columns
|  | Submit Energisation Request Form to builder with plans of areas to be energised highlighted |  | Submit Energisation Request Form to builder with plans of areas to be energised highlighted
|  | Prior To Energising All Personnel Involved To Be Inducted Into Energisation Procedure |  | Prior To Energising All Personnel Involved To Be Inducted Into Energisation Procedure And All Steps Undertaken To Ensurecompliance With This Procedure
|  | Place all required signage & barricading & have LV rescue kit on standby. |  | Place all required signage and barricading and have LV rescue kit on standby.
|  | Refer To As Installed Drawings |  | Refer To As Installed Drawings
|  | Obtain Copy Of Switchboard Schedule & Schematic Drawings |  | Obtain Copy Of Switchboard Schedule And Schematic Drawings
|  | Mark Up Any Additions Or Deletions Found Whilst Commissioing |  | Mark Up Any Additions Or Deletions Found Whilst Commissioing
|  | Complete Visual Checks |  | Complete Visual Checks
|  | Refer To Mandatory Testing From As/Nzs 3000:2018 8.3.3 Below |  | Refer To Mandatory Testing From As/Nzs 3000:2018 8.3.3 Below
|  | Complete Mandatory Tests Using Metrel Tester, Save & Log Results On Tester |  | Complete Mandatory Tests Using Metrel Tester, Save And Log Results On Tester
|  | Any Failed Results To Be Rectified Saved & Logged On Tester |  | Any Failed Results To Be Rectified Saved And Logged On Tester
|  | Ensure Correct Opertation Of All Control/Equipment Installed In Switchboard |  | Ensure Correct Opertation Of All Control/Equipment Installed In Switchboard
|  | Ensure Vast Witness Test Has Been Completed |  | Ensure Vast Witness Test Has Been Completed
|  | Ensure Escutcheons, Pole Fillers, Fixing Screws Are Reinstated |  | Ensure Escutcheons, Pole Fillers, Fixing Screws Are Reinstated
|  | Ensure No Access To Live Parts |  | Ensure No Access To Live Parts
|  | Complete Switchboard Schedules On Vast Template, Install & Fix To Allocated Postion In Switchboard |  | Complete Switchboard Schedules On Vast Template, Install And Fix To Allocated Postion In Switchboard
|  | Download Test Results From Metrel Tester & Save To Project Folder |  | Download Test Results From Metrel Tester And Save To Project Folder
|  | Complete Certificate Of Electrical Safety & Save To Project Folder |  | Complete Certificate Of Electrical Safety And Save To Project Folder
|  | Energisation permit completed prior to energisation & submitted to builder with plans of areas to be energised highlighted |  | Energisation permit completed prior to energisation and submitted to builder with plans of areas to be energised highlighted
|  | Address site at prestart & inform of no access to area under commissioning. |  | Address site at prestart and inform of no access to area under commissioning.
|  | Place all relevent signage & barricading & have LV rescue kit on standby. |  | Place all relevent signage and barricading and have LV rescue kit on standby.
|  | Visual check of DB serviced areas |  | Visual check of DB serviced areas
|  | Dead Testing |  | Dead Testing
|  | Live Testing |  | Live Testing
|  | Ensure Correct Opertation Of All equipment |  | Ensure Correct Opertation Of All equipment
|  | Conduct test on lighting control switches |  | Conduct test on lighting control switches
|  | Check operation of all sensors (individually on minimum time setting ) |  | Check operation of all sensors (individually on minimum time setting )
|  | Check sensors are set to specified time & lux |  | Check sensors are set to specified time and lux
|  | Test 4 pin plug base for switching (if applicable) |  | Test 4 pin plug base for switching (if applicable)
|  | Fit cover plates to all GPO’s, switches, Exit signs etc . |  | Fit cover plates to all GPO’s, switches, Exit signs etc .
|  | Report any issues to supervisor & generate plan to rectify (if any) |  | Report any issues to supervisor and generate plan to rectify (if any)
|  | REFER TO INSTALLED DRAWINGS |  | REFER TO INSTALLED DRAWINGS
|  | Test terminations using COPPER STRUCTURED CABLING tester & LOG RESULTS |  | Test terminations using COPPER STRUCTURED CABLING tester AND LOG RESULTS
|  | RECTIFY ANY FAILED RESULTS, RE-TEST & LOG |  | RECTIFY ANY FAILED RESULTS, RE-TEST AND LOG
|  | LABEL FRAMES & PATCH PANELS |  | LABEL FRAMES AND PATCH PANELS
|  | COMPLETE PATCH PANEL SCHEDULE |  | COMPLETE PATCH PANEL SCHEDULE
|  | DOWNLOAD RESULTS FROM TESTER TO PROJECT FOLDER |  | DOWNLOAD RESULTS FROM TESTER TO PROJECT FOLDER
|  | Ensure area is left clean |  | Ensure area is left clean
|  | Photos |  | Photos
Exit & Emergency Testing Overall Progress
| Scope |  |  | Exit & Emergency Testing
Rows
|  | Exit & Emergency Testing | dynamic | Exit & Emergency Testing
Columns
|  | Start Time | Start Time | Drawing Rev No.
|  | Lamp Duration | Lamp Duration | Drawing Rev No.
|  | Starter Switch | Starter Switch | Drawing Rev No.
|  | Charge Indicator | Charge Indicator | Drawing Rev No.
|  | Test Switch | Test Switch | Drawing Rev No.
|  | Circuit Board | Circuit Board | Drawing Rev No.
|  | Clean Diffuser | Clean Diffuser | Drawing Rev No.
|  | Pass Fail N/A |  | Pass Fail N/A
|  | COMPLETE LOG BOOK |  | COMPLETE LOG BOOK
|  | Comment | add comment | COMPLETE LOG BOOK
|  | Ensure area is left clean |  | Ensure area is left clean
|  | Photos |  | Photos
Conqa Summary
| Scope |  |  | Conqa Summary
Rows
|  | Conqa Summary | dynamic | Conqa Summary
Columns
|  | Upload Doc |  | Upload Doc
Preventative Maintenance Checklist
| Scope |  |  | Preventative Maintenance Checklist
Rows
|  | 6 month |  | Preventative Maintenance Checklist | 6 month
|  | 12 month |  | Preventative Maintenance Checklist | 12 month
Columns
|  | Visual Inspection of Electrical Installation |  | Visual Inspection of Electrical Installation
|  | Exit & Emergency Lighting Testing Carried Out & Logbook Completed |  | Exit & Emergency Lighting Testing Carried Out & Logbook Completed
|  | Operation of Switchboards Checked |  | Operation of Switchboards Checked
|  | Operation of Lighting Control Checked |  | Operation of Lighting Control Checked
|  | Check & Replace Fault Lamps |  | Check & Replace Fault Lamps
|  | Fire Detection System Test carried Out |  | Fire Detection System Test carried Out
|  | Fire Detection System Test Results Issued |  | Fire Detection System Test Results Issued
|  | Switchboard Thermal Imaging Test Carried Out & Report Completed |  | Switchboard Thermal Imaging Test Carried Out & Report Completed
|  | Solar |  | Solar
|  | UPS |  | UPS
|  | Data & Communications |  | Data & Communications
|  | Ensure area is left clean |  | Ensure area is left clean
|  | Photos |  | Photos