## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP045 - ALER 3 Fire Services | itp |  |  |  |  | FH-ZU2-QU-ITP045 - ALER 3 Fire Services - Rev 0
section | 1.0 - Preliminary Activities
checkpoint | 1.1 - Check for correct documentation
label | Frequency - Prior to commencing works
label | Acceptance Criteria - Current revision of drawings, technical specifications and any other construction documentation is being utilised by Fulton Hogan and subcontractors.
label | ○ Current revisions of these documents to be obtained via Aconex or ACC.
label | Reference Documents - Current Revisions in Aconex or ACC
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed
label | HP*
label | Responsibility - Project / Site Engineer
date | Date Completed:
checkpoint | 1.2 - Implementation of all measures and controls
label | Frequency - Prior to commencing works
label | Acceptance Criteria - All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, SWMS & WMS
label | Reference Documents - PSP, EMP, TMP, SWMS, WMS
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed
label | HP*
label | Responsibility - Project / Site Engineer
date | Date Completed:
checkpoint | 1.3 - Submission & approval of shop drawings
label | Frequency - Prior to commencing works
label | Acceptance Criteria - HOLD POINT
label | ○ Submit shop drawings, calculation reports & cause & effect matrix to the principal’s representative for approval prior to fabrication commencement.
label | Reference Documents - ZULU-BECA-001-SPC-00005, Drawing Package 030-32
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed, Aconex Ref
label | HP
label | Responsibility - Project Engineer / Site Engineer / Principal’s Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.4 - Material Submissions
label | Frequency - Prior to commencing works
label | Acceptance Criteria - Items to include but not limited to:
label | ○ Fire Indicator Panel (main & Sub)
label | ○ VESDA Panel
label | ○ Agent Release Control Panel
label | ○ Manual gas release/aborting switch
label | ○ Alarm Speaker
label | ○ Horn Speaker
label | ○ Visual Alarms
label | ○ Manual Call Points
label | ○ Visual Alarm Devices (Internal & external)
label | ○ All related signage
label | ○ Smoke Detectors
label | ○ Thermal Detectors
label | ○ Gas cylinders
label | ○ Pipes, connections, and valves
label | ○ Sampling Points and pipes
label | ○ Pressure relief vent
label | Reference Documents - ZULU-BECA-001-SPC-00005, C2300.6.1, C2300.6.3
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed, Aconex Ref
label | HP*
label | Responsibility - Project / Site Engineer
date | Date Completed:
checkpoint | 1.5 - Survey Set out
label | Frequency - Prior to commencing works
label | Acceptance Criteria - Confirm survey set out has been completed on site prior to commencement of works
label | Reference Documents - Survey Process
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed
label | HP*
label | Responsibility - Project / Site Engineer
date | Date Completed:
section | 2.0 - Construction
checkpoint | 2.1 - Installation of Gaseous Suppression System
label | Frequency - Each Lot
label | Acceptance Criteria - Installation of Fire Suppression System as per shop drawings and manufacturer specifications. Check for
label | ○ Correct pipe support spacing
label | ○ Penetrations are fire rated as required
label | ○ In accordance with approved drawings
label | ○ Gas cylinders
label | ○ Pipes, connections and valves
label | ○ Manual gas release/aborting switch
label | ○ Agent release control panel
label | Reference Documents - Drawing Package 030-32, ZULU-BECA-001-SPC-00005, C2300
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed, BE ITC
label | IP
label | Responsibility - Project / Site Engineer
date | Date Completed:
checkpoint | 2.2 - Installation of VESDA Fire Detection
label | Frequency - Each Lot
label | Acceptance Criteria - Installation of VESDA fire detection system as per drawings and manufacturer specification. Check installation of:
label | ○ VESDA Pipes
label | ○ VESDA Panel
label | ○ End cap with sampling point
label | ○ 2 way valves
label | Reference Documents - Drawing Package 030-32, ZULU-BECA-001-SPC-00005, C2300
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed, BE ITC
label | IP
label | Responsibility - Project / Site Engineer
date | Date Completed:
checkpoint | 2.3 - Installation of Fire Alarm & Warning System
label | Frequency - Each Lot
label | Acceptance Criteria - Installation of Fire Alarm & Warning Systems as per drawings & Specifications. Check installation of:
label | ○ Alarm Speaker
label | ○ Horn Speaker
label | ○ Visual Alarms
label | ○ Manual Call Points
label | ○ Visual Alarm Devices (Internal & external)
label | ○ All related signage
label | ○ Smoke Detectors
label | ○ Thermal Detectors
label | Reference Documents - Drawing Package 030-32
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed, BE ITC
label | IP
label | Responsibility - Project / Site Engineer
date | Date Completed:
checkpoint | 2.4 - Installation of FDCIE & SFDCIE
label | Frequency - Each Lot
label | Acceptance Criteria - Ensure FDCIE installed in correct position as per IFC drawing
label | ○ Ensure SFDCIE installed in correct position as per IFC drawing
label | Reference Documents - Drawing Package 030-32 ZULU-BECA- 001-SPC-00005 C2300
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed, BE ITC
label | WP IP
label | Responsibility - Project / Site Engineer
date | Date Completed:
checkpoint | 2.5 - Installation of Fire Doors
label | Frequency - Each Lot
label | Acceptance Criteria - Ensure the door closers are fitted and adjusted correctly to close shut once opened.
label | ○ Verify the door is fireproof door.
label | — Confirm S/N Tags
label | ○ Certificate proving fire door is compliant to AS/NZS 1905.1
label | ○ Ensure the ‘fire door do not obstruct’ sign is installed.
label | Reference Documents - ZULU-BECA-001-SPC-00005 – 0453, AS/NZS 1905.1
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed, Fire Door Certificate, BE ITC
label | WP IP
label | Responsibility - Project / Site Engineer
date | Date Completed:
checkpoint | 2.6 - Installation of Fire Extinguishers
label | Frequency - Each Lot
label | Acceptance Criteria - All fire extinguishers installed as per approved layout. Check:
label | ○ Installed with horn, wall bracket and visual indicator
label | ○ Correct type
label | ○ Housed in a lockable enclosed metal cabinet
label | ○ Key to each cabinet shall be secured in a break glass box
label | ○ Fire Extinguisher Signs Installed
label | ○ Fire Extinguishers have tags up to date
label | Reference Documents - ZULU-BECA-001-SPC-00005, C2300.2 C2345.1 AS2444 BCA 2022, AS/NZS 2444
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed, BE ITC
label | IP
label | Responsibility - Project / Site Engineer
date | Date Completed:
checkpoint | 2.7 - Air Tightness
label | Frequency - Each Lot
label | Acceptance Criteria - Ensure protected rooms are adequately sealed for the proper functioning of the gas suppression system. The necessary airtightness measures shall be undertaken
label | ○ Conduct room integrity test to AS1851 and provide certification
label | Reference Documents - ZULU-BECA-001-SPC-00005, C2300.2.2 (ix), AS1851
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed, Certificate, BE ITC
label | HP*
label | Responsibility - Project / Site Engineer
date | Date Completed:
checkpoint | Final Inspection
label | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality \System Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
date | Work Completed On:
date | Date: