## Break down
Edmund Hillary Audit Repairs - Job #75340
Entire Village
1. Fire to Nurse Call interface test
Programme all Annunciators in the Village with text scrolling (Attach Photos)
SCU
5. Display - SCU Lounge
Tie up Ethernet connection cable that is hanging below the display (Attach Photos)
Clean the display, as it is dirty (Attach Photos)
6. SCU - 402
Check Pendant removal alarm - activates after a long delay (Attach Photos)
7. SCU - 404
Check Door alarm - activates after a long delay (30 Seconds) when DCS is active (Attach Photos)
8. SCU - 405
Check DCS - failed to track movements inside the room (Attach Photos)
9. SCU - 406
Bedroom light is not working when DCS is active - please check (Attach Photos)
Check DCS panel at door - shows incorrect movements (Attach Photos)
10. SCU - 408
Install surrounding plate for the bed mat socket (Attach Photos)
11. SCU - 411
Install surrounding plate for the bed mat socket (Attach Photos)
12. SCU - 424
Check Pendant removal alarm - activates after a long delay (Attach Photos)
13. SCU - 429
Correct Nurse Presence Call Point - it is installed upside down (Attach Photos)
Serviced Apartments
14. Serviced Apartment - 110
Check reassurance LED on Bedroom and WC Call Points, very dim and hardly visible (Attach Photos)
15. Serviced Apartment - 112
Check Staff Assist alarm, it's not working (Attach Photos)
16. Serviced Apartment - 114
Check Shower Pull Cord reassurance LED, it's not working (Attach Photos)
17. Serviced Apartment - 204
Check Short-Range wireless pendant, as it failed (Attach Photos)
18. Serviced Apartment - 205
Check Staff Assist alarm, it's not working (Attach Photos)
19. Serviced Apartment - 206
Check Alarm generated by Bedhead Call Point - generating Resident Call when it should be Emergency Alarm (Attach Photos)
20. Serviced Apartment - 210
Check Alarm generated by Bedhead Call Point - generating Resident Call when it should be Emergency Alarm (Attach Photos)
21. Serviced Apartment - 308
Check Shower Pull Cord reassurance LED, it's not working (Attach Photos)
22. Serviced Apartment - 315
Check Shower Pull Cord, it gets stuck during pull test and needs to be manually pushed back to reset the alarm (Attach Photos)
23. Serviced Apartment - 318
Check ODL - brightness is very low and hardly visible (Attach Photos)
24 and 25. Serviced Apartment - 320
Check Shower Pull Cord, as it failed (Attach Photos)
Check Short-Range pendant, as it fails intermittently (Attach Photos)
Rest Home
26. Rest Home Room - 314
Install surrounding cover on the Ensuite Toilet Call Point (Attach Photos)
27. Rest Home Room - 316
Check Nurse Presence Call Point - it's not working and causes the virtual Staff Assist alarm to fail as well (Attach Photos)
28. Rest Home Room - 329
Check Shower Pull Cord, as it failed (Attach Photos)
29. Rest Home Room - 334
Check Pendant removal alarm, as it fails intermittently (Attach Photos)
30. Rest Home Room - 335
Replace Ensuite Toilet Call Point - requires very hard pressing to activate (Attach Photos)
31. Rest Home Room - 336
Replace Ensuite Toilet Call Point - requires very hard pressing to activate (Attach Photos)
32. Rest Home Room - 338
Check Floor Pressure mat, as it failed (Attach Photos)
33. Rest Home - Lounge 2
Check ODL, as it failed (Attach Photos)
Hospital
4 and 154. Display - Hospital 2 - Ollivier
Check Displays in the Hallway near Room 228, one looks like it has no power (Attach Photos)
34 and 35. Hospital 2 - Room 203
Check Staff Assist alarm, text description is wrong on the displays - shows "H208" (Attach Photos)
Check Floor Pressure mat, as it failed (Attach Photos)
36. Hospital 2 - Room 207
Install surrounding cover on the Bedhead Call Point (Attach Photos)
37. Hospital 2 - Room 208
Install surrounding cover on the Bedhead Call Point (Attach Photos)
38 and 39. Hospital 2 - Room 210
Check Staff Assist Alarm, as it failed (Attach Photos)
Check Floor Pressure mat, as it failed (Attach Photos)
40. Hospital 2 - Room 212
Replace Bedhead Call Point - requires very hard pressing to activate (Attach Photos)
41. Hospital 2 - Room 219
Replace Bedhead Call Point - requires very hard pressing to activate (Attach Photos)
42. Hospital 2 - Room 220
Install surrounding cover on the Bedhead Call Point (Attach Photos)
43. Hospital 2 - Room 221
Tidy wireless pendant cables (Attach Photos)
Mount receiver onto the wall (Attach Photos)
44. Hospital 2 - Room 223
Check wired pendant lead, as it failed (Attach Photos)
45. Hospital 2 - Room 225
Change Ensuite Toilet from Emergency Call Point to a Resident Call Point (Attach Photos)
46. Hospital 2 - Room 226
Change Floor Pressure Mat connection cable, as it is damaged (Attach Photos)
47 and 48. Hospital 2 - Room 235
Check ODL - illuminates Red for Staff Assist and/or Resident Call Alarm - should be Flashing Yellow for Staff Assist and Solid Yellow for Resident Call (Attach Photos)
Check Red Bedhead Call Point, this is activating a Resident Call Alarm and should be activating an Emergency Call Alarm (Attach Photos)
49. Hospital 2 - Room 236
Install surrounding cover on the ODL (Attach Photos)
50. Hospital 2 - Room 237
Change Floor Pressure Mat connection cable, as it is damaged (Attach Photos)
Change Splitter cable, as it is damaged (Attach Photos)
51. Hospital 2 - Room 238
Tidy wireless pendant cables (Attach Photos)
Mount receiver onto the wall (Attach Photos)
52. Hospital 2 - Room 242
Check wired pendant lead, as it failed (Attach Photos)
53. Hospital 3 - Room 434
Install surrounding cover on the Ensuite Toilet Call Point (Attach Photos)
54. Hospital 3 - Room 435
Tidy wireless pendant cables (Attach Photos)
Mount receiver onto the wall (Attach Photos)
55. Hospital 3 - Room 442
Tidy wireless pendant cables (Attach Photos)
Mount receiver onto the wall (Attach Photos)
56. Hospital 3 - Room 447
Tidy wireless pendant cables (Attach Photos)
Mount receiver onto the wall (Attach Photos)
57. Hospital 3 - Room 451
Install surrounding cover on the Bedhead Call Point (Attach Photos)
58. Hospital 3 - Room 452
Tidy wireless pendant cables (Attach Photos)
Mount receiver onto the wall (Attach Photos)
59 and 60. Hospital 3 - Room 454
Check Staff Assist alarm, text description is wrong on the displays - shows "H3 Rm455" (Attach Photos)
Tidy wireless pendant cables (Attach Photos)
Mount receiver onto the wall (Attach Photos)
61. Hospital 3 - Room 457
Replace insert in the Ensuite Toilet Call Point, requires Green Insert (Attach Photos)
62. Hospital 3 - Room 458
Install surrounding cover on the Ensuite Toilet Call Point (Attach Photos)
63 and 64. Hospital 3 - Room 459
Install surrounding cover on the Bedhead Call Point (Attach Photos)
Tidy wireless pendant cables (Attach Photos)
Mount receiver onto the wall (Attach Photos)
65. Hospital 3 - Toilet
Install surrounding cover on the Toilet Call Point (Attach Photos)
Village Centre
66. Village Centre - SA Main WC Women
Check Call Point - Failed to generate any alarm, should be an Emergency Call Alarm (Attach Photos)
67. Village Centre - Sales Office
Displays as "Doctors Office", this needs to be updated (Attach Photos)
Install surrounding cover on the ODL (Attach Photos)
68. Village Centre - Gym
Connect Gym Call Point to the ODL at the Gym Entrance - inside the same area, so should work (Attach Photos)
69. Village Centre - Gym F WC
Check ODL, as it failed (Attach Photos)
Install ODL above Female Toilet Door (Attach Photos)
Change Call Point insert from green to red (Attach Photos)
70. Village Centre - Pool
Check Call Point - requires hard pressing to activate (Attach Photos)
71. Village Centre - Lounge, by Bar area
Check Call Point by the Bar, as it failed (Attach Photos)
Townhouses
72. Townhouse - 2
Change Guest Toilet Call Point Faceplate from Green to Red (Attach Photos)
73. Townhouse - 3
Change Ensuite Toilet Call Point insert from Green to Red (Attach Photos)
74. Townhouse - 4
Change Ensuite Toilet Call Point insert from Green to Red (Attach Photos)
75. Townhouse - 6
Change Master Bedroom Call Point insert, should be Red (Attach Photos)
76. Townhouse - 7
Change Guest Bedroom Call Point Faceplate to a Red Emergency Call Faceplate (Attach Photos)
Change Ensuite Toilet Call Point Faceplate to a Red Emergency Call Faceplate (Attach Photos)
Change Guest Toilet Call Point Faceplate to a Red Emergency Call Faceplate (Attach Photos)
77. Townhouse - 9
Check Master Bedroom Call Point - requires hard pressing to activate (Attach Photos)
Check Shower Pull Cord reassurance LED, as it failed (Attach Photos)
Change Ensuite Toilet Call Point insert from Green to Red (Attach Photos)
Change Guest Toilet Call Point insert from Green to Red (Attach Photos)
78. Townhouse - 10
Check Guest Toilet Call Point - requires hard pressing to activate (Attach Photos)
Change Ensuite Toilet Call Point insert from Green to Red (Attach Photos)
Change Guest Toilet Call Point insert from Green to Red (Attach Photos)
79. Townhouse - 11
Change Master Bedroom Bedhead Call Point insert from Green to Red (Attach Photos)
Change Ensuite Toilet Call Point insert from Green to Red (Attach Photos)
Change Guest Toilet Call Point insert from Green to Red (Attach Photos)
80. Townhouse - 12A
Change Guest Toilet Call Point insert from Green to Red (Attach Photos)
80. Townhouse - 15
Change Master Bedroom Bedhead Call Point insert from Green to Red (Attach Photos)
Change Ensuite Toilet Call Point insert from Green to Red (Attach Photos)
Change Guest Toilet Call Point insert from Green to Red (Attach Photos)
81. Townhouse - 16
Change Guest Toilet Call Point insert from Green to Red (Attach Photos)
82. Townhouse - 27
Replace Call Point in Ensuite Toilet - requires hard press to activate (Attach Photos)
83. Townhouse - 33
Check Smoke Detector (HM) in the Hallway, as it failed the Smoke Test (Attach Photos)
Check Master Bedroom Bedhead Call Point - requires hard pressing to activate (Attach Photos)
84. Townhouse - 35
Replace battery on Short Range Wireless Pendant - still working, but activation LED on pendant is dim (Attach Photos)
85. Townhouse - 36
Check Reassurance Light in Master Bedroom Bedhead Call Point, failed when alarm is active (Attach Photos)
86. Townhouse - 37
Change Ensuite Toilet Call Point insert from Green to Red (Attach Photos)
87. Townhouse - 39
Change Ensuite Toilet Call Point insert from Green to Red (Attach Photos)
88. Townhouse - 43
Check Ensuite Shower Pull Cord, it fails intermittently (Attach Photos)
89. Townhouse - 56
Check Ensuite Shower Pull Cord, as it failed (Attach Photos)
90. Townhouse - 61
Check Ensuite Shower Pull Cord reassurance LED, as it's not working when the alarm is active (Attach Photos)
91. Townhouse - 63
Check Lounge Smoke Detector (System Sensor), as it failed to activate the alarm on Nurse Call Displays and Pagers (Attach Photos)
92. Townhouse - 66
Change Master Bedroom Bedhead Call Point insert from Green to Red (Attach Photos)
93. Townhouse - 67
Check Ensuite Shower Pull Cord, as it failed (Attach Photos)
94. Townhouse - 71
Check Ensuite Shower Pull Cord reassurance LED, as it's not working when the alarm is active (Attach Photos)
95. Townhouse - 79
Check both Smoke Detectors (System Sensor), as they both failed to activate the alarm on Nurse Call Displays and Pagers (Attach Photos)
96. Townhouse - 80
Check both Smoke Detectors (System Sensor), as they both failed to activate the alarm on Nurse Call Displays and Pagers (Attach Photos)
97. Townhouse - 83
Check both Smoke Detectors (VST), as they both failed to activate the alarm on Nurse Call Displays and Pagers (Attach Photos)
98. Townhouse - 84
Check both Smoke Detectors (VST), as they both failed to activate the alarm on Nurse Call Displays and Pagers (Attach Photos)
99. Townhouse - 85
Check both Smoke Detectors (HM), as they both failed to activate the alarm on Nurse Call Displays and Pagers (Attach Photos)
100. Townhouse - 87
Check both Smoke Detectors (VST in Hallway and HM in the Lounge), as they both failed to activate the alarm on Nurse Call Displays and Pagers (Attach Photos)
Check Pendant removal alarm, as it failed (Attach Photos)
101. Townhouse - 90
Check both Smoke Detectors (System Sensors in the Hallway and Lounge), as they both failed to activate the alarm on Nurse Call Displays and Pagers (Attach Photos)
Independent Apartments - Mallory
102. Independent Apartment - Mallory - 121
Replace Shower Pull Cord, as it requires to be manually pushed back up to rest position to cancel the call (Attach Photos)
103. Independent Apartments - Mallory - 122
Check Shower Pull Cord, as it is failing intermittently (Attach Photos)
104. Independent Apartments - Mallory - 126
Tidy wireless pendant cables (Attach Photos)
Mount receiver onto the wall (Attach Photos)
Change Ensuite Toilet Call Point insert from Green to Red (Attach Photos)
Change Guest Toilet Call Point insert from Green to Red (Attach Photos)
105. Independent Apartments - Mallory - 128
Check Ensuite Shower Pull Cord reassurance LED, as it's not working when the alarm is active (Attach Photos)
106. Independent Apartments - Mallory - 130
Check Ensuite Shower Pull Cord, as it is failing intermittently (Attach Photos)
107. Independent Apartments - Mallory - 221
Change Lounge Call Point insert from Green to Red (Attach Photos)
Change Ensuite Toilet Call Point insert from Green to Red (Attach Photos)
Change Guest Toilet Call Point insert from Green to Red (Attach Photos)
108. Independent Apartments - Mallory - 226
Change Guest Bedroom Call Point insert from Green to Red (Attach Photos)
Change Guest WC Call Point insert from Green to Red (Attach Photos)
109. Independent Apartments - Mallory - 230
Check Ensuite Shower Pull Cord reassurance LED, as it's not working when the alarm is active (Attach Photos)
Check Master Bedroom Bedhead Pendant removal alarm, as it failed (Attach Photos)
110. Independent Apartments - Mallory - 321
Change Ensuite Toilet Call Point insert from Green to Red (Attach Photos)
Change Guest Toilet Call Point insert from Green to Red (Attach Photos)
111. Independent Apartments - Mallory - 331
Check Ensuite Shower Pull Cord reassurance LED, as it failed (Attach Photos)
112. Independent Apartments - Mallory - 332
Check Ensuite Shower Pull Cord, as it failed (Attach Photos)
113. Independent Apartments - Mallory - 334
Check Corded Pendant, as it failed (Attach Photos)
Check Master Bedroom Bedhead Pendant removal alarm, as it failed (Attach Photos)
114. Independent Apartments - Mallory - 427
Change Ensuite Toilet Call Point insert from Green to Red (Attach Photos)
Change Guest Toilet Call Point insert from Green to Red (Attach Photos)
Change Guest Bedroom Call Point insert from Green to Red (Attach Photos)
115. Independent Apartments - Mallory - 430
Check Shower Pull Cord, as it is failing intermittently (Attach Photos)
116. Independent Apartments - Mallory - 433
Replace Shower Pull Cord, as it requires to be manually pushed back up to rest position to cancel the call (Attach Photos)
117. Independent Apartments - Mallory - 434
Check Toilet Call Point, as it is not securely mounted (Attach Photos)
Independent Apartments - Scott
3 and 153. NC Equipment Cabinet - IA SCOTT - Carpark
Replace 12V Battery and label with the replacement date (Attach Photos)
Clean enclosure and remove junk from floor (Attach Photos)
118 and 121. Independent Apartments - Scott - 135
Check Shower Pull Cord, as it is failing intermittently (Attach Photos)
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
119 and 121. Independent Apartments - Scott - 235
Check Shower Pull Cord, as reassurance LED failed (Attach Photos)
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
120 and 121. Independent Apartments - Scott - 236
Check Shower Pull Cord, as reassurance LED failed (Attach Photos)
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
121. Independent Apartments - Scott - 136
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
121. Independent Apartments - Scott - 137
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
121. Independent Apartments - Scott - 138
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
121. Independent Apartments - Scott - 139
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
121. Independent Apartments - Scott - 140
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
121. Independent Apartments - Scott - 237
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
121. Independent Apartments - Scott - 238
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
121. Independent Apartments - Scott - 239
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
121. Independent Apartments - Scott - 240
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
121. Independent Apartments - Scott - 335
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
121. Independent Apartments - Scott - 336
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
121. Independent Apartments - Scott - 337
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
121. Independent Apartments - Scott - 338
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
121. Independent Apartments - Scott - 339
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
121. Independent Apartments - Scott - 340
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
121. Independent Apartments - Scott - 435
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
121. Independent Apartments - Scott - 436
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
121. Independent Apartments - Scott - 437
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
121. Independent Apartments - Scott - 438
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
121. Independent Apartments - Scott - 439
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
121. Independent Apartments - Scott - 440
Change ALL Call Points in the Apartment to have Red inserts (Attach Photos)
Independent Apartments - Shackleton
122. Independent Apartments - Shackleton - 146
Check Guest Bedroom Bedhead Pendant removal alarm, as it failed (Attach Photos)
123. Independent Apartments - Shackleton - 242
Replace Shower Pull Cord, as it requires to be manually pushed back up to rest position to cancel the call (Attach Photos)
124. Independent Apartments - Shackleton - 341
Check ODL, as it failed (Attach Photos)
Independent Apartments - Tenzing
125. Independent Apartments - Tenzing - 150
Check Shower Pull Cord reassurance LED, as it failed (Attach Photos)
126. Independent Apartments - Tenzing - 159
Check Shower Pull Cord reassurance LED, as it failed (Attach Photos)
127. Independent Apartments - Tenzing - 160
Check Master Bedroom Bedhead Pendant removal alarm, as it failed (Attach Photos)
Change Toilet Call Point insert from Green to Red (Attach Photos)
128. Independent Apartments - Tenzing - 250
Check Long Range Wireless Pendant alarm, as it does not display on the Pagers (Attach Photos)
129. Independent Apartments - Tenzing - 347
Check ODL, as it is failing intermittently (Attach Photos)
130. Independent Apartments - Tenzing - 359
Change Ensuite Toilet Call Point insert from Green to Red (Attach Photos)
Change Guest Toilet Call Point insert from Green to Red (Attach Photos)
131. Independent Apartments - Tenzing - 450
Check Shower Pull Cord, as it failed (Attach Photos)
132. Independent Apartments - Tenzing - 452
Check Long Range Wireless Pendant alarm, as it does not display on the Pagers (Attach Photos)
133. Independent Apartments - Tenzing - 453
Check Master Bedroom Bedhead Call Point, as the pendent removal alarm failed (Attach Photos)
134. Independent Apartments - Tenzing - 455
Tidy wireless pendant cables (Attach Photos)
Mount receiver onto the wall (Attach Photos)
Independent Apartments - Cook
135. Independent Apartments - Cook - G77
Check ODL, as it failed (Attach Photos)
136. Independent Apartments - Cook - Activities Female WC
Check both entrances ODL's, as one failed (Attach Photos)
137. Independent Apartments - Cook - 175
Remove the Miracle RF Wireless Pendant Receiver that is installed, as the resident does not have a wireless pendant (Attach Photos)
138. Independent Apartments - Cook - 176
Replace Call Socket on the Master Bedroom Bedhead Call Point, as It is broken (Attach Photos)
139. Independent Apartments - Cook - 178
Check Long Range Wireless Pendant alarm, as it does not display on the Pagers (Attach Photos)
140. Independent Apartments - Cook - 271
Check Long Range Wireless Pendant alarm, as it does not display on the Pagers (Attach Photos)
141. Independent Apartments - Cook - 279
Provide longer corded pendant, as resident advises current 1.5m pendant only just reaches across (Attach Photos)
142. Independent Apartments - Cook - 372
Check Long Range Wireless Pendant alarm, as it does not display on the Pagers (Attach Photos)
143. Independent Apartments - Cook - 374
Check ODL, as it failed (Attach Photos)
Independent Apartments - Everest
144. Independent Apartments - Everest - 163
Check Master Bedroom Bedhead Pendant removal alarm, as it failed (Attach Photos)
145. Independent Apartments - Everest - 170
Check ODL, as it failed (Attach Photos)
146. Independent Apartments - Everest - 263
Check Master Bedroom Bedhead Pendant removal alarm, as it failed (Attach Photos)
Check Guest Showers Pull Cord Call Point, as it is not securely mounted (Attach Photos)
147. Independent Apartments - Everest - 266
Check ODL - brightness is very low and hardly visible (Attach Photos)
Independent Apartments - Ross
148. Independent Apartments - Ross - 191
Check ODL, as it failed (Attach Photos)
149. Independent Apartments - Ross - 285
Check Toilet Call Point, as the cancel button is not working (Attach Photos)
150. Independent Apartments - Ross - 388
Check Long Range Wireless Pendant alarm, as it does not display on the Pagers (Attach Photos)
Independent Apartments - Nepal
151. Independent Apartments - Nepal - 301
Check Shower Pull Cord reassurance LED, as it is not working (Attach Photos)
152. Independent Apartments - Nepal - 302
Check ODL, as it failed (Attach Photos)
Change Master Bedroom Bedhead Call Point Faceplate from Green to Red (Attach Photos)
Change Toilet Call Point Faceplate from Green to Red (Attach Photos)