## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | BESS & PCS footing Touch Up paint FIC - | [5 empty] | BESS & PCS footing Touch Up paint FIC
section | 2. SPECIFICATION
checkpoint-no-status | Coat: 1
label | Product: Surface preparation – Bristle blast the damaged areas to achieve a profile of 50-75um and feather the surrounding sound galv up to 50mm
label | Colour: n/a
label | DFT (μm , Min-Max): n/a
checkpoint-no-status | Coat: 2
label | Product: Apply the Interzinc 52 @ 75um
label | Colour: Grey
label | DFT (μm , Min-Max): 75 (total)
checkpoint-no-status | Coat: 3
label | Product: Apply the Interplus 1180 @ 200um (if applying by brush or roller this can be done in multiple coats)
label | Colour: Grey
label | DFT (μm , Min-Max): 200 (100 for each coat)
section | 3. SURFACE PREPARATION
checkpoint | Does visual standard of surface preparation comply with specified requirements?
section | 4. COATING APPLICATION
checkpoint | COATING APPLICATION
number | Coat No.:
date | Application Date:
textbox | Batch No.:
textbox | % RH
textbox | Ambient Temp (ºC)
label | Steel Temp (ºC): >10, Comply to ASTM D3276
textbox | Dew Point (ºC)
textbox | Wet Film Thickness (μm)
section | 5. FIC - SPECIFIC CHECK ITEMS
checkpoint | Ambient conditions (steel temp, air temp, % RH, dew point) complies?
checkpoint | Application method complies to manufacturer’s recommendations?
checkpoint | Recoat intervals complies to manufacturer’s recommendations?
checkpoint | Colour complies to specifications?
checkpoint | Dry film thickness/Wet film thickness complies to specifications?
checkpoint | Final appearance (runs, overspray, uniformity, etc.) acceptable?
section | Document Sign-off
checkpoint | Close-out
textbox | SEPD - Name:
textbox | SEPD - Position:
date | SEPD - Date:
signoff | Add Signature