## Project Breakdown
QA Folder Structure
Site QA
CONNECTIONS |  | Service Connections
|  |  | Water connection | Water Connection
|  |  | Sewer Connection | Sewer Connection
|  |  | Stormwater connection | Stormwater Connection
|  |  | Gas connection | Gas Connection
SOUTH BLDG
| GROUND | Inground services | Pour 6 | In-Ground Drainage Hydraulic Services ITP V.210121
|  |  | Pour 6 | Concrete Pour Checklist (Apartment and hotel floors)
Aerial Drainage
Pressure Services Installation ITP V.210121
Pressure services on apartments/ Hotel or commercial floors.
|  |  | Unit G.01 | Apartment / Hotel
|  |  | Unit G.02 | Apartment / Hotel
|  |  | Unit G.03 | Apartment / Hotel
|  |  | Unit G.04 | Apartment / Hotel
|  |  | Unit G.05 | Apartment / Hotel
|  |  | Unit G.06 | Apartment / Hotel
HOT WATER PLANT and RETURN PUMPS
Garbage Room Work
|  | Inground services | Pour 5 | In-Ground Drainage Hydraulic Services ITP V.210121
| LEVEL 01 | UNITS | Pour 10 | Concrete Pour Checklist (Apartment and hotel floors)
Aerial Drainage
Pressure Services Installation ITP V.210121
Pressure services on apartments/ Hotel or commercial floors.
|  |  | Unit 1.07 | Apartment / Hotel
|  |  | Unit 1.08 | Apartment / Hotel
|  |  | Unit 1.09 | Apartment / Hotel
|  |  | Unit 1.10 | Apartment / Hotel
|  |  | Unit 1.11 | Apartment / Hotel
|  |  | Unit 1.12 | Apartment / Hotel
|  | CARPARK | Pour 11 | In-Ground Drainage Hydraulic Services ITP V.210121
Pressure Services Installation ITP V.210121
Aerial Drainage
Carpark finalisation
| LEVEL 02 | UNITS | Pour 10 | Concrete Pour Checklist (Apartment and hotel floors)
Aerial Drainage
Pressure Services Installation ITP V.210121
Pressure services on apartments/ Hotel or commercial floors.
|  |  | Unit 2.13 | Apartment / Hotel
|  |  | Unit 2.14 | Apartment / Hotel
|  |  | Unit 2.15 | Apartment / Hotel
|  |  | Unit 2.16 | Apartment / Hotel
|  |  | Unit 2.17 | Apartment / Hotel
|  |  | Unit 2.18 | Apartment / Hotel
|  | CARPARK | Pour 11 | Setout and Penetration installation (Retail, Commercial and carpark areas)
Pressure Services Installation ITP V.210121
Cold Water Pressure Pump
Garbage Room Work
Sewer Pump Station
Aerial Drainage
Carpark finalisation
| LEVEL 03 | UNITS | Pour 10 | Concrete Pour Checklist (Apartment and hotel floors)
Aerial Drainage
Pressure Services Installation ITP V.210121
Pressure services on apartments/ Hotel or commercial floors.
|  |  | Unit 3.19 | Apartment / Hotel
|  |  | Unit 3.20 | Apartment / Hotel
|  |  | Unit 3.21 | Apartment / Hotel
|  |  | Unit 3.22 | Apartment / Hotel
|  |  | Unit 3.23 | Apartment / Hotel
|  |  | Unit 3.24 | Apartment / Hotel
|  | CARPARK | Pour 11 | Setout and Penetration installation (Retail, Commercial and carpark areas)
Pressure Services Installation ITP V.210121
Cold Water Pressure Pump
Aerial Drainage
Carpark finalisation
| LEVEL 04 | UNITS | Pour 10 | Concrete Pour Checklist (Apartment and hotel floors)
Aerial Drainage
Pressure Services Installation ITP V.210121
Pressure services on apartments/ Hotel or commercial floors.
|  |  | Unit 4.25 | Apartment / Hotel
|  |  | Unit 4.26 | Apartment / Hotel
|  |  | Unit 4.27 | Apartment / Hotel
|  |  | Unit 4.28 | Apartment / Hotel
|  |  | Unit 4.29 | Apartment / Hotel
| ROOF |  |  | Roof work
CLUB BLDG
| GROUND |  | Pour 4 | Setout and Penetration installation (Retail, Commercial and carpark areas)
In-Ground Drainage Hydraulic Services ITP V.210121
Aerial Drainage
Pressure Services Installation ITP V.210121
Commercial / Club Tenancy
| LEVEL 01 |  | Pour 7 | Setout and Penetration installation (Retail, Commercial and carpark areas)
|  |  | Pour 8 | Setout and Penetration installation (Retail, Commercial and carpark areas)
|  |  | Pour 9 | Setout and Penetration installation (Retail, Commercial and carpark areas)
Aerial Drainage
Pressure Services Installation ITP V.210121
Commercial / Club Tenancy
HOT WATER PLANT and RETURN PUMPS
| LEVEL 02 |  | Pour 7 | Setout and Penetration installation (Retail, Commercial and carpark areas)
|  |  | Pour 8 | Setout and Penetration installation (Retail, Commercial and carpark areas)
|  |  | Pour 9 | Setout and Penetration installation (Retail, Commercial and carpark areas)
Aerial Drainage
Pressure Services Installation ITP V.210121
Commercial / Club Tenancy
| LEVEL 03 |  | Pour 7 | Setout and Penetration installation (Retail, Commercial and carpark areas)
|  |  | Pour 8 | Setout and Penetration installation (Retail, Commercial and carpark areas)
|  |  | Pour 9 | Setout and Penetration installation (Retail, Commercial and carpark areas)
Aerial Drainage
Pressure Services Installation ITP V.210121
Commercial / Club Tenancy
| ROOF |  |  | Roof work
NORTH BLDG
| LOWER GROUND | Inground services | Pour 1 | In-Ground Drainage Hydraulic Services ITP V.210121
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
Aerial Drainage
Pressure Services Installation ITP V.210121
Pressure services on apartments/ Hotel or commercial floors.
|  |  | Unit F.30 | Apartment / Hotel
|  |  | Unit F.31 | Apartment / Hotel
|  |  | Unit F.32 | Apartment / Hotel
|  |  | Unit F.33 | Apartment / Hotel
|  |  | Unit F.34 | Apartment / Hotel
Garbage Room Work
Sewer Tank
| GROUND |  | Pour 1 | In-Ground Drainage Hydraulic Services ITP V.210121
|  |  | Pour 2 | In-Ground Drainage Hydraulic Services ITP V.210121
|  |  | Pour 3 | In-Ground Drainage Hydraulic Services ITP V.210121
|  |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
Aerial Drainage
Pressure Services Installation ITP V.210121
Pressure services on apartments/ Hotel or commercial floors.
|  |  | Unit G.35 | Apartment / Hotel
|  |  | Unit G.36 | Apartment / Hotel
|  |  | Unit G.37 | Apartment / Hotel
|  |  | Unit G.38 | Apartment / Hotel
|  |  | Unit G.39 | Apartment / Hotel
|  |  | Unit G.40 | Apartment / Hotel
|  |  | Unit G.41 | Apartment / Hotel
|  |  | Unit G.42 | Apartment / Hotel
|  |  | Unit G.43 | Apartment / Hotel
|  |  | Unit G.44 | Apartment / Hotel
|  |  | Unit G.45 | Apartment / Hotel
|  |  | Unit G.46 | Apartment / Hotel
|  |  | Unit G.47 | Apartment / Hotel
|  |  | Unit G.48 | Apartment / Hotel
|  |  | Unit G.49 | Apartment / Hotel
|  |  | Unit G.50 | Apartment / Hotel
Garbage Room Work
HOT WATER PLANT and RETURN PUMPS
Sewer Tank
| LEVEL 01 |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
Aerial Drainage
Pressure Services Installation ITP V.210121
Pressure services on apartments/ Hotel or commercial floors.
|  |  | Unit 1.51 | Apartment / Hotel
|  |  | Unit 1.52 | Apartment / Hotel
|  |  | Unit 1.53 | Apartment / Hotel
|  |  | Unit 1.54 | Apartment / Hotel
|  |  | Unit 1.55 | Apartment / Hotel
|  |  | Unit 1.56 | Apartment / Hotel
|  |  | Unit 1.57 | Apartment / Hotel
|  |  | Unit 1.58 | Apartment / Hotel
|  |  | Unit 1.59 | Apartment / Hotel
|  |  | Unit 1.60 | Apartment / Hotel
|  |  | Unit 1.61 | Apartment / Hotel
|  |  | Unit 1.62 | Apartment / Hotel
|  |  | Unit 1.63 | Apartment / Hotel
|  |  | Unit 1.64 | Apartment / Hotel
|  |  | Unit 1.65 | Apartment / Hotel
|  |  | Unit 1.66 | Apartment / Hotel
Garbage Room Work
| LEVEL 01 | CARPARK | Pour 4 | In-Ground Drainage Hydraulic Services ITP V.210121
|  |  | Pour 5 | In-Ground Drainage Hydraulic Services ITP V.210121
|  |  | Pour 6 | In-Ground Drainage Hydraulic Services ITP V.210121
Aerial Drainage
Carpark finalisation
| LEVEL 02 |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
Aerial Drainage
Pressure Services Installation ITP V.210121
Pressure services on apartments/ Hotel or commercial floors.
|  |  | Unit 2.67 | Apartment / Hotel
|  |  | Unit 2.68 | Apartment / Hotel
|  |  | Unit 2.69 | Apartment / Hotel
|  |  | Unit 2.70 | Apartment / Hotel
|  |  | Unit 2.71 | Apartment / Hotel
|  |  | Unit 2.72 | Apartment / Hotel
|  |  | Unit 2.73 | Apartment / Hotel
|  |  | Unit 2.74 | Apartment / Hotel
|  |  | Unit 2.75 | Apartment / Hotel
|  |  | Unit 2.76 | Apartment / Hotel
|  |  | Unit 2.77 | Apartment / Hotel
|  |  | Unit 2.78 | Apartment / Hotel
|  |  | Unit 2.79 | Apartment / Hotel
|  |  | Unit 2.80 | Apartment / Hotel
|  |  | Unit 2.81 | Apartment / Hotel
|  |  | Unit 2.82 | Apartment / Hotel
Garbage Room Work
| LEVEL 02 | CARPARK | Pour 4 | Setout and Penetration installation (Retail, Commercial and carpark areas)
|  |  | Pour 5 | Setout and Penetration installation (Retail, Commercial and carpark areas)
|  |  | Pour 6 | Setout and Penetration installation (Retail, Commercial and carpark areas)
Aerial Drainage
Pressure Services Installation ITP V.210121
Carpark finalisation
| LEVEL 03 |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 3 | Concrete Pour Checklist (Apartment and hotel floors)
Aerial Drainage
Pressure Services Installation ITP V.210121
Pressure services on apartments/ Hotel or commercial floors.
|  |  | Unit 3.83 | Apartment / Hotel
|  |  | Unit 3.84 | Apartment / Hotel
|  |  | Unit 3.85 | Apartment / Hotel
|  |  | Unit 3.86 | Apartment / Hotel
|  |  | Unit 3.87 | Apartment / Hotel
|  |  | Unit 3.88 | Apartment / Hotel
|  |  | Unit 3.89 | Apartment / Hotel
|  |  | Unit 3.90 | Apartment / Hotel
|  |  | Unit 3.91 | Apartment / Hotel
|  |  | Unit 3.92 | Apartment / Hotel
|  |  | Unit 3.93 | Apartment / Hotel
|  |  | Unit 3.94 | Apartment / Hotel
|  |  | Unit 3.95 | Apartment / Hotel
|  |  | Unit 3.96 | Apartment / Hotel
|  |  | Unit 3.97 | Apartment / Hotel
Garbage Room Work
|  | CARPARK | Pour 4 | Setout and Penetration installation (Retail, Commercial and carpark areas)
|  |  | Pour 5 | Setout and Penetration installation (Retail, Commercial and carpark areas)
|  |  | Pour 6 | Setout and Penetration installation (Retail, Commercial and carpark areas)
Aerial Drainage
Pressure Services Installation ITP V.210121
Carpark finalisation
| LEVEL 04 |  | Pour 1 | Concrete Pour Checklist (Apartment and hotel floors)
|  |  | Pour 2 | Concrete Pour Checklist (Apartment and hotel floors)
Aerial Drainage
Pressure Services Installation ITP V.210121
Pressure services on apartments/ Hotel or commercial floors.
|  |  | Unit 4.98 | Apartment / Hotel
|  |  | Unit 4.99 | Apartment / Hotel
|  |  | Unit 4.100 | Apartment / Hotel
|  |  | Unit 4.101 | Apartment / Hotel
|  |  | Unit 4.102 | Apartment / Hotel
|  |  | Unit 4.103 | Apartment / Hotel
|  |  | Unit 4.104 | Apartment / Hotel
|  |  | Unit 4.105 | Apartment / Hotel
|  |  | Unit 4.106 | Apartment / Hotel
Garbage Room Work
| ROOF |  |  | Roof work
Project Finalisation |  |  |  | Project finalisation

## Resources
type | name | values
checklist | In-Ground Drainage Hydraulic Services ITP V.210121
section | Sewer/ Tradewaste
checkpoint | Sewer drainage, Tradewaste drainage and vents installed as per workshop drawings. | pass, fail, n/a
button | Minimum Grades, Bracketing and IO's installed as per AS3500. | yes, No
button | Pipework risers labelled, pink primer and blue glue used only. | yes, No
Checkpoint | Check all electrofusion welds (HDPE) or glued joints (UPVC) for any faults. | pass, fail, n/a
checkpoint | All pipe risers to be protected with pipe caps & or duck tape. | pass, fail, n/a
checkpoint | Inspection by Fair Trading for sewer drainage to be done & other inspections if required by others. | pass, fail, n/a
label | Photograph inspection booking.
checkpoint | Backfill trenches with materials as per Australian standards & project requirements. | pass, fail, n/a
label | Ensure compaction of fill materials is to specifications & Australian Standards.
button | Compaction testing of trenches once backfilled to the Australian Standard requirements. | yes, No
checkpoint | All works completed to specification/drawings & Area left clean/tidy & excess material stored away. | pass, fail, n/a
section | Stormwater
checkpoint | Stormwater drainage installed as per workshop drawings. | pass, fail, n/a
button | Minimum Grades, Bracketing and IO's installed as per AS3500. | yes, No
checkpoint | Installation of pits to the correct levels. | pass, fail, n/a
button | Ensure correct grates & lids used with appropriate load ratings for locations to traffic movements. | yes, No
button | Pits to be sparged - Made water tight to inlet & outlet pipework. | yes, No
checkpoint | All pipe risers to be protected with pipe caps & or duck tape. | pass, fail, n/a
checkpoint | HOLD POINT - Inspections if required by relevant authorised persons . | pass, fail, n/a
label | Attach inspection reports below.
checkpoint | Backfill trenches with materials as per Australian standards & project requirements. | pass, fail, n/a
label | Ensure compaction of fill materials is to specifications & Australian Standards.
button | Compaction testing of trenches once backfilled to the Australian Standard requirements. | yes, No
checkpoint | All Stormwater Work completed to specification/drawings & Area left clean/tidy & excess material stored away. | pass, fail, n/a
section | Handover
checkpoint | Update As Built drawing immediately - Confirm IL of pipework. Attach with ITP submission. | pass, fail, n/a
checkpoint | CCTV completed pipework to ensure no defects before concrete pour to prevent future problems. | pass, fail, n/a
checkpoint | Pictures of works completed - Attached below. | pass, fail, n/a
text | Concrete pour date.
checklist | Inground Pressure Services Installation.
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans. | pass, fail, n/a
label | Check working pressures & ensure material can cater for those pressures.
checkpoint | Calibration of crimp tools, welding equipment & deburring machine ready for use.. | pass, fail, n/a
checkpoint | CW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and scematics. | pass, fail, n/a
label | Ensure to keep seperation between NPCW & other services as per Australian Standards.
button | Witness marks on all press fittings checked. | yes, no
checkpoint | HOLD POINT - Fair Trading inspections for installations of recycled water service if any. | pass, fail, n/a
label | Photograph inspection booking.
checkpoint | Fire services installed correctly as per workshop drawings. | pass, fail, n/a
checkpoint | Water servces tested @ 1500KPA or 1.5 x Working pressure. Whichever is higher for a minimum duration of 60 minutes. | pass, fail, n/a
checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes. | pass, fail, n/a
checkpoint | Backfill trenches with materials as per Australian standards & project requirements. | pass, fail, n/a
label | Ensure trace taoe is installed
label | Ensure compaction of fill materials is to specifications & Australian Standards.
button | Compaction testing of trenches once backfilled to the Australian Standard requirements. | pass, fail, n/a
label | All services left under pressure during construction.
checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy. (attach photos if necessary) | pass, fail, n/a
checklist | Setout and Penetration installation (Retail, Commercial and carpark areas)
checkpoint | Latest DWG file sent to surveyor. With correct floor levels understood & attained. | pass, fail, n/a
checkpoint | Wall Penetrations for pressure and drainage services complete? Installed at correct Invert levels? | pass, fail, n/a
checkpoint | Downpipes with columns installed and capped off with DWV caps ONLY. | pass, fail, n/a
checkpoint | Sewer, stormwater and pressure penetration points installed. Check off Hydraulic plans. | pass, fail, n/a
checkpoint | Cast in services installed at correct grades (as per AS3500) and locations. Check off Hydraulic plans. | pass, fail, n/a
checkpoint | HOLD POINT - Fair Trading inspections for installations of major sewer services cast in. | pass, fail, n/a
label | Photograph inspection booking.
checkpoint | Correct fire collars installed with test reports on file. | pass, fail, n/a
label | Hour rating to meet slab FRL.
checkpoint | Puddle flanges installed for floor wastes and balconies at minimum concrete height stated on structural drawings. | pass, fail, n/a
checkpoint | Car park drains,RWO's , trench drains and risers installed. Trafficable grates to be class D only. | pass, fail, n/a
label | Correct grade of drain to be installed.
checkpoint | Miscellaneous penetrations installed. | pass, fail, n/a
checkpoint | All pipe risers to be protected with pipe caps and or duck tape. | pass, fail, n/a
checkpoint | Top up water on the morning prior concrete pour for major casting. | pass, fail, n/a
checkpoint | Pictures of works completed. | pass, fail, n/a
text | Concrete pour date:
label | All Penetration Work completed to specification/drawings & Area left clean/tidy.
type | name | values
checklist | Concrete Pour Checklist (Apartment and hotel floors)
checkpoint | Latest DWG file sent to surveyor. With correct floor levels understood & attained. | pass, fail, n/a
checkpoint | Wall Penetrations for pressure & drainage services complete & Installed at correct Invert levels. | pass, fail, n/a
checkpoint | Downpipes with columns installed & capped off. | pass, fail, n/a
checkpoint | Correct fire collars installed with test reports on file. | pass, fail, n/a
label | Integrity and insulation hour rating to meet slab FRL.
checkpoint | All hydraulic service penetrations points installed. | pass, fail, n/a
label | Cast in services installed at correct grades (as per AS3500) & locations.
checkpoint | HOLD POINT - Fair Trading inspections for installations of major sewer services cast in. | pass, fail, n/a
label | Photograph inspection booking.
checkpoint | Balcony, Bathroom, Kitchen & Laundry Layouts Checked. | pass, fail, n/a | label | Check off Hydraulic plans
checkpoint | Puddle flanges installed for floor wastes and balcony drains at minimum concrete height stated on structural drawings. | pass, fail, n/a
label | Car Park Drains Checked.
label | Correct grates, Planter box drains or RWO installed.
checkpoint | All pipe risers to be protected with pipe caps & or duck tape. | pass, fail, n/a
checkpoint | Top up water on the morning prior concrete pour for major casting. | pass, fail, n/a
checkpoint | Cold water, Hot water and gas service conduits installed from lobby to apartment/hotel. | pass, fail, n/a
button | Cold water, Hot water and gas service conduits loops to balconies and kitchen islands installed. | yes, no
checkpoint | Pictures of works completed. | pass, fail, n/a
text | Concrete pour date:
label | All Penetration Work completed to specification/drawings & Area left clean/tidy. (attach photos if necessary)
checklist | Aerial Drainage
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans. | pass, fail, n/a
label | Check scope of works/specification & ensure all documents are current.
checkpoint | Fire collars cleared of concrete slurry & replaced if damaged. | pass, fail, n/a
checkpoint | Sewer, Stormwater, tradewaste and vent services installed correctly as per workshop drawings and schematics. | pass, fail, n/a
button | Minimum Grades, Bracketing and IO's installed as per AS3500. | yes, no
button | Check for cross connections. | yes, no
label | Pink primer and Blue glue used only on UPVC.
checkpoint | Syphonics installed as per manufacturers recommendation | pass, fail, n/a
button | Check all electrofusion welds (HDPE) or glued joints (UPVC) for any faults. | yes, no
checkpoint | Hydrostatic test filled with water to a height not less than 1m above soffit level of highest pipe for a minimum of 30min. | pass, fail, n/a
checkpoint | PAPA Valve installed in correct position and within maximum distance from stack | pass, fail, n/a
checkpoint | Retro fit fire collars installed. | pass, fail, n/a
button | Fire penetration stickers installed and photographed. High top collars to be smoke sealed. | yes, no
checkpoint | Pipes labelled as per AS3500. | pass, fail, n/a
checkpoint | Acoustic lagging as per project requirements. | pass, fail, n/a
checkpoint | All points capped off to ensure no builders debri enters system. | pass, fail, n/a
button | Floor waste protected with sponge. | yes, no
checkpoint | Update As Built drawing immediately. Confirm IL of pipework. | pass, fail, n/a
checkpoint | All Drainage works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary) | pass, fail, n/a
checklist | Pressure Services Installation
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans. | pass, fail, n/a
label | Check scope of works/specification & ensure all documents are current.
label | Check working pressures & ensure material can cater for those pressures.
checkpoint | Calibration of crimp tools & deburring machine onsite complete. | pass, fail, n/a
checkpoint | CW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and scematics. | pass, fail, n/a
label | Ensure to keep seperation between NPCW & other services as per Australian Standards.
button | Witness marks on all press fittings checked. | Yes, No
checkpoint | HOLD POINT - Fair Trading inspections for installations of recycled water service if any. | pass, fail, n/a
label | Photograph inspection booking.
checkpoint | Fire services installed correctly as per workshop drawings. | pass, fail, n/a
button | Gal pipe grooves checked with a groove tape. | Yes, No
checkpoint | Bracketing installed as per AS3500 & manufacturer's specifications. | pass, fail, n/a
button | Pipe spacers installed to avoid electrofusion. | Yes, No
checkpoint | Water servces tested @ 1500KPA or 1.5 x Working pressure. Whichever is higher for a minimum duration of 60 minutes. | pass, fail, n/a
checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes. | pass, fail, n/a
label | All services left under pressure during construction.
checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc. | pass, fail, n/a
button | Smoke seal applied to all penetrations required. | Yes, No
checkpoint | Pipes labelled as per AS3500. | pass, fail, n/a
checkpoint | Thermal lagging as per project requirements & AS3500. | pass, fail, n/a
checkpoint | Fire hose reel installed as pe Australian standards and tested. | pass, fail, n/a
checkpoint | Fire hose reel tagged. | pass, fail, n/a
checkpoint | RPZD valve installed as per AS3500. | pass, fail, n/a
button | RPZD drain installed & tested. | yes, no
label | Please attach photo of serial number and valve.
checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy. (attach photos if necessary) | pass, fail, n/a
checklist | Pressure services on apartments/ Hotel or commercial floors.
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans. | pass, fail, n/a
label | Check scope of works/specification & ensure all documents are current.
label | Check working pressures & ensure material can cater for those pressures.
checkpoint | Calibration of crimp tools & deburring machine onsite complete. | pass, fail, n/a
checkpoint | CW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and scematics. | pass, fail, n/a
label | Ensure to keep seperation between NPCW & other services as per Australian Standards.
button | Witness marks on all press fittings checked. | Yes, No
checkpoint | Bracketing installed as per AS3500 & manufacturer's specifications. | pass, fail, n/a
button | Pipe spacers installed to avoid electrofusion. | Yes, No
checkpoint | Water servces tested @ 1500KPA or 1.5 x Working pressure. Whichever is higher for a minimum duration of 60 minutes. | pass, fail, n/a
checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes. | pass, fail, n/a
label | All services left under pressure during construction.
checkpoint | Isolation lever shut off valves and PRV,s installed. | pass, fail, n/a
button | Tempering valve or Thermostatic mixing valve installed in the correct orientation. | Yes, No
button | Cold water, Hot water and or meter bars installed and labelled. | Yes, No
button | Connection of all reticulated cold, hot, Gas & NPCW PEX pipes to points of connections from manifold setups. | Yes, No
checkpoint | Floor waste grate installed. | pass, fail, n/a
checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc. | pass, fail, n/a
button | Smoke seal applied to all penetrations required. | Yes, No
checkpoint | Pipes labelled as per AS3500. | pass, fail, n/a
checkpoint | Thermal lagging as per project requirements & AS3500. | pass, fail, n/a
checkpoint | Fire hose reel installed as pe Australian standards, tested and tagged. (IF APPLICABLE). | pass, fail, n/a
checkpoint | Garbage Chute RPZD installed and tested. (IF APPLICABLE). | pass, fail, n/a
checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary). | pass, fail, n/a
checklist | Apartment / Hotel
Section | Roughin
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans. | pass, fail, n/a
label | Check scope of works/specification & ensure all documents are current
checkpoint | CW,HW,WW, GAS, NPCW & or RAINWATER services installed correctly as per workshop drawings and scematics | pass, fail, n/a
checkpoint | Check for any cross connections. | pass, fail, n/a
checkpoint | Balcony gas bayonet or water taps installed as per AS5601 and AS3500. Check foothold requirements | pass, fail, n/a
checkpoint | Basin wastes and toilet waste offset and tested with water if required. | pass, fail, n/a
checkpoint | Internal cistern installed and tested. Ensure cistern is installed as far forward. | pass, fail, n/a
checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward. | pass, fail, n/a
checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications. | pass, fail, n/a
button | Seperation of services as per AS3500 | Yes, No
checkpoint | All setouts ok and run eyes over crimps | pass, fail, n/a
checkpoint | HOLD POINT - Inspections if required by relevant authorised persons . | Yes, No, N/A
label | Photograph inspection booking.
checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own. | pass, fail, n/a
checkpoint | Gas services tested @ 300KPA for a minimum of 60 minutes | pass, fail, n/a
checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc | pass, fail, n/a
button | Smoke seal applied to all penetrations required. | Yes, No
checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy | pass, fail, n/a
label | Pictures of works completed if applicable.
Section | Apartment Commissioning
checkpoint | Bathroom, Kitchen and Laundry setout off current Architectural drawings. | pass, fail, n/a
checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED, Laundry,bathroom, ensuite and balcony. | pass, fail, n/a
checkpoint | Kitchen mixer and sink installation complete. | pass, fail, n/a
button | Kitchen mixer solid, check for cross connection, run tap, clear S&P trap, tighten flexis& trap and check mini cock for leaks. | Yes, No
button | Waste connected (FILL & TEST BOWL). CHECK NO LEAKS and AAV installed if applicable. | Yes, No
checkpoint | Dishwaher installed with hoses, Power lead not kinked and dishwasher plum. (cover plate for hoses must be installed) | pass, fail, n/a
button | Run full dishwashing cyle and inspect for faults. | Yes, No
pass, fail, n/a
button | Once gas is on, purge gas safely. Confirm yes once complete. | Yes, No
text | Hot water delivery to kitchen sink.
checkpoint | Laundry tub and mixer installed? | pass, fail, n/a
label | Tub door to swing the correct way.
button | Clean aerator, Remove Trap & Clean Out (Tighten Trap) & Test Floor Waste - Clean Out | Yes, No
button | Laundry mixer solid, check for cross connection, run tap, tighten flexis& trap and check mini cock and trap for leaks. | Yes, No
button | A/C Tundish(Cap if there is no Tundish by AC). Ensure 25mm airgap achieved. | Yes, No
button | Washing Machine taps Installed Under Tub/Opp Tub, cover plates installed and AAV installed if applicable. | Yes, No
checkpoint | Toilet's, Toilet seat's, Cistern's and flush button installed and water tested. | pass, fail, n/a
button | Flush toilet's 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes, No
checkpoint | Basin mixer's and basin's installed. (photo) | pass, fail, n/a
button | Basin mixer's solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes, No
button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes, No
checkpoint | Shower mixer cover plate/handle and shower rail or rose installed. | pass, fail, n/a
button | Run Shower for 15 min, inspect for cross connections, floorwaste blockages and ensure aerators are cleared. | Yes, No
text | Hot water delivery to Shower.
checkpoint | Bath installed, Cement grouted in, fill tested and water tetsed for any pipe or plug and waste leaks. | pass, fail, n/a
checkpoint | Bath mixer cover plate/handle and bath spout installed. | pass, fail, n/a
button | Bath fill test and water run test, inspect for cross connections, floorwaste blockages and ensure aerators are cleared. | Yes, No
checkpoint | Balcony drians clear, overflows in place? | pass, fail, n/a
checkpoint | Balcony gas bayonet and or water taps installed as per AS5601 and AS3500. Test for leaks and operation. | pass, fail, n/a
checkpoint | Gas valves tagged, CW meter installed and tagged, Hw meter installed and tagged and NPCW installed if applicable. | pass, fail, n/a
checkpoint | Gas Tested with Manometer - on hold for 10 minutes. Ensure absolutely no leaks! | pass, fail, n/a
checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters) | pass, fail, n/a
checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters). | pass, fail, n/a
button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes, No
text | Pressure Reading and temperature within apartment or hotel.
checkpoint | All fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary) | pass, fail, n/a
label | General photos, comments & observations during fitout stage (Add below).
checklist | Roof work
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans. | pass, fail, n/a
label | Check scope of works/specification & ensure all documents are current.
checkpoint | Builder has overflows installed. | pass, fail, n/a
checkpoint | Sewer vents terminated as per AS3500. | pass, fail, n/a
button | CCTV of sewer completed | Yes, No
checkpoint | RWO cleared of debri and CCTV completed. | pass, fail, n/a
checkpoint | RWO grates installed and secured. | pass, fail, n/a
label | Ensure pprotection screen installed so no pebbles block drains
checkpoint | Pressure services installed. | pass, fail, n/a
checkpoint | Provisions for other services installed. (IF APPLICABLE) | pass, fail, n/a
checkpoint | UV thermal lagging installed. | pass, fail, n/a
checkpoint | All hydraulic works completed to specification/drawings & Area left clean/tidy. | pass, fail, n/a
label | Pictures of works completed if applicable.
HOT WATER PLANT and RETURN PUMPS
Section | Hot water plant
checkpoint | Installation – refer to installation check list for hot and cold water. | pass, fail, n/a
checkpoint | Testing – Pressure tested to1500kpa or 1.5 times working pressure whichever is greater. | pass, fail, n/a
checkpoint | Flue installed as per manufacturers specification. | pass, fail, n/a
button | Power flue turned on. | Yes, No
checkpoint | Temp relief points ran to tundishes. | pass, fail, n/a
checkpoint | Temperature probe from control box installed into storage tanks. | pass, fail, n/a
checkpoint | Check that an adequate water supply is available to the hot water system. | pass, fail, n/a
checkpoint | Water supply pressure shall not exceed the maximum pressure stated by manufacturer. | pass, fail, n/a
checkpoint | Open cold water inlet valve, hot water outlet valve | pass, fail, n/a
checkpoint | Exercise all valves and ensure correct operation. Ensure all valves are in open position prior turning power on. | pass, fail, n/a
checkpoint | Check the system is fully charged & all air is bled from the system & no leaks are evident | pass, fail, n/a
checkpoint | Ensure hot water heaters and storage tanks are full of water and all valves are open. | pass, fail, n/a
checkpoint | Ensure pressures are not greater then 750Kpa to the heaters or storage tanks. | pass, fail, n/a
checkpoint | Open all individual gas isolation valves & purge gas lines. | pass, fail, n/a
checkpoint | Test gas pipe work for leaks. | pass, fail, n/a
checkpoint | Check the gas supply pressure at the inlet to the water heater with the water heater and all | pass, fail, n/a
checkpoint | range is NG: 1.13Kpa - 3.5Kpa & LPG: 2.75Kpa - 3.5Kpa | pass, fail, n/a
button | Clean filters and strainers once after 4 hours of use. | Yes, No
checkpoint | Set temperature to 65 degrees. | pass, fail, n/a
Section | HOT WATER RETURN PUMPS
checkpoint | Hot water return pumps - Installation – refer to installation check list for hot and cold water. | pass, fail, n/a
checkpoint | Testing – Pressure tested to1500kpa or 1.5 times working pressure whichever is greater. | pass, fail, n/a
checkpoint | Ensure there is water supply to the pumps. | pass, fail, n/a
checkpoint | Clean filters and strainers once after 4 hours of use. | pass, fail, n/a
checkpoint | Turn on power to the pumps. Set the pumps to alternate. | pass, fail, n/a
checkpoint | Purge pumps of air. Ensure water is visible from the purging points. | pass, fail, n/a
checkpoint | Set balancing valves. | pass, fail, n/a
checkpoint | Inspect system for any leaks or faults. | pass, fail, n/a
checklist | Common Male Bathroom Rough In
Section | Roughin
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards. | pass, fail, n/a
label | Check scope of works/specification & ensure all documents are current
checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and scematics | pass, fail, n/a
checkpoint | Check for any cross connections. | pass, fail, n/a
checkpoint | Basin wastes and toilet waste offset and tested with water if required. | pass, fail, n/a
checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward. | pass, fail, n/a
checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward. | pass, fail, n/a
checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided. | pass, fail, n/a
checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications. | pass, fail, n/a
button | Seperation of services as per AS3500 | Yes, No
checkpoint | All setouts ok and run eyes over crimps | pass, fail, n/a
checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own. | pass, fail, n/a
checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc | pass, fail, n/a
button | Smoke seal applied to all penetrations required. | Yes, No
checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary) | pass, fail, n/a
Section | Fitout and Commissioning
checkpoint | Bathroom fixtures installed at correct height/ clearnce. Comply with Architectural drawings and Australian standards. | pass, fail, n/a
checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED. | pass, fail, n/a
checkpoint | Toilet's, Toilet seat's, Cistern's and flush button installed and water tested. | pass, fail, n/a
button | Flush toilet's 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes, No
checkpoint | Basin mixer's and basin's installed. | pass, fail, n/a
button | Basin mixer's solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes, No
button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes, No
checkpoint | Shower mixer cover plate/handle and shower rail or rose installed. | pass, fail, n/a
button | Run Shower for 15 min, inspect for cross connections, floorwaste blockages and ensure aerators are cleared. | Yes, No
checkpoint | Urinals installed and connected to solenoid and waste. | pass, fail, n/a
button | Flush Urinal 3 Times (check that sensor is working fine). | Yes, No
checkpoint | HW heater installed as per drawings and specification, purged and tested. | pass, fail, n/a
checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters) | pass, fail, n/a
checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters). | pass, fail, n/a
button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes, No
text | Pressure Reading and temperature within apartment or hotel.
checkpoint | All fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary) | pass, fail, n/a
label | General photos, comments & observations during fitout stage (Add below).
checklist | Common Female Bathroom Rough In
Section | Roughin
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards. | pass, fail, n/a
label | Check scope of works/specification & ensure all documents are current
checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and scematics | pass, fail, n/a
checkpoint | Check for any cross connections. | pass, fail, n/a
checkpoint | Basin wastes and toilet waste offset and tested with water if required. | pass, fail, n/a
checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward. | pass, fail, n/a
checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward. | pass, fail, n/a
checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided. | pass, fail, n/a
checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications. | pass, fail, n/a
button | Seperation of services as per AS3500 | Yes, No
checkpoint | All setouts ok and run eyes over crimps | pass, fail, n/a
checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own. | pass, fail, n/a
checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc | pass, fail, n/a
button | Smoke seal applied to all penetrations required. | Yes, No
checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary) | pass, fail, n/a
Section | Fitout and Commissioning
checkpoint | Bathroom fixtures installed at correct height/ clearnce. Comply with Architectural drawings and Australian standards. | pass, fail, n/a
checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED. | pass, fail, n/a
checkpoint | Toilet's, Toilet seat's, Cistern's and flush button installed and water tested. | pass, fail, n/a
button | Flush toilet's 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes, No
checkpoint | Basin mixer's and basin's installed. | pass, fail, n/a
button | Basin mixer's solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes, No
button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes, No
checkpoint | Shower mixer cover plate/handle and shower rail or rose installed. | pass, fail, n/a
button | Run Shower for 15 min, inspect for cross connections, floorwaste blockages and ensure aerators are cleared. | Yes, No
checkpoint | HW heater installed as per drawings and specification, purged and tested. | pass, fail, n/a
checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters) | pass, fail, n/a
checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters). | pass, fail, n/a
button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes, No
text | Pressure Reading and temperature within apartment or hotel.
checkpoint | All fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary) | pass, fail, n/a
label | General photos, comments & observations during fitout stage (Add below).
checklist | Common Disabled bathroom roughins
Section | Roughin
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards. | pass, fail, n/a
label | Check scope of works/specification & ensure all documents are current
checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and scematics | pass, fail, n/a
checkpoint | Check for any cross connections. | pass, fail, n/a
checkpoint | Basin wastes and toilet waste offset and tested with water if required. | pass, fail, n/a
checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward. | pass, fail, n/a
checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward. | pass, fail, n/a
checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided. | pass, fail, n/a
checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications. | pass, fail, n/a
button | Seperation of services as per AS3500 | Yes, No
checkpoint | All setouts ok and run eyes over crimps | pass, fail, n/a
checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own. | pass, fail, n/a
checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc | pass, fail, n/a
button | Smoke seal applied to all penetrations required. | Yes, No
checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary) | pass, fail, n/a
Section | Fitout and Commissioning
checkpoint | Bathroom fixtures installed at correct height/ clearnce. Comply with Architectural drawings and Australian standards. | pass, fail, n/a
checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED. | pass, fail, n/a
checkpoint | Toilet's, Toilet seat's, Cistern's and flush button installed and water tested. | pass, fail, n/a
button | Flush toilet's 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes, No
checkpoint | Basin mixer's and basin's installed. | pass, fail, n/a
button | Basin mixer's solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes, No
button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes, No
checkpoint | Shower mixer cover plate/handle and shower rail or rose installed. | pass, fail, n/a
button | Run Shower for 15 min, inspect for cross connections, floorwaste blockages and ensure aerators are cleared. | Yes, No
checkpoint | HW heater installed as per drawings and specification, purged and tested. | pass, fail, n/a
checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters) | pass, fail, n/a
checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters). | pass, fail, n/a
button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes, No
text | Pressure Reading and temperature within apartment or hotel.
checkpoint | All fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary) | pass, fail, n/a
label | General photos, comments & observations during fitout stage (Add below).
checklist | Garbage Room Work
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans. | pass, fail, n/a
label | Check scope of works/specification & ensure all documents are current.
checkpoint | Pressure and drianage services installed as per workshop drawings and AS3500. | pass, fail, n/a
button | Thermal lagging as per project requirements. | yes, no
checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications. | pass, fail, n/a
checkpoint | Hose taps installed at correct heights. | pass, fail, n/a
checkpoint | Bucket trap wastes installed and grate secured. | pass, fail, n/a
checkpoint | Clear out debris from bucket trap floor wastes. | pass, fail, n/a
checkpoint | Tundish points installed as required. | pass, fail, n/a
checkpoint | HW heater installed as per drawings and specification, purged and tested. | pass, fail, n/a
checkpoint | RPZD valve installed as per AS3500. | pass, fail, n/a
button | RPZD drain installed and tested. | yes, no
label | Please attach photo of serial number and valve.
checkpoint | All tests completed as per AS3500. | yes, no
checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary) | pass, fail, n/a
checklist | Cleaners Rooms
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls and Reflected ceiling plans. | pass, fail, n/a
label | Check scope of works/specification & ensure all documents are current.
checkpoint | Pressure and drianage services installed as per workshop drawings and AS3500. | pass, fail, n/a
button | Thermal lagging as per project requirements. | yes, no
checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications. | pass, fail, n/a
checkpoint | Hose taps installed at correct heights. | pass, fail, n/a
checkpoint | Bucket trap or floor wastes installed and grate secured. | pass, fail, n/a
checkpoint | Clear out debris from bucket trap or floor wastes. | pass, fail, n/a
checkpoint | Tundish points installed as required. | pass, fail, n/a
checkpoint | Fit out of cleaners room hydraulic PC items | pass, fail, n/a
button | Commision PC items and set Temp valve to 49 degrees | yes, no
checkpoint | All tests completed as per AS3500. | yes, no
checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary) | pass, fail, n/a
checklist | Parents Room Rough In
Section | Roughin
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards. | pass, fail, n/a
label | Check scope of works/specification & ensure all documents are current
checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and scematics | pass, fail, n/a
checkpoint | Check for any cross connections. | pass, fail, n/a
checkpoint | Basin wastes and toilet waste offset and tested with water if required. | pass, fail, n/a
checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward. | pass, fail, n/a
checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward. | pass, fail, n/a
checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided. | pass, fail, n/a
checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications. | pass, fail, n/a
button | Seperation of services as per AS3500 | Yes, No
checkpoint | All setouts ok and run eyes over crimps | pass, fail, n/a
checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own. | pass, fail, n/a
checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc | pass, fail, n/a
button | Smoke seal applied to all penetrations required. | Yes, No
checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary) | pass, fail, n/a
Section | Fitout and Commissioning
checkpoint | Bathroom fixtures installed at correct height/ clearnce. Comply with Architectural drawings and Australian standards. | pass, fail, n/a
checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED. | pass, fail, n/a
checkpoint | Toilet's, Toilet seat's, Cistern's and flush button installed and water tested. | pass, fail, n/a
button | Flush toilet's 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes, No
checkpoint | Basin mixer's and basin's installed. | pass, fail, n/a
button | Basin mixer's solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes, No
button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes, No
checkpoint | Shower mixer cover plate/handle and shower rail or rose installed. | pass, fail, n/a
button | Run Shower for 15 min, inspect for cross connections, floorwaste blockages and ensure aerators are cleared. | Yes, No
checkpoint | HW heater installed as per drawings and specification, purged and tested. | pass, fail, n/a
checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters) | pass, fail, n/a
checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters). | pass, fail, n/a
button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes, No
text | Pressure Reading and temperature within apartment or hotel.
checkpoint | All fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary) | pass, fail, n/a
label | General photos, comments & observations during fitout stage (Add below).
checklist | Managers Office Work - Bathroom
Section | Roughin
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards. | pass, fail, n/a
label | Check scope of works/specification & ensure all documents are current
checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and scematics | pass, fail, n/a
checkpoint | Check for any cross connections. | pass, fail, n/a
checkpoint | Basin wastes and toilet waste offset and tested with water if required. | pass, fail, n/a
checkpoint | Internal cisterns installed and tested. Ensure cisterns is installed as far forward. | pass, fail, n/a
checkpoint | In Wall mixers installed and tested. Ensure Mixer is installed as far forward. | pass, fail, n/a
checkpoint | Urinal sensors installed with cabling. Ensure access panels will be provided. | pass, fail, n/a
checkpoint | Grommets, Bracketing installed as per AS3500 and manufacturer's specifications. | pass, fail, n/a
button | Seperation of services as per AS3500 | Yes, No
checkpoint | All setouts ok and run eyes over crimps | pass, fail, n/a
checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own. | pass, fail, n/a
checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc | pass, fail, n/a
button | Smoke seal applied to all penetrations required. | Yes, No
checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary) | pass, fail, n/a
Section | Fitout and Commissioning
checkpoint | Bathroom fixtures installed at correct height/ clearnce. Comply with Architectural drawings and Australian standards. | pass, fail, n/a
checkpoint | ALL FLOOR WASTES TO BE INSPECTED FOR BLOCKAGES AND CLEARED. | pass, fail, n/a
checkpoint | Toilet's, Toilet seat's, Cistern's and flush button installed and water tested. | pass, fail, n/a
button | Flush toilet's 5 times, check seat's, check cistern level, Silicon finish acceptable and button operation. | Yes, No
checkpoint | Basin mixer's and basin's installed. | pass, fail, n/a
button | Basin mixer's solid, check for cross connection, run tap, clear trap, tighten flexis & trap and check mini cocks+traps for leaks. | Yes, No
button | Waste's connected (FILL & TEST BOWL) check for leaks, AAV's installed if applicable and cover plates installed. | Yes, No
checkpoint | Shower mixer cover plate/handle and shower rail or rose installed. | pass, fail, n/a
button | Run Shower for 15 min, inspect for cross connections, floorwaste blockages and ensure aerators are cleared. | Yes, No
checkpoint | HW heater installed as per drawings and specification, purged and tested. | pass, fail, n/a
checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters) | pass, fail, n/a
checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters). | pass, fail, n/a
button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes, No
text | Pressure Reading and temperature within apartment or hotel.
checkpoint | All fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary) | pass, fail, n/a
label | General photos, comments & observations during fitout stage (Add below).
checklist | Commercial / Club Tenancy
Section | Roughin
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards. | pass, fail, n/a
label | Check scope of works/specification & ensure all documents are current
checkpoint | CW,HW,WW, NPCW & or RAINWATER services installed correctly as per workshop drawings and scematics | pass, fail, n/a
checkpoint | Check for any cross connections. | pass, fail, n/a
button | Seperation of services as per AS3500 | Yes, No
checkpoint | All setouts ok and run eyes over crimps | pass, fail, n/a
checkpoint | Hydrostatic test filled with water and pumped @ 1000kpa. Ensure shower mixers are off and test the shower head on its own. | pass, fail, n/a
checkpoint | Passive fire requirements installed, Fire Penetration stickers installed & logged on firedoc | pass, fail, n/a
button | Smoke seal applied to all penetrations required. | Yes, No
checkpoint | All Pressure Services work completed to specification/drawings & Area left clean/tidy (attach photos if necessary) | pass, fail, n/a
Section | Fitout and Commissioning
checkpoint | Kitchen mixer and sink installation complete. | pass, fail, n/a
button | Kitchen mixer solid, check for cross connection, run tap, clear S&P trap, tighten flexis& trap and check mini cock for leaks. | Yes, No
button | Waste connected (FILL & TEST BOWL). CHECK NO LEAKS and AAV installed if applicable. | Yes, No
checkpoint | Tundish point installed as required. | pass, fail, n/a
checkpoint | HW heater installed as per drawings and specification, purged and tested. | pass, fail, n/a
checkpoint | Check pressure reading in unit, Set & Clear PRV. No less than 250kpa or more than 450Kpa (clear filters) | pass, fail, n/a
checkpoint | Temp valve or Thermostatic mixing valve installed and tested (clear filters). | pass, fail, n/a
button | Set temp valve to 48-49 degrees and Thermostatic mixing valve to a maximum of 45 degrees. (attach photo of TMV) | Yes, No
text | Pressure Reading and temperature within apartment or hotel.
checkpoint | All fit out Service works completed to specification/drawings & Area left clean/tidy (attach photos if necessary) | pass, fail, n/a
label | General photos, comments & observations during fitout stage (Add below).
checklist | Tenancy Works
checkpoint | Set out to be off current Hydraulic and Architectural drawings. Consider Walls, RCP's and Australian standards. | pass, fail, n/a
checkpoint | Sewer and trade waste Provisions installed in correct locations and capped off. | pass, fail, n/a
checkpoint | Vent provisions and AAVS installed as per documetation and AS3500. | pass, fail, n/a
checkpoint | Cold Water Gas Point Provision Installed in correct locations and capped off. | pass, fail, n/a
button | Sydney water meter installed if applicable. | yes, no
checkpoint | Fire hose reel installed as pe Australian standards, tested and tagged. (IF APPLICABLE) | pass, fail, n/a
checkpoint | CCTV all lines to ensure clear | pass, fail, n/a
checklist | Water Connection
checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required. | pass, fail, n/a
checkpoint | Services scan within area completed | pass, fail, n/a
checkpoint | Opening permits from authorities complete. Traffic control booked in. | pass, fail, n/a
checkpoint | Non destructive excavation if many services are within the footpath or road. | pass, fail, n/a
checkpoint | Works installed as per drawings and Tested as per AS3500. (attach photos if necessary) | pass, fail, n/a
checklist | Sewer Connection
checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required. | pass, fail, n/a
checkpoint | Services scan within area completed | pass, fail, n/a
checkpoint | Opening permits from authorities complete. Traffic control booked in. | pass, fail, n/a
checkpoint | Non destructive excavation if many services are within the footpath or road. | pass, fail, n/a
checkpoint | Works installed as per drawings and Tested as per AS3500. (attach photos if necessary) | pass, fail, n/a
checkpoint | Fair trading inspection complete. | pass, fail, n/a
checklist | Stormwater Connection
checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required. | pass, fail, n/a
checkpoint | Services scan within area completed | pass, fail, n/a
checkpoint | Opening permits from authorities complete. Traffic control booked in. | pass, fail, n/a
checkpoint | Non destructive excavation if many services are within the footpath or road. | pass, fail, n/a
checkpoint | Works installed as per drawings and Tested as per AS3500. (attach photos if necessary) | pass, fail, n/a
checkpoint | Council inspection complete. | pass, fail, n/a
checklist | Gas Connection
checkpoint | Dial Before You Dig drawings obtained and are read and fully understood. Standby booked in if required. | pass, fail, n/a
checkpoint | Services scan within area completed | pass, fail, n/a
checkpoint | Opening permits from authorities complete. Traffic control booked in. | pass, fail, n/a
checkpoint | Non destructive excavation if many services are within the footpath or road. | pass, fail, n/a
checkpoint | Works installed as per drawings and Tested as per Jemena requirements (attach photos if necessary) | pass, fail, n/a
checklist | DDCV for Fire supply
checkpoint | DDCV installed as per Sydney water guidelines. | pass, fail, n/a
checkpoint | check for leaks and also bracketing as per AS3500. | pass, fail, n/a
checkpoint | DDCV valve installed as per AS3500. For fire supply. | pass, fail, n/a
button | DDCV drain installed and tested. | yes, no
label | Please attach photo of serial number and valve.
checklist | RPZD and Water Meter Install
checkpoint | Water meter installed as per Sydney water guidelines. | pass, fail, n/a
checkpoint | check for leaks and also bracketing as per AS3500. | pass, fail, n/a
checkpoint | Take photos of device & ensure to get all serial numbers | pass, fail, n/a
checkpoint | Test & commission device as required by certified persons | pass, fail, n/a
checkpoint | RPZD valve installed as per AS3500. | pass, fail, n/a
button | RPZD drain installed & tested. | yes, no
label | Please attach photo of serial number and valve.
checklist | Gas Meter
checkpoint | Arrange gas inspector for inspection and requirements. | pass, fail, n/a
checkpoint | Gas reg to be installed on plinth if external. Install as per Jemena requirments. | pass, fail, n/a
checkpoint | Run breather vents off regulators if installed internally. Pipe size usually 25mm | pass, fail, n/a
checkpoint | Ensure the Gas reg is installed in correct orientation. | pass, fail, n/a
checkpoint | Labelling - 1050kpa, 210kpa and or 5 Kpa | pass, fail, n/a
checkpoint | Test all pipework and joints for leaks. | pass, fail, n/a
checkpoint | Reg test point to be facing in a direction where accessible. | pass, fail, n/a
checkpoint | Union or flange connection with valves so that reg can be removed or serviced. | pass, fail, n/a
checkpoint | Take photo of serial number and gas meter. | pass, fail, n/a
checkpoint | Arrange gas inspector for inspection. | pass, fail, n/a
label | All works completed to specification/drawings, Jemena standards & Area left clean/tidy
checklist | Oil Separator Install
checkpoint | Check Tank, Clean and flush out. | pass, fail, n/a
checkpoint | Check all valves are installed & correct. SWING CHECK VALVE TO BE INSTALLED ONLY. | pass, fail, n/a
checkpoint | Check all connections are secured and sound, | pass, fail, n/a
checkpoint | Ensure power has been connected to pump set. Tank to be a minimum 1500mm away from pump. | pass, fail, n/a
checkpoint | Check all floats & wiring are installed correctly. Book pump supplier to commision. | pass, fail, n/a
checkpoint | Check for leaks as fill outlet line with water. | pass, fail, n/a
checkpoint | Oil Separator installed in correct orientation (inlet/outlet). | pass, fail, n/a
checkpoint | Ensure all items including oil drum are with oil Separator | pass, fail, n/a
checkpoint | Ensure all venting requirements are met | pass, fail, n/a
checkpoint | Take photo of serial number and tank. | pass, fail, n/a
label | All works completed to specification/drawings, Sydney water standards & Area left clean/tidy
checklist | Grease Tank
checkpoint | Check Tank, Clean and flush out. | pass, fail, n/a
checkpoint | Grease tank installed in correct orientation (inlet/outlet) | pass, fail, n/a
checkpoint | 100mm Chamber vent to atmosphere. | pass, fail, n/a
checkpoint | Trade waste inlet connection. | pass, fail, n/a
checkpoint | Accessibility around tank minimum 600mm. | pass, fail, n/a
checkpoint | Platform installed within room. | pass, fail, n/a
checkpoint | Suction line within room installed. 80mm minimum line, storz adapter and shut off valve. | pass, fail, n/a
checkpoint | I.O's installed inlet and outlet. | pass, fail, n/a
checkpoint | Ensure lids are closed off properly. | pass, fail, n/a
checkpoint | Take photo of serial number and tank. | pass, fail, n/a
checkpoint | RPZD valve installed as per AS3500. | pass, fail, n/a
button | RPZD drain installed & tested. | yes, no
label | Please attach photo of serial number and valve.
checkpoint | Arrange trade waste inspection if required. | pass, fail, n/a
label | All works completed to specification/drawings, Sydney water standards & Area left clean/tidy
checklist | Sewer Pump Station
checkpoint | Check Tank, Clean and flush out. | pass, fail, n/a
checkpoint | Check all valves are installed & correct. SWING CHECK VALVE TO BE INSTALLED ONLY. | pass, fail, n/a
checkpoint | Check all connections are secured and sound, | pass, fail, n/a
checkpoint | Ensure power has been connected to pump set. | pass, fail, n/a
checkpoint | Check all floats & wiring are installed correctly. Book pump supplier to commision. | pass, fail, n/a
checkpoint | Check for leaks as fill outlet line with water. | pass, fail, n/a
checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary) | pass, fail, n/a
checklist | Storm Water Pump Station
checkpoint | Check Tank, Clean and flush out. | pass, fail, n/a
checkpoint | Check all valves are installed & correct. SWING CHECK VALVE TO BE INSTALLED ONLY. | pass, fail, n/a
checkpoint | Check all connections are secured and sound, | pass, fail, n/a
checkpoint | Ensure power has been connected to pump set. | pass, fail, n/a
checkpoint | Check all floats & wiring are installed correctly. Book pump supplier to commision. | pass, fail, n/a
checkpoint | Check for leaks as fill outlet line with water. | pass, fail, n/a
checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary) | pass, fail, n/a
checklist | Rainwater Pressure Pump and filtration
checkpoint | RW pump and fiiltration installed as per AS3500 and workshop drawings. | pass, fail, n/a
checkpoint | Plinth poured and vibration mounts installed. | pass, fail, n/a
checkpoint | Ensure all connections are sound and secure. | pass, fail, n/a
checkpoint | Ensure all clips & fixings installed as required. | pass, fail, n/a
checkpoint | Pump and filtration panel to have elctrical wired up | pass, fail, n/a
checkpoint | Pump supplier to commission . Purge pumpset and set pressures corrcetly. | pass, fail, n/a
text | Date of commission
checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary) | pass, fail, n/a
checklist | Cold Water Pressure Pump
checkpoint | RW pump and fiiltration installed as per AS3500 and workshop drawings. | pass, fail, n/a
checkpoint | Plinth poured and vibration mounts installed. | pass, fail, n/a
checkpoint | Ensure all connections are sound and secure. | pass, fail, n/a
checkpoint | Ensure all clips & fixings installed as required. | pass, fail, n/a
checkpoint | Pump and filtration panel to have elctrical wired up | pass, fail, n/a
checkpoint | Pump supplier to commission . Purge pumpset and set pressures corrcetly. | pass, fail, n/a
text | Date of commission
checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary) | pass, fail, n/a
checklist | Water Storage Tank
checkpoint | Workshop Drawings issued for construction/ COORDINATED and approved. | pass, fail, n/a
checkpoint | Slab or plinth poured and waterproofed. | pass, fail, n/a
checkpoint | Tank installers to install tank only. | pass, fail, n/a
Button | Tank supplier issues certificates and authorisation to fill tank. | pass, fail, n/a
checkpoint | All valves, overflows , tank top up and sludge drains installed to tank. | pass, fail, n/a
checkpoint | Fill tank up in 500mm increments. Inspect tank for any leaks and continue till you reach desired level design. | pass, fail, n/a
checkpoint | Dump tank and ensure sludge drain and pipe work is operational. | pass, fail, n/a
checkpoint | Set float valve as per manufacturer's specification. | pass, fail, n/a
checkpoint | Once tank is commissioned book in Chlorination by tank supplier. | pass, fail, n/a
checkpoint | Tank level indicator installed and connected to BMS | pass, fail, n/a
checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary) | pass, fail, n/a
checklist | Fire Hydrant/Sprinkler Pump Room & Tank
checkpoint | Workshop Drawings issued for construction/ COORDINATED and approved. | pass, fail, n/a
checkpoint | Cold water services installed correctly as per workshop drawings | pass, fail, n/a
checkpoint | Rainwater reuse service s installed correctly as per workshop drawings. | pass, fail, n/a
checkpoint | Bracketing installed as per AS3500 and manufacturer's specifications. | pass, fail, n/a
checkpoint | Supply & install tank top up supply with correct float valve. | pass, fail, n/a
checkpoint | Wastes to be in correct locations | pass, fail, n/a
checkpoint | Floor wastes installed | pass, fail, n/a
checkpoint | Clear out debris from floor wastes | pass, fail, n/a
checkpoint | Tundish points installed as required | pass, fail, n/a
checkpoint | Water services pressure tested @ 1500KPA or 1.5 x working pressure | pass, fail, n/a
label | Whichever is higher for a minimum duration of 60 minutes | yes, no
checkpoint | Coordination with walls and other services overviewed and coordinated onsite. | pass, fail, n/a
checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary) | pass, fail, n/a
checklist | Hot water flush for trade waste
checkpoint | HW heater installed as per drawings and specification, purged and tested. | pass, fail, n/a
checkpoint | Drainage installed as per AS3500 | pass, fail, n/a
button | Hot water flush installed and commissioned | yes, no
checkpoint | 25mm airgap to void cross contamination | pass, fail, n/a
checkpoint | All tests completed as per AS3500. | yes, no
checkpoint | All works completed to specification/drawings & Area left clean/tidy. (attach photos if necessary) | pass, fail, n/a
checklist | Carpark finalisation
checkpoint | Bracketing completed as per AS3500 | pass, fail, n/a
checkpoint | Pipe jettiing and CCTV completed | pass, fail, n/a
checkpoint | All RWO or CPO grates installed and secured. | pass, fail, n/a
checkpoint | Fire doc finalised and submitted | pass, fail, n/a
checkpoint | All works completed to specification/drawings & Area left clean/tidy (attach photos if necessary) | pass, fail, n/a
checklist | Project finalisation
checkpoint | CCTV complted throughout | pass, fail, n/a
checkpoint | Fire doc finalised and submitted | pass, fail, n/a
checkpoint | SSD produced by designer. | pass, fail, n/a
checkpoint | Asbuilts completed and issued to builder. | pass, fail, n/a
checkpoint | O&M manual completed and sent to builder. | pass, fail, n/a
checkpoint | RPZ test completed and issued to Sydney water. | pass, fail, n/a
checkpoint | DDCV test completed and issued to Sydney water. | pass, fail, n/a
checkpoint | TMV's tested throughout. | pass, fail, n/a
checkpoint | Gas final inspection completed and certificates sent. | pass, fail, n/a
checkpoint | Certification of everything required issued to builder. | pass, fail, n/a
checkpoint | Trade waste final inspection and certified. | pass, fail, n/a
checkpoint | Maintenace manual created and locked in. | pass, fail, n/a
checkpoint | FHR flow test completed and issued. | pass, fail, n/a
checklist | Variation
checkpoint | Variation Details Approved | pass, fail, n/a
text | Reference/Drawing/Instruction Number
text | Variation Area
text | Materials & labour breakdown (Names, Hours & Material(s)/Quantities)
checkpoint | Variation Completed | pass, fail, n/a