## General
Modify template as required prior to use, e.g. to accommodate project or customer specific requirements, then delete this instructional text when complete.
SECTION 1 – GENERAL DETAILS
Project Name: | Seacliff Wastewater Treatment and Disposal Upgrade |  |  |  |  | Inspection Key Use in sections 3, 4 and 5. |  | Responsibilities Use in sections 3, 4 and 5.
Project Number: | 561469 |  |  |  |  | A | Action | Role Key |  | Name | Signature/ Initial
Customer: | Dunedin City Council |  |  |  |  | B | Report by Breach | CM | Construction Manager
Contract Number: | 9776 |  |  |  |  | C | Check | CR | Cust. Representative
Area/ Sub-System: |  |  | Lot ID Number: |  |  | D | Dimension Inspection | IP | Inspection Personnel
[6 empty] | E | Examine | MC | Material Controller
ITP Number: | 1 |  | Version: | 1 |  | H | Hold Point | OP | Operations Manager
ITP Description: | Culverts |  |  |  |  | I | Inspection | PM | Project Manager
Discipline: | [5 empty] | M | Monitor on Random Basis | PS | Project Supervisor
Specification: | Seacliff Watewater Treatment Plant Upgrade |  |  |  |  | O | Operation | QE | Quality Engineer
[6 empty] | R | Review | QM | QA Manager
Drawings: | 310103025-01-001-C101 to C112 and C120 to C125 |  |  |  |  | S | Subcontractor | SP | Supervisor
[6 empty] | V | Visual Verification | ST | Superintendent
Prepared By: (Name) | Sebastian Charlin |  | Date: | 2023-11-03 |  | W | Witness Point | SV | Surveyor
Quality Specified: | [7 empty] | WS | Welding Supervisor
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  | Name: |  |  | Signature: |  |  |  |  | Date:
Downer Approval |  | Name: |  |  | Signature: |  |  |  |  | Date:
Customer Approval |  | Name: |  |  | Signature: |  |  |  |  | Date:

## Receiving Inspection
SECTION 3 – RECEIVING INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key) | Signature
3.1 | Review all Drawings and Documents | Review all drawings and documentation provided to the Contractor. | Prior to the commencement of Works it must be ensure that all necessary documentation has been provided. | ITP | Prior to the commencement of Works | Visual | R | PM/QE
3.2 | Setting Out Levels and Alignment | All setting out shall be performed by or under the control of a licensed surveyor, who shall certify the accuracy of key dimensions of the as constructed works. Specs 1000: 3.2.4 | Levels and allignment Set Out matches marks shown on the Drawings, 2D data and linework provided or agreed with the Engineer | Compliance surveys or spot checks | Prior to the commencement of Works | Visual, Instrumental | H | SP/QE/SV
3.3 | Service location and Hydro Vacumming | Physically locate the services inside and close to the alignment area and levels depth. Specs 1131: 15.2.1 | All services identified in B4UDig, plans and mark outs has been physically located | Plans Mark out, photos | Prior to the commencement of Works | Visual | H | CR
3.4 | Pipes Delivery | Pipes and pipe fittings shall be of the material, pipe class and joint type nominated on the Drawings. Specs 1131: 14.1 and Drawings C152 - C153 | The charasteritics of the pipes delivered to site match the corresponding drawings details or approved equivalent | Delivery docket, Supplier certificate, Photo | Prior to the commencement of Works | Visual | C | QE/CR
3.5 | Valves Delivery | Gate valves shall comply with AS/NZS 2638. Valves greater than DN50 shall be resilient seated sluice valves. DN50 shall be gate valves. Sluice valves shall be anti-clockwise closing. DN50 gate valves shall be clockwise closing. Valves shall be provided with a surface box according to the asset owner’s engineering standards. Specs 1131: 14.3.1 | The charasteritics of the valves delivered to site match the corresponding specifications, drawings details or approved equivalent | Delivery docket, Supplier certificate, Photo | Prior to the commencement of Works | Visual | C | QE/CR
3.6 | Joints and Fittings | All joints and fittings must comply with wath is estipulated on Specs 1131: 14.3.2 | The charasteritics of the fittings delivered to site match the corresponding specifications, drawings details or approved equivalent | Delivery docket, Supplier certificate, Photo | Prior to the commencement of Works | Visual | C | QE/CR
3.7 | Pipe Bedding and Haunching Agregate | Pipe bedding should be AP20 and in accordance with AS/NZS 2566.2 or AS/NZA 3725. Maximum Dry Density (MDD) and Optimum Water Content (OWC) of the aggregate must be provided. Specs 1131: 14.9.1 | Visual Inspection, Engineer approval | Delivery Docket, Laboratory test results | Prior to the commencement of Works | Visual, Lab Test | H | QE/SP/MC
3.8 | Buried Warning Tape | Metallic detector tape shall be provided to comply with the NZUAG code of practice. Tapes shall comply with AS/NZS 2648.1. Tapes shall incorporate a 316 stainless steel detectable tracer wire where required. Specs 1131: 14.6.1 | Received warning tape comply with specifications and standard | Delivery docket, Supplier certificate, Photo | Prior to the commencement of Works | Visual | C | QE/SP/MC
3.9 | Backfill Aggregate | Backfill aggregate should be GAP 65. Samples of backfill material should be tested in accordence of NZS 4402 to determine the MDD at OMC. The solid density of aggregate should be tested in accordance with NZS 4407. Specs 1131: 16.1.1 | Visual Inspection, Engineer approval | Delivery Docket, Laboratory test results | Prior to the commencement of Works | Visual, Lab Test | H | QE/SP/MC
3.10 | Concrete Manhole, Catchpits and Access Chambers | Precast concrete estructures shall comply with NZS 3106. Specs 1131: 14.5 | Manhole charasteritics Match NZS 3106 | Delivery docket, Supplier certificate, Photo | Prior to the commencement of Works | Visual | C | QE/SP/MC
3.11 | Route Markers | Route markers shall be provided where shown on the Drawings or as required by the Principal. Specs 1131: 14.6.3 | Route marker supplied according to the drawings and requirements | Delivery docket, Photo | Prior to the commencement of Works | Visual | C | QE/SP/MC
3.12 | Material Storage | Storage for materiales must be arranged as it is described in: Specs 1131: 14.10 | Pipe stored according to specifications | Photo | Prior to the commencement of Works | Visual | C | QE/SP/MC
3.13 | Backfill Trail Compaction Testing | Prior to commencement of fill compaction. Trial compaction plateau test should be conducted under presense of Engineer or principal. Methodology to be confirmed in advance generally in accordance with TNZ B/02 specification. Specs 1131: 16.1.1, 16.1.2, 16.1.4. | Compaction Value ≥ Specification Value | Nuclear Density Meter (NDM) Results Sheet, or Clegg Hamer test records | Prior to the commencement of Works. | On site Test | H | QE/CR
3.14 | Defective Materials | Any materials that do not comply with this specification or that have been damaged as a result of the Contractor’s operations shall be removed from site and replaced at the Contractor’s expense. Repairs may be considered at the sole discretion of the Engineer. Specs 1131: 14.12 | Defective material detected and removed from site | Delivery docket, Photo | Prior to the commencement of Works | Visual | C | QE/SP/MC

## In Process Inspections
SECTION 4 – IN-PROCESS INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key) | Signature
4.1 | Site Clearance | The material obtained from site celarance must be dumped at an approved location outside the Site. Specs 1100: 5.1 | Location approved by the Engineer | Dumping Docket | After site clearance | Document Check | C | QE/SP/CR
4.2 | Trees Removal | No tree shall be cut down until the Engineer has given written authorisation for such work to commence. Specs 1100: 6.2 | Engineer Approval | Engineer Writen Authorisation | Before remove any tree | Client Consultation | H | CR
4.3 | Removal of Topsoil | Topsoil shall be stockpiled in areas approved by the Engineer for this purpose. stockpiling operations must ensure the maximum utilisation of each area. Specs 1110: 9.4, TNZ F/1 Clause 4 | Engineer Approval | Engineer Writen Authorisation | Before Topsoil Removal | Client Consultation | C | CR
4.4 | Hazardous Waste and Contaminated soils | Contaminated soils (Type H materials) encountered shall be treated and/or disposed off site in accordance with statutory requirements. Specs 1110: 9.3 | Dumping site approval for contamiantion type | Dumping Docket | If constaminated soils are found | Document Check | C | QE/SP/CR
4.5 | Trench Excavation | Trenches for flexible pipes shall be excavated within tollerances in table from Specs 1131: 15.2.5 unless otherwise stated. | Trench width and pipe clearance to walls comply with requirements | Installation Check Sheet | During trench excavation | Visual, Measurement Check | C | QE/SP
4.6 | Pipe Bedding and Haunching | Bedding and Haunching for flexible pipes should be in accordance with AS/NZS 2556.2 and have minimum embedment zone as shown in table from Specs 1131: 15.2.8.2 | Bedding and haunching high and with comply width requirements | Installation Check Sheet | During bedding and haunching installation | Visual, Measurement Check | C | QE/SP
4.7 | Pipe Line and Level | Pipes shall be laid true to the design line and level within the tolerances specified in Specs 1131: 15.9. Invert levels shall take precedence over depths. Specs 1131: 15.3.12 | Pipe levels are within the tolerance and according to the drawings, 2D data and linework provided or agreed with the Engineer | Grade Check sheet | During pipe installation | Visual, Instrumental | C | SP/QE/SV
4.8 | PE Pipe Installation | Buried PE pipes shall be installed in accordance with AS/NZS 2033 and AS/NZA 2566.2, as applicable. Specs 1131: 15.3.2.2 | PE Pipe Joints and Intallation comply with standard and specifications | Pipe welds QA records, welding checksheets and machine printouts, destructive tests results (if required) | Per weld, and during pipe installation | Visual, Document Check, Lab test (if required) | C | QE/SP
4.9 | PVC Pipe Installation | Buried PVC pipes shall be installed in accordance with AS/NZS 2032 and AS/NZS 2566.2, as applicable. Fusible PVC pipes shall be welded and installed in accordance with the pipe manufacturers recommendations. Specs 1131: 15.3.1. | PVC Pipes Joints and Intallation comply with standard and specifications | Methodology, Pipe welds QA records, welding checksheets and machine printouts, destructive tests results (if required) | Per joint or weld, and during pipe installation | Visual, Document Check, Lab test (if required) | C | QE/SP
4.10 | Precast Concrete Pipe Installation | Joints between precast pipe units shall be self-centering and shall be sealed with butyl mastic or similar approved to form a watertight joint. Concrete pipes shall be installed in accordance with AS/NZS 3725. Specs 1131: 15.3.6 | Precast concrete pipes Joints and Intallation comply with standard and specifications | Methodology. QA records | Per joint, and during pipe installation | Visual | C | QE/SP
4.11 | Aggregate Compaction | Compaction shall be as stated in Specs 1131: 15.4.4. For concrete pipes the verification testing of compaction shall use a method recommended in table 3 of the CPAA Technical Note on Installing Concrete Pipe and approved by the Engineer. Specs 1131: 15.3.6 | Compaction Value ≥ Specification Value | Depending of Pipe material or Aggregate: CBR Checksheet, Nuclear Density Meter (NDM) Results Sheet, Clegg Hamer test records | Every 50m of trench (not confirmed) or specified by Engineer | On site Test | H | QE/CR
4.12 | Backfill Compaction | Selected fill within 0.8m depth from finished surface shall be AP 65. Subgrade and subbase shall be compacted in layers no greater than 200 mm thick unless otherwise agreed with the Engineer. Under carriageway basecourse shall be compacted in layers no greater than 150mm thick unless otherwise aggred with the engineer. Specs 1131: 15.4.3.2, 15.4.3.3 | Dry Density ≥ 95% MDD (Under Carriageway). Dry Density ≥ 90% MDD (Outside Carriageway) | Nuclear Density Meter (NDM) Results Sheet or Clegg Hamer test records | Every 20m of trench, each layer (Under Carriageway) Every 50m of trench, each layer (Outside Carriageway) | On site Test | H | QE/CR
4.13 | Cutting pipes | Where pipes need to be cut to form non-stardard lengths, pipes shall be cut by a method which complies with manufacturers recommendations and provides a clean square profile. Specs 1131: 15.3.7 | Pipe cutted up to the specifications | Methodology, Photos | During pipe installation | Visual | C | QE/SP
4.14 | Manhole Benching | Benching concrete shall have a crushing strength of 20MPa at 28 days. Semi-circular channels and fittings shall be placed in possition simultaneously with concrete benching and be embedded in true to grade level and line. All benching and sloping surfaces on manhole floor shall be rendered in 20mm thick 1:3 mortar and finished with steel trowel and rounded at corners. Specs 1131: 15.5 | Benching built up to the specifications | Methodology, Delivery Dockey, Photos | During benching contruction | Visual | C | QE/SP
4.15 | Subsoil Drains Installation | Drains shall be constructed, geotextile layed and backfill carried out in accordance with TNZ Specification F/6. Specs 1131: 15.7 | Benching built up to the specifications | Methodology, TNZ Specifications F/6 and F/7, Photos, QA records | During Drains Installation | Visual | C | QE/SP
4.16 | Topsoiling and grassing | Topsoil shall be used to dress areas disturbed by the contrat works to a minimum thickness of 100mm. Grass seed shall be sown evenly over the prepared topsoil area. Specs 1131: 15.8.6 | Topsoil installed and grass seed spread in the specified rate and mixture. | QA records, Photos | After compaction of final layer of backfill | Visual | C | QE/SP
4.17 | Tracing Wire | Tracing wire shall be installed and tested according to what is detailed in: Specs 1131: 14.6.2 | Tracer wire installation complies with the specifications | QA records, Photos | Before pipe and fittings installation, testing after the completion of the network section installation | Visual, On site test | C | QE/SP
| Welding PE pipes | Jointing shall be done in accordance with pipe manufactures specifications. Where unspecified PE butt welding shall be in accordance with PIPA POP003 and PE electrofusion welding in accordance with PIPA POP001. All welds shall be marked with weld number and welder identification. (maybe put here that everything must be in accordance to the specs) | Specification 1131 15.3.2.1 | Weld records | each weld
| Bulkheads | Shall be placed and constructed as per DCC typical detail 10328 | Drawing C120, C220 | methodology | During installation
| Joint inspections | Each butt-welded joint will be visually inspected by the engineer | Specification 1131 16.3.2.1 | QA records
| Lab Testing | Three butt welded joints and one section of virgin pipe shall be tested in accordance with ISO 13953. | Specification 1131 16.3.2.2
| Joint inspections | Each electrofusion joint shall be visually inspected by the contractor | Specification 1131 16.3.1 | QA records
| Lab Testing | pipes with nominal diameters 90mm and larger shall be tested in accordance with ISO 13954 | Specification 1131 16.3.2.3
| Ductile Iron Pipe Installation | a) Ductile iron pipes shall be installed in accordance with AS/NZS 2566.2. b) Ductile Iron Pipes shall be cement mortar lined in accordance with AS 1281 or AS/NZS 1516 and comply with NZS 3122 and be externally painted with a bituminous coating in accordance with AS/NZS 3750.4 for Bitumen Paint. c) When laid underground, DI pipes shall have a loose polyethylene protective sleeve to AS 3680 and applied in accordance with AS 3681. Specs 1131: 15.3.3
| Steel Pipe Installation | a) Steel pipes shall be installed in accordance with AS/NZS 2566.2. b) Steel pipes shall have spigot and socket joints with rubber rings or shall be plain ended and butt welded as appropriate. Steel pipes shall be flanged where shown on the Drawings. c) Flanges shall be drilled as specified. d) Pipes for welding shall be joined by an automatic arc welding process capable of consistently producing welds complying with the requirements of NZS 4442. e) Manual arc welding with automatic wire feed and automatic fluxing may only be used for the repair of weld defects. Manual welding shall occupy no more than 2 % of the total weld length in any pipe, and no weld repair shall be longer than 300 mm. f) Full details of the welding procedure and of the edge preparation proposed to be used shall be supplied to the Engineer prior to welding. g) Any faulty welds shall be cut out and rewelded. On no account shall leaks be sealed by caulking. h) On completion and acceptance of the welding, the external corrosion protection shall be suitably repaired, and both the weld and coating inspected by the Principal or Engineer. i) Steel pipes shall be externally protected with one of the following: i. for buried pipes, a high-density polyethylene sleeve, “black jacket” complying with AS/NZS 1518 or “Polyken Synergy” wrapping, or “Polyken YG111” wrapping. ii. for pipe above ground, a zinc metal spray sealed with vinyl or epoxy coating complying with AS/NZS 2312, or a fusion bonded epoxy coating complying with AS/NZS 3862. j) Steel pipes shall be fitted with cathodic protection complying with AS 2239 and AS 2832.1. Specs 1131: 15.3.4
| Stainless Steel Pipe Installation | a) Stainless steel pipes shall be installed in accordance with AS/NZS 2566.2. b) All welds between stainless steel components shall be in accordance with AS 4041. Butt welds shall be full penetration. The weld preparation shall be in accordance with AS/NZS 1554.1. c) All stainless-steel welding shall be carried out using approved welding techniques and appropriate procedures. Welds shall be chemically cleaned and fully passivated to an approved procedure. Specs 1131: 15.3.5
| Pipes in a Common Trench | a) Parallel pipelines in a common trench shall be laid sufficiently apart to ensure that the required compaction and support of the side support material is achieved. b) Minimum clear distances between pipes can be reduced where flowable fill embedment materials are used, in line with the applicable pipeline installation standards. Specs 1131: 15.3.8
| Clearances to other Services | Unless agreed with the Engineer or specified elsewhere herein or on the Drawings: • The minimum clearance of sewer to other services is in table 5.6 to other utility services and structures in clause 5.3.7.10 of NZS4404. • The minimum clearance of water pipelines is in table 6.4 to other utility services and structures in clause 6.3.9.2 of NZS4404. Specs 1131: 15.3.9
| Pipes Connected to Structures | a) Where a pipe is built into an underground structure, a flexible joint shall be provided as close as possible to the outside face of the structure. A short length of rocker pipe shall be connected to the flexible joint. The length of the rocker pipe shall not exceed 8 times the diameter or three (3) metres, whichever is the shorter and shall be a minimum of 1,200 mm. b) PE, PVC connections through walls and floors: an annular space of not less than 6 mm shall be left around the pipe or fitting and the clearance shall be sealed with a flexible sealant such as loosely packed felt, a rubber convolute sleeve or other suitable flexible sealing material such as PE foam or neoprene. c) Water-tightness at penetrations. Unless otherwise specified, for (material A, etc.) penetrations through a chamber or manhole wall shall be secured either with a concrete anchor block extending 1.5 x pipe diameters and puddle flange with rubber ‘O’ ring and hydrophilic sealant strip. For (material X, etc.) penetrations shall be secured with a concrete anchor block extending 1.5 x pipe diameter with hydrophilic sealant strips. Specs 1131: 15.3.10
| Cast in-situ Concrete | Concrete cast in-situ for bedding, haunching, thrust blocks, anchor blocks and minor structures shall have a minimum strength of 20 Mpa at 28 days | Specification 1131 14.7

## Final Inspection and Handover
SECTION 5 – FINAL INSPECTION AND HANDOVER Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key) | Signature
5.1 | As-built Drawings | Two hard copies and one electronic copy of As-built drawings shall be prepared in draft and final versions following Schedule 1D in NZS4404:2010. Specs 1000: 3.9.2 | Engineer Approval | QA records | At completion | - | H | QE/CR
5.2 | Gravity Pipes Testing | Stormwater pipes shall be by visual inspection for pipe diameters greater than 750mm and by water testing for diameters up to 750mm. Testing shall be in the presence of the engineer. Specs 1131: 16.2.1 | Engineer Approval | Test Records | For every section of pipe installed (24hr prior notice to the engineer before test) | Test | H | QE/CR
5.3 | Manholes | Manholes should be tested seperately to pipeline for water tightness up to lower rim of manhole cover frame. Testing shall be in the presence of the engineer. Specs 1131: 16.2.2.5 | A maximum drop in water level over 30 min should not exceed 2mL/hr/mm of diameter/meter height of the manhole. Engineer Approval | Test Records | For every manhole installed (24hr prior notice to the engineer before test) | Test | H | QE/CR
5.4 | CCTV Inspection | All pipelines shall pass a CCTV instpection. All pipelines shall be free of debris and flushed 24hrs prior to inspection. Specs 1131: 16.2.3 | A pipeline will fail its inspection if: - The pipe is horizontally misaligned or deformed by more than 5 % of the pipe diameter. - The pipe has visible dips or ponding of water. - The pipe has visible defects, such as open or displaced joints, defective or protruding laterals, cracked barrels or similar defects. - There is evidence of infiltration at joints or laterals. | CCTV footage and log sheets | At every section of pipe installed. | Visual | H | QE/CR
5.5 | Surplus Materials and Refuse Disposal | All surplus, redundant and faulty materials must be removed from the Site and dispose of them in a safe and legal manner. Any demolition material or rubbish coming from the execution of the project must be removed as well. Specs 1000: 3.13.2 | - | - | At completion | Visual | C | QE/SP/CR
5.6 | Cleaning | Completed items of construction about to be placed in service or occupied for their intended use must be properly and thoroughly cleaned of all foreign matter and other debris. Specs 1000: 3.13.3 | - | - | At completion | Visual | C | QE/SP/CR
| Air testing |  | Specification 1131 16.2.2.1 | Test Records
| Pressure Testing | PE pipelines shall be completed in accordance with AS/NZS 2566.2:2002 relevant appendices | Specification 1131 16.3.1 | Test records
| Corrosin Protection | a) Metallic connections shall be appropriately protected against galvanic / dissimilar material corrosion. b) Metallic connections in contact with soil, regardless of any factory applied corrosion protection (e.g. HDG, FBE), shall be fully protected with a suitable petrolatum based wrapping tape (e.g. Denso Petrolatum, Polyken tape), including appropriate filler treatment (e.g. Densyl Mastic, Polyken Mastic) as and where required to ensure the tape does not bridge voids. c) Corrosion protection systems shall be made available for inspection once they have been installed in situ, unless the Engineer permits otherwise. Specs 1131: 14.4
SECTION 6 – COMMENTS
|  |  | Customer Release Granted: | ☐ Yes | ☐ No | Date:
Certificate Number: