## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | FHC-ITP-039 - Hearing Loops (AFILs) Rev1 | itp |  |  |  |  | FHC-ITP-039 - Hearing Loops (AFILs) Rev1
section | 1 - Preliminary Works
checkpoint | 1.1 Check for correct documentation
label | FREQUENCY: Prior to commencing any activity
label | – – – – – – – – –
label | ACCEPTANCE CRITERIA: Ensure that all employees and subcontractors are:
label | – using the correct and complete set of drawings
label | – all drawings are the latest revision
label | – – – – – – – – –
label | REFERENCE DOCUMENTS: Drawings and drawing registers
label | – – – – – – – – –
label | INSPECTION/TEST METHOD: Visual inspection
label | – – – – – – – – –
label | RECORD OF CONFORMITY: This ITP signed off
label | – – – – – – – – –
label | IP
label | – – – – – – – – –
label | RESPONSIBILITY: Fulton Hogan Engineer
label | – – – – – – – – –
text | DATE:
checkpoint | 1.2 Implementation of all measures and controls
label | FREQUENCY: Prior to commencing any activity
label | – – – – – – – – –
label | ACCEPTANCE CRITERIA: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, JSEA, SWMS & WP
label | – – – – – – – – –
label | REFERENCE DOCUMENTS: PSP, EMP, TMP, JSEA, SWMS, WP
label | – – – – – – – – –
label | INSPECTION/TEST METHOD: Visual Inspection
label | – – – – – – – – –
label | RECORD OF CONFORMITY: This ITP signed off
label | – – – – – – – – –
label | IP
label | – – – – – – – – –
label | RESPONSIBILITY: Fulton Hogan Engineer
label | – – – – – – – – –
text | DATE:
section | 2 - Construction Works
checkpoint | 2.1 Setting Out
label | FREQUENCY: Prior to start
label | – – – – – – – – –
label | ACCEPTANCE CRITERIA: Set out work in accordance with drawings and in accordance with alignments, levels, grades, and sections
label | – – – – – – – – –
label | REFERENCE DOCUMENTS: Drawings
label | – – – – – – – – –
label | INSPECTION/TEST METHOD: Visual Inspection
label | – – – – – – – – –
label | RECORD OF CONFORMITY: This ITP signed off
label | – – – – – – – – –
label | IP
label | – – – – – – – – –
label | RESPONSIBILITY: Fulton Hogan Engineer
label | – – – – – – – – –
text | DATE:
checkpoint | 2.2 Position of AFILs
label | FREQUENCY: Prior to application
label | – – – – – – – – –
label | ACCEPTANCE CRITERIA: AFILs shall be installed in coundit underneath concrete & above any reinforcing. The hearing loops shall be installed within a 25 or 32mm conduit with dimensions 4m x 8m to suit drawing setout.
label | – – – – – – – – –
label | REFERENCE DOCUMENTS: NIST-013 6.1.3.1.3.2
label | – – – – – – – – –
label | INSPECTION/TEST METHOD: Visual inspection
label | – – – – – – – – –
label | RECORD OF CONFORMITY: This ITP signed off
label | – – – – – – – – –
label | IP
label | – – – – – – – – –
label | RESPONSIBILITY: Fulton Hogan Engineer
label | – – – – – – – – –
text | DATE:
checkpoint | 2.3 Materials
label | FREQUENCY: Prior to commencement
label | – – – – – – – – –
label | ACCEPTANCE CRITERIA: Hearing loop cable shall be 1C 6mm2 cable & feeder cable star quad 4C 4/6mm2 (twisted pair speaker cable). Hearing loop cable shall be placed in conduit underneath footpath concrete.
label | – – – – – – – – –
label | REFERENCE DOCUMENTS: Drawings
label | – – – – – – – – –
label | INSPECTION/TEST METHOD: Visual inspection
label | – – – – – – – – –
label | RECORD OF CONFORMITY: This ITP signed off
label | – – – – – – – – –
label | IP
label | – – – – – – – – –
label | RESPONSIBILITY: Fulton Hogan Engineer / Subcontractor
label | – – – – – – – – –
text | DATE:
checkpoint | 2.4 Jointing
label | FREQUENCY: Prior to commissioning
label | – – – – – – – – –
label | ACCEPTANCE CRITERIA: Hearing loop 1C 6mm2 cable shall be jointed to 4C feeder cable injunction box located in detector loop pit adjacent to each hearing loop.
label | – – – – – – – – –
label | REFERENCE DOCUMENTS: Drawings
label | – – – – – – – – –
label | INSPECTION/TEST METHOD: Visual inspection
label | – – – – – – – – –
label | RECORD OF CONFORMITY: This ITP signed off
label | – – – – – – – – –
label | IP
label | – – – – – – – – –
label | RESPONSIBILITY: Fulton Hogan Engineer / Subcontractor
label | – – – – – – – – –
text | DATE:
checkpoint | 2.5 OCS Room Connection
label | FREQUENCY: Prior to commissioning for feeder cables
label | – – – – – – – – –
label | ACCEPTANCE CRITERIA: The 4C feeder cable shall be connected to amplifiers in station OCS room ready for commissioning.
label | – – – – – – – – –
label | REFERENCE DOCUMENTS: Drawings
label | – – – – – – – – –
label | INSPECTION/TEST METHOD: Visual inspection
label | – – – – – – – – –
label | RECORD OF CONFORMITY: This ITP signed off
label | – – – – – – – – –
label | HP*
label | – – – – – – – – –
label | RESPONSIBILITY: Fulton Hogan Engineer / Subcontractor
label | – – – – – – – – –
text | DATE:
checkpoint | 2.6 Signage
label | FREQUENCY: Each hearing loop
label | – – – – – – – – –
label | ACCEPTANCE CRITERIA: Public Address loop signage shall be installed in compliance with the drawings.
label | – – – – – – – – –
label | REFERENCE DOCUMENTS: Drawings, AS1428.1, NIST-013 6.1.3.1.5.1
label | – – – – – – – – –
label | INSPECTION/TEST METHOD: Visual inspection
label | – – – – – – – – –
label | RECORD OF CONFORMITY: This ITP signed off
label | – – – – – – – – –
label | IP
label | – – – – – – – – –
label | RESPONSIBILITY: Fulton Hogan Engineer / Subcontractor
label | – – – – – – – – –
text | DATE:
section | 3 - Completion
checkpoint | 3.1 Commissioning
label | FREQUENCY: Each hearing loop
label | – – – – – – – – –
label | ACCEPTANCE CRITERIA: Each hearing loop shall be commissioined by an experienced sound technician / professional in accorance with relevant Australian Standards and IEC standards.
label | – – – – – – – – –
label | REFERENCE DOCUMENTS: AS1428, AS60118.4, IEC 60118.4, NIST-013 6.1.3.1.3
label | – – – – – – – – –
label | INSPECTION/TEST METHOD: Verify
label | – – – – – – – – –
label | RECORD OF CONFORMITY: Commissioning Checklist & Commissioning Certification
label | – – – – – – – – –
label | TP
label | – – – – – – – – –
label | RESPONSIBILITY: Fulton Hogan Engineer / Subcontractor
label | – – – – – – – – –
text | DATE:
checkpoint | 3.2 As-Built
label | FREQUENCY: Post Completion
label | – – – – – – – – –
label | ACCEPTANCE CRITERIA: Red-line markup cable route and installation to suit actual conditions.
label | – – – – – – – – –
label | REFERENCE DOCUMENTS: IFC Drawings, Redline Markup
label | – – – – – – – – –
label | INSPECTION/TEST METHOD: Document Review
label | – – – – – – – – –
label | RECORD OF CONFORMITY: This ITP signed off
label | – – – – – – – – –
label | IP
label | – – – – – – – – –
label | RESPONSIBILITY: Fulton Hogan Engineer
label | – – – – – – – – –
text | DATE:
checkpoint | Final Inspection
label | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
text | Print Name:
text | Position:
text | Date: