## ITP - PCR Precast Panels
INSPECTION & TEST PLAN
|  | Contract Name: | [6 empty] | Rev: | Originator | Date | Approved | Date
|  | 7017 Civil Works |  |  | Hold Point (H) | Verify (V) |  |  | 0 | Michael Polglase | 2023-10-04
ITP - PCR Precast Panels |  |  |  |  | Submit (S) | Review (R) |  |  | 1 | JBD | 2023-10-30
[5 empty] | Approve(A) | Witness (W)
Surveillance (SU)
TASK | SPECIFICATION REFERENCE | TEST REQUIRED | INSPECTION BY | TASK TIMING OR TASK FREQUENCY | ACCEPTANCE CRITERIA | UCCL Signature | Client Signature | UCCL | Client | DATE | COMMENTS
Pre Construction
Review of proposed work | 1235 SHOP DRAWINGS - ITEM 1.10 | Shop drawings to be reviewed and permission to proceed given. | Named reviewer or contract administrator | Start of task | Shop drawings to be accepted by the reviewer. Building Information Model (BIM) is being used for the construction works. |  |  | H | A
Materials
Concrete Mix Design | Ruakaka BESS-Concrete Pads Project Specification 6-P0304.03 | Supplier Documentation | UCCL, MEL | Each Mix Design used prior to use | Foundations (including retaining wall footing) - Aggregate: 19mm 28 day strength: 35MPa Precast retaining wall - Aggregate size: 19mm 28 day strength: 35MPa |  |  | S | R
Certificates | 1.12 Certificates | Portland cement to NZS3121, | UCCL | Each Batch | NZS 3122 |  |  | S | R
Reinforcement | RUK-UMC-DS-01-12 | Supplier Documentation, photos of spacings | UCCL, MEL | Prior to pouring | Reinforcement of precast retaining wall to be YD12-200 vertical and horizontal with D12-200 starters. Reinforcement of in-situ strip footing to be 2/YD12 with R6-300 stirrups |  |  | V | R
strip Footing | RUK-UMC-DS-01-12 | Photos | UCCL, MEL | Prior to pouring | Reinforcement to have maximum 75mm clearance and minimum 50mm clearance.
Cast in Items - Nuts, Bolts and Studs | RUK-UMC-DS-01-10 | Supplier Documentation | UCCL | Prior to Ordering | EA bolts to be M16 Hilti RE-500 |  |  | V | R
Air content test | 1.13 | Supplier Documentation/IANZ Laboratory | UCCL | Each Batch | NZS3109 |  |  | V | R
Slump Test | 1,13 | Supplier Documentation/IANZ Laboratory | UCCL | Each Batch | NZS3109 |  |  | V | R
Conduct 7 day strength test | 3105 - concrete requirements - 1.11 | 7 day strength test | UCCL | 7 day after casting | 60 % of the specified strength |  |  | V | SU
Pre Construction - Site works
Strip Footing |  | Photos | UCCL | Prior to placing site concrete | Strip footing to be 400mm wide and 200mm deep |  |  | V | Su
Subgrade Strength |  | Scala Penetrometer Records | UCCL | Prior to placing site concrete | Subgrade to meet 3 blows/ 100mm with scala testing |  |  | V | W
Formwork | 3105 - concrete requirements - 1.14 | Quality shape and size of formwork | UCCL | Prior to placing concrete | All formwork to meet the specification required for the unit being constructed |  |  | V | W
Site Concrete | = | Visual inspection | UCCL | Each Foundation | Site concrete to be placed at the thicknesses shown on the drawings and finished to a height of +/- 10mm |  |  | V | Su
Setout |  | Survey | UCCL | Each string | Foundations and embedded items shall be set out following the tolerances, heights and positions shown in each foundations respective drawing. |  |  | V | Su
Prepour Inspection
Pre pour inspection |  | Visual Inspection | UCCL, MEL, WSP | Prior to placing structural concrete | Pre pour inspection sheet to be completed prior to placing concrete. WCL to be notified of pours for inspection at least 24 hours prior to placing concrete. |  |  | H | W
Postpour Inspection
Post pour inspection |  | Visual Inspection | UCCL | Following placement of concrete | Post pour inspection sheet to be completed following each pour. |  |  | A | Su
Post Construction
As Built & Final Design Documentation |  | Surveying | UCCL | Completion of PCS slab | Confirmation From Engineer on as built records & redline mark ups |  |  | S | R
Records of: | Products and materials selected for alternatives specified Approved substitutions and accepted alternatives Other approved changes and deviations to items specified. |  | UCC | Completion of PCS slab | Confirmation From Engineer of all records |  |  | S | R
Producer statement | 3105 - concrete requirements - 1.14 | Submit a producer statement for precast units | UCCL | Completion of PCS slab | Producer statement to verify the products meet the requirements specified. |  |  | S | R
Completion Inspection inc. Construction Defects Report |  | Completion inspection on each foundation by CEL | UCCL | Completion of PCS slab | Provided a completed construction defect report that that details any remedial measures taken, & snag lists closed out |  |  | S | R
Identification of panels |  | Panel identification location | UCCL | Completion of PCS slab | Panels to be marked and identified as to which pour they're from and final location. |  |  | V | R
Note on O10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Ref: WSP-CONSC-000137 for shop drawing amendments & IFC drawings have been issued

## Checksheet #1
Ch