## res_ITP_1_Inspection_and_Test_P
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | PCR Precast Panels |  |  |  |  | Yes | ITP - PCR Precast Panels
section | Pre Construction
checkpoint | Review of proposed work
label | SPECIFICATION REFERENCE - 1235 SHOP DRAWINGS - ITEM 1.10
label | TEST REQUIRED - Shop drawings to be reviewed and permission to proceed given.
label | INSPECTION BY - Named reviewer or contract administrator
label | TASK TIMING OR TASK FREQUENCY - Start of task
label | ACCEPTANCE CRITERIA - Shop drawings to be accepted by the reviewer. Building Information Model (BIM) is being used for the construction works.
label | UCCL - H
label | Client - A
holdpoint | HOLD POINT
section | Materials
checkpoint | Concrete Mix Design
label | SPECIFICATION REFERENCE - Ruakaka BESS-Concrete Pads Project Specification 6-P0304.03
label | TEST REQUIRED - Supplier Documentation
label | INSPECTION BY - UCCL, MEL
label | TASK TIMING OR TASK FREQUENCY - Each Mix Design used prior to use
label | ACCEPTANCE CRITERIA -
label | Foundations (including retaining wall footing) -
label | ○ Aggregate: 19mm
label | ○ 28 day strength: 35MPa
label | Precast retaining wall -
label | ○ Aggregate size: 19mm
label | ○ 28 day strength: 35MPa
label | UCCL - S
label | Client - R
checkpoint | Certificates
label | SPECIFICATION REFERENCE - 1.12 Certificates
label | TEST REQUIRED - Portland cement to NZS3121,
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Each Batch
label | ACCEPTANCE CRITERIA - NZS 3122
label | UCCL - S
label | Client - R
checkpoint | Reinforcement
label | SPECIFICATION REFERENCE - RUK-UMC-DS-01-12
label | TEST REQUIRED - Supplier Documentation, photos of spacings
label | INSPECTION BY - UCCL, MEL
label | TASK TIMING OR TASK FREQUENCY - Prior to pouring
label | ACCEPTANCE CRITERIA - Reinforcement of precast retaining wall to be YD12-200 vertical and horizontal with D12-200 starters. Reinforcement of in-situ strip footing to be 2/YD12 with R6-300 stirrups
label | UCCL - V
label | Client - R
checkpoint | Strip Footing
label | SPECIFICATION REFERENCE - RUK-UMC-DS-01-12
label | TEST REQUIRED - Photos
label | INSPECTION BY - UCCL, MEL
label | TASK TIMING OR TASK FREQUENCY - Prior to pouring
label | ACCEPTANCE CRITERIA - Reinforcement to have maximum 75mm clearance and minimum 50mm clearance.
checkpoint | Cast in Items - Nuts, Bolts and Studs
label | SPECIFICATION REFERENCE - RUK-UMC-DS-01-10
label | TEST REQUIRED - Supplier Documentation
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Prior to Ordering
label | ACCEPTANCE CRITERIA - EA bolts to be M16 Hilti RE-500
label | UCCL - V
label | Client - R
checkpoint | Air content test
label | SPECIFICATION REFERENCE - 1.13
label | TEST REQUIRED - Supplier Documentation/IANZ Laboratory
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Each Batch
label | ACCEPTANCE CRITERIA - NZS3109
label | UCCL - V
label | Client - R
checkpoint | Slump Test
label | SPECIFICATION REFERENCE - 1,13
label | TEST REQUIRED - Supplier Documentation/IANZ Laboratory
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Each Batch
label | ACCEPTANCE CRITERIA - NZS3109
label | UCCL - V
label | Client - R
checkpoint | Conduct 7 day strength test
label | SPECIFICATION REFERENCE - 3105 - concrete requirements - 1.11
label | TEST REQUIRED - 7 day strength test
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - 7 day after casting
label | ACCEPTANCE CRITERIA - 60 % of the specified strength
label | UCCL - V
label | Client - SU
section | Pre Construction - Site works
checkpoint | Strip Footing
label | TEST REQUIRED - Photos
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Prior to placing site concrete
label | ACCEPTANCE CRITERIA - Strip footing to be 400mm wide and 200mm deep
label | UCCL - V
label | Client - Su
checkpoint | Subgrade Strength
label | TEST REQUIRED - Scala Penetrometer Records
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Prior to placing site concrete
label | ACCEPTANCE CRITERIA - Subgrade to meet 3 blows/ 100mm with scala testing
label | UCCL - V
label | Client - W
checkpoint | Formwork
label | SPECIFICATION REFERENCE - 3105 - concrete requirements - 1.14
label | TEST REQUIRED - Quality shape and size of formwork
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Prior to placing concrete
label | ACCEPTANCE CRITERIA - All formwork to meet the specification required for the unit being constructed
label | UCCL - V
label | Client - W
checkpoint | Site Concrete
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Each Foundation
label | ACCEPTANCE CRITERIA - Site concrete to be placed at the thicknesses shown on the drawings and finished to a height of +/- 10mm
label | UCCL - V
label | Client - Su
checkpoint | Setout
label | TEST REQUIRED - Survey
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Each string
label | ACCEPTANCE CRITERIA - Foundations and embedded items shall be set out following the tolerances, heights and positions shown in each foundations respective drawing.
label | UCCL - V
label | Client - Su
section | Prepour Inspection
checkpoint | Pre pour inspection
label | TEST REQUIRED - Visual Inspection
label | INSPECTION BY - UCCL, MEL, WSP
label | TASK TIMING OR TASK FREQUENCY - Prior to placing structural concrete
label | ACCEPTANCE CRITERIA - Pre pour inspection sheet to be completed prior to placing concrete. WCL to be notified of pours for inspection at least 24 hours prior to placing concrete.
label | UCCL - H
label | Client - W
holdpoint | HOLD POINT
section | Postpour Inspection
checkpoint | Post pour inspection
label | TEST REQUIRED - Visual Inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Following placement of concrete
label | ACCEPTANCE CRITERIA - Post pour inspection sheet to be completed following each pour.
label | UCCL - A
label | Client - Su
section | Post Construction
checkpoint | As Built & Final Design Documentation
label | TEST REQUIRED - Surveying
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
label | ACCEPTANCE CRITERIA - Confirmation From Engineer on as built records & redline mark ups
label | UCCL - S
label | Client - R
checkpoint | Records of:
label | SPECIFICATION REFERENCE - Products and materials selected for alternatives specified, Approved substitutions and accepted alternatives, Other approved changes and deviations to items specified.
label | INSPECTION BY - UCC
label | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
label | ACCEPTANCE CRITERIA - Confirmation From Engineer of all records
label | UCCL - S
label | Client - R
checkpoint | Producer statement
label | SPECIFICATION REFERENCE - 3105 - concrete requirements - 1.14
label | TEST REQUIRED - Submit a producer statement for precast units
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
label | ACCEPTANCE CRITERIA - Producer statement to verify the products meet the requirements specified.
label | UCCL - S
label | Client - R
checkpoint | Completion Inspection inc. Construction Defects Report
label | TEST REQUIRED - Completion inspection on each foundation by CEL
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
label | ACCEPTANCE CRITERIA - Provided a completed construction defect report that that details any remedial measures taken, & snag lists closed out
label | UCCL - S
label | Client - R
checkpoint | Identification of panels
label | TEST REQUIRED - Panel identification location
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Completion of PCS slab
label | ACCEPTANCE CRITERIA - Panels to be marked and identified as to which pour they're from and final location.
label | UCCL - V
label | Client - R