## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | Civil Checklist - Lighting Columns/Selector Switch/Fixture |  |  |  |  | Yes | Civil Checklist - Lighting Columns/Selector Switch/Fixture | 09b73725-7f70-4d17-a843-2494b911fbbc
checkpoint-group |  |  | section | Verify that lighting columns are:
checkpoint-status |  |  | checkpoint | As-per drawings
checkpoint-group |  |  | section | Verify lighting selector switch is:
checkpoint-status |  |  | checkpoint | Installed per manufacturers specification
checkpoint-status |  |  | checkpoint | As-per drawings
checkpoint-group |  |  | section | Light fixtures
checkpoint-status |  |  | checkpoint | Verify Lumens as per specification
checkpoint-status |  |  | checkpoint | Record serial numbers
holdpoint |  |  | signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist-sectioned |  |  | checklist | Electrical checklist - LV Pillar |  |  |  |  | Yes | Electrical checklist - LV Pillar | 1037f661-7491-46b0-9155-8e96631fb22c
checkpoint-group |  |  | section | LV Pillar Setup/Installation
checkpoint-status |  |  | checkpoint | Confirm the switchboard is correctly located, aligned and foundation bolts and fixings are secure as-per switchroom layout drawings
checkpoint-status |  |  | checkpoint | Check that the final factory test and inspection record is enclosed with the LV Pillar delivered.
checkpoint-status |  |  | checkpoint | Check the LV pillar serial number matches the factory test and inspection record.
checkpoint-status |  |  | checkpoint | Check the LV Pillar is correctly installed and sealed on the foundation plinth, as per the IOM Manual
checkpoint-status |  |  | checkpoint | Visually inspect the LV pillar for external damage (including paintwork)
checkpoint-status |  |  | checkpoint | Verify nameplate details against data sheet. (LV Pillar type, compliance standard, rating in amps)
checkpoint-status |  |  | checkpoint | Check all cubicle doors can be fully opened without obstruction and that door hinges are installed correctly.
checkpoint-status |  |  | checkpoint | Check inside of the switchboard is clean and dry, check that all preservation (i.e. silica gel) has been removed (Pre-Energization)
checkpoint-status |  |  | checkpoint | Ensure all major components conform to vendor's design documentation and drawings.
checkpoint-status |  |  | checkpoint | Check all fuses/fuse carriers and link are correct to drawings
checkpoint-status |  |  | checkpoint | Check all equipment carries the correct circuit identification
checkpoint-status |  |  | checkpoint | Check busbar phase identifications are correct and phasing is maintained
checkpoint-status |  |  | checkpoint | Ensure all busbars are encapsulated as-per design requirements
checkpoint-status |  |  | checkpoint | Check the protective device(s) rating match the approved design
checkpoint-status |  |  | checkpoint | Check LV Cable terminations are completed correctly and are tight and secure
holdpoint |  |  | signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist-sectioned |  |  | checklist | Electrical checklist - Lighting and Small Power |  |  |  |  | Yes | Electrical checklist - Lighting and Small Power | 4c3d2154-6522-4345-9b03-4c20772d0b85
checkpoint-group |  |  | section | Lighting Columns
checkpoint-status |  |  | checkpoint | Verify the number as-per the drawing
checkpoint-status |  |  | checkpoint | Provide lighting cable test results
checkpoint-status |  |  | checkpoint | Check lighting operation
checkpoint-status |  |  | checkpoint | Check lux level of lighting meets design requirements
checkpoint-group |  |  | section | Power supply for Comsat unit
checkpoint-status |  |  | checkpoint | Verify the install is per the agreed design
checkpoint-status |  |  | checkpoint | Provide test results for the small power installation (separate test sheet)
checklist-sectioned |  |  | checklist | Civil Checklist - NAL Solution/Monolithic Foundation |  |  |  |  | Yes | Civil Checklist - NAL Solution/Monolithic Foundation | 532270ce-75e1-4e72-ab5c-e28a81d26b11
checkpoint-group |  |  | section | Ground Conditions:
checkpoint-status |  |  | checkpoint | Verify ground conditions are as per design assumptions
checkpoint-group |  |  | section | Verify STAKKAbox Installation is:
checkpoint-status |  |  | checkpoint | Subgrade prepared per drawings
checkpoint-status |  |  | checkpoint | STAKKAbox installed at location shown on drawing
checkpoint-status |  |  | checkpoint | Correct number of STAKKAbox installed
checkpoint-status |  |  | checkpoint | STAKKAbox are clear of any debris
checkpoint-status |  |  | checkpoint | STAKKAbox are installed at correct depth
checkpoint-status |  |  | checkpoint | Conduits enter at correct locations and verify depth
checkpoint-status |  |  | checkpoint | Protruding above the ground within the specified limits
checkpoint-group |  |  | section | Verify NAL EV Charger Socket is:
checkpoint-status |  |  | checkpoint | Installed per drawing
checkpoint-status |  |  | checkpoint | Correct depth as-per drawing
checkpoint-status |  |  | checkpoint | Verify level prior to EV charger placement
checkpoint-group |  |  | section | Verify NAL Bollard Sockets are:
checkpoint-status |  |  | checkpoint | Installed per drawing & Counts verified
checkpoint-status |  |  | checkpoint | Correct depth & spacing
checkpoint-status |  |  | checkpoint | Verify level
checkpoint-group |  |  | section | Verify NAL Flex-Bollards are:
checkpoint-status |  |  | checkpoint | Installed per drawing & counts verified
checkpoint-status |  |  | checkpoint | Correct height & spacing
checkpoint-status |  |  | checkpoint | Verify they are plumb
checkpoint-status |  |  | checkpoint | Pass pull-test/unable to be lifted out by hand
checkpoint-group |  |  | section | Verify Monolithic foundation (as required) is:
checkpoint-status |  |  | checkpoint | Installed as-per drawing
checkpoint-status |  |  | checkpoint | Pad/foundation is correct depth and dimensions
checkpoint-status |  |  | checkpoint | Rebar is proper size and correctly spaced (Photo)
checkpoint-status |  |  | checkpoint | Top of pad is free of defects, has an even surface with broom finish
checkpoint-status |  |  | checkpoint | Verify conduits are stubbed up in correct location
checkpoint-status |  |  | checkpoint | Protruding above the ground within the specified limits
checkpoint-group |  |  | section | Verify Anchor bolts:
checkpoint-status |  |  | checkpoint | In correct location as per drawing
checkpoint-status |  |  | checkpoint | Proper embedment depth
checkpoint-status |  |  | checkpoint | Pass pull-test/unable to be lifted out by hand
holdpoint |  |  | signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist-flat |  |  | checklist | Toolbox Meeting |  |  |  |  | Yes | Toolbox Meeting | 5d037628-54e7-4093-bd29-9e83729030bf
checkpoint-no-status |  |  | checkpoint | Toolbox meeting
date | 07be43a9-ef90-51e4-8bb3-ff0067e46716 |  | date | Date:
text | 3ef9a2c6-8dd7-5a00-8ddd-392424f6b915 |  | textbox | Meeting location:
text | 0116c33c-9b26-5d71-abd8-e060674c27e8 |  | textbox | Meeting conducted by:
text | c4064d35-12fa-5132-a911-797de49bcf4e |  | textbox | Meeting attendees:
text | df8d43b8-eef1-5cdf-8f9f-cea02b577b7f |  | textbox | Today's work scope/Hazards
text | 20077c2b-ffce-51f6-ad84-b4133d629956 |  | textbox | Hazard controls:
holdpoint |  |  | signoff | Signatures
checklist-sectioned |  |  | checklist | Civil Checklist - LV Pillar Foundation |  |  |  |  | Yes | Civil Checklist - LV Pillar Foundation | 600f5314-391d-44e6-b6d1-97e770cb88d9
checkpoint-group |  |  | section | Ground Conditions:
checkpoint-status |  |  | checkpoint | Verify ground conditions are as-per design assumption
checkpoint-group |  |  | section | NAL/Schneider LV Pillar foundation installation:
checkpoint-status |  |  | checkpoint | Correct location per drawings
checkpoint-status |  |  | checkpoint | Subgrade has been prepared per drawings (attach photo)
checkpoint-status |  |  | checkpoint | Check for level
checkpoint-group |  |  | section | Ensure the conduits between Pillar and EV Charger are:
checkpoint-status |  |  | checkpoint | Sized as indicated in drawing
checkpoint-status |  |  | checkpoint | Routed per drawings
checkpoint-status |  |  | checkpoint | Depth defined in drawing
checkpoint-group |  |  | section | Ensure the conduits between Pillar and Site Lighting/Selector Switch are:
checkpoint-status |  |  | checkpoint | Sized as indicated in drawing
checkpoint-status |  |  | checkpoint | Routed per drawings
checkpoint-status |  |  | checkpoint | Depth defined in drawing
checkpoint-group |  |  | section | Ensure the Fibre Optic/Earthing conduits between Pillar and Sales Store are:
checkpoint-status |  |  | checkpoint | Sized as indicated in drawing
checkpoint-status |  |  | checkpoint | Routed per drawings
checkpoint-status |  |  | checkpoint | Depth defined in drawing
checkpoint-group |  |  | section | Verify working space from front of LV Pillar
checkpoint-status |  |  | checkpoint | Ensure placement will allow for working area and emergency egress
checkpoint-group |  |  | section | As-built height of foundation
checkpoint-status |  |  | checkpoint | Verify protrusion above ground level is as per specification/drawing
checkpoint-group |  |  | section | LV Pillar Installation - if LF Pillar is installed ensure:
checkpoint-status |  |  | checkpoint | Ensure LV Pillar has been bolted down with the correct torque settings as per LV pillar specification
checkpoint-status |  |  | checkpoint | Water tightness/IP Specifications are being met
checkpoint-status |  |  | checkpoint | Record and photograph the serial number of the LV Pillar
holdpoint |  |  | signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist-sectioned |  |  | checklist | Electrical checklist - Metering |  |  |  |  | Yes | Electrical checklist - Metering | 7315fd30-4cfd-4af0-8f82-bc5af92f7cc3
checkpoint-group |  |  | section | DNO Cutout and Metering
checkpoint-status |  |  | checkpoint | Check that the metering unit matches the approved design
checkpoint-status |  |  | checkpoint | check sufficient space is available between the meter and incoming cutout
holdpoint |  |  | signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist-sectioned |  |  | checklist | Civil Checklist - EV Charging Parking Stalls |  |  |  |  | Yes | Civil Checklist - EV Charging Parking Stalls | 74ce1c92-b850-45d0-8812-847f9ffc3b20
checkpoint-group |  |  | section | Verify dimensions match drawings
checkpoint-status |  |  | checkpoint | Depth, Length and Width are per drawings
checkpoint-group |  |  | section | Painted stripes are clean and correct colour
checkpoint-status |  |  | checkpoint | No over spray, colour is correct, lines are straight
holdpoint |  |  | signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist-sectioned |  |  | checklist | Electrical checklist - Cables/Cable Entry Points/Cable Containment |  |  |  |  | Yes | Electrical checklist - Cables/Cable Entry Points/Cable Containment | 79d41136-9978-4dc4-8bcd-eb1909c7248e
checkpoint-group |  |  | section | Cables/Cable Entry Points/Cable Containment
checkpoint-status |  |  | checkpoint | Check all cable entries are correct to design requirements and spare enters are correctly plugged with Rayflates/Foam
checkpoint-status |  |  | checkpoint | Check that the depth of installation of the duct network matches the approved design. (To be witnessed by BP)
checkpoint-status |  |  | checkpoint | Check the number and type/size of ducts installed meets the approved design. (To be witnessed by BP)
checkpoint-status |  |  | checkpoint | Check the cable entry is at the correct depth (Minimum bending radius achieved)
checkpoint-status |  |  | checkpoint | Check the correct type of reinstatement material has been used to backfill the cable/duct network. (100mm of sand below and on top of ducts/cables.)
checkpoint-status |  |  | checkpoint | Check cable warning tape is laid prior to backfilling
checkpoint-status |  |  | checkpoint | Check the high level cable containment (Trays/Ladders) and cable cleats match the approved design.
checkpoint-status |  |  | checkpoint | Check all metal cable containments are bonded and connected to the main earthing system
checkpoint-status |  |  | checkpoint | Check that the tray/ladder is not damaged and is free of any sharp edges.
checkpoint-group |  |  | section | Cables
checkpoint-status |  |  | checkpoint | Check the cables installed are the correct type/size, as per the approved design.
checkpoint-status |  |  | checkpoint | Check the correct bending radius is being applied to the cable at the entry/exit points
checkpoint-status |  |  | checkpoint | Check the cable cleat and clamp screw are secure and tight
checkpoint-status |  |  | checkpoint | Check that the cables have been fully tested after installation and prior to terminating to the LV Pillar (Continuity, insulation resistance)
checkpoint-status |  |  | checkpoint | Check that the cable ends have been correctly capped after installation in ducts, to avoid water ingress in the cable (unless terminated straight after installation and testing)
holdpoint |  |  | signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist-flat |  |  | checklist | Certificate of compliance (COC) |  |  |  |  | Yes | Certificate of compliance (COC) | 7c08be97-7fa8-4291-b9bf-96daf809c06d
checkpoint-status |  |  | checkpoint | Please upload Certificate of Compliance here when complete (COC)
checklist-flat |  |  | checklist | Tritium - Site Installation checklist |  |  |  |  | Yes | Tritium - Site Installation checklist | 91a1f6d9-9235-4587-9f1e-bb042b24f55b
checkpoint-status |  |  | checkpoint | Upload completed Tritium checklist scan
checklist-sectioned |  |  | checklist | Civil Checklist - Miscellaneous Site Civil |  |  |  |  | Yes | Civil Checklist - Miscellaneous Site Civil | 99219a41-c64e-46db-bb3f-c131d94761c6
checkpoint-group |  |  | section | New curb/gutter footpath per plans
checkpoint-status |  |  | checkpoint | Concrete is consistent and installed to match existing appearance and levels
checkpoint-group |  |  | section | Existing curb/gutter sidewalk undamaged
checkpoint-status |  |  | checkpoint | No damage to existing curb/gutters
checkpoint-group |  |  | section | Landscaping removed/damaged during construction is replaced to match
checkpoint-status |  |  | checkpoint | Replacements match what was damaged
checkpoint-group |  |  | section | New landscaping installed per plans. Ensure proper watering is in plans. Verify:
checkpoint-status |  |  | checkpoint | Correct species
checkpoint-status |  |  | checkpoint | height of plants is per plan
checkpoint-status |  |  | checkpoint | irrigation is provided
checkpoint-group |  |  | section | Irrigation system working properly. Irrigation that was disrupted during construction is:
checkpoint-status |  |  | checkpoint | Repaired and operation verified (Site host to provide signature)
checkpoint-status |  |  | checkpoint | Spray patterns are set correctly
checkpoint-group |  |  | section | Air & Water station relocation
checkpoint-status |  |  | checkpoint | Verify air & water station is functioning after relocation (Site host to provide signature)
checkpoint-group |  |  | section | Wheel stops are installed per drawings
checkpoint-status |  |  | checkpoint | Dimensions, height and width are per drawings
checkpoint-group |  |  | section | Parking stall signage complete per plans
checkpoint-status |  |  | checkpoint | Confirm the height of sign posts above grade is accurate and matches drawings
checkpoint-group |  |  | section | Site clean up
checkpoint-status |  |  | checkpoint | All debris removed by the time commissioning occurs. Site housekeeping must be kept up to minimize the disruption to the landlords
holdpoint |  |  | signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist-sectioned |  |  | checklist | Telecom DMC Checklist |  |  |  |  | Yes | Telecom DMC Checklist | a0277eaa-0dc0-471c-9eb9-a3e6809b5298
checkpoint-group |  |  | section | LV Pillar Transceivers
checkpoint-status |  |  | checkpoint | Confirm the emergeny stop details match confirmed design
checkpoint-status |  |  | checkpoint | Confirm emergency stop transciever and shop closer modules match design
checkpoint-status |  |  | checkpoint | Confirm emergency stop is mointed and installed correctly
checkpoint-status |  |  | checkpoint | Check the shop closure transceiver is mounted and has been installed correctly
checkpoint-status |  |  | checkpoint | Check that the protection settings for the protective devices match approved design
checkpoint-status |  |  | checkpoint | Check the protective device(s) ratings match the approved design
checkpoint-status |  |  | checkpoint | Check all equipment carries the correct circuit identification
checkpoint-status |  |  | checkpoint | Check that the fibre optic cables are fitted with the correct plug connectors.
checkpoint-status |  |  | checkpoint | Check that the fibre optic cables are terminated correctly to transciever devices
checkpoint-status |  |  | checkpoint | Check the fibre optic cables are glanded correctly.
checkpoint-status |  |  | checkpoint | Check that the commissioning/lest records for the transceivers are available on site.
checkpoint-status |  |  | checkpoint | Check that the transceivers are earthed correctly
checkpoint-group |  |  | section | Transceivers in shop
checkpoint-status |  |  | checkpoint | Check that the transceiver enclosure is mounted to design requirements
checkpoint-status |  |  | checkpoint | Confirm the E-stop Comnet transceiver and shop closure transceiver model matches design
checkpoint-status |  |  | checkpoint | Confirm the emergency stop Comnet transceiver and shop closure transceiver module selection match the design
checkpoint-status |  |  | checkpoint | Confirm the E-stop Comnet transceiver and shop closure transceiver model matches design
checkpoint-status |  |  | checkpoint | Check all equipment carries the correct circuit identification
checkpoint-status |  |  | checkpoint | Check that the fibre optic cables are fitted with the correct plug connectors.
checkpoint-status |  |  | checkpoint | Check that the fibre optic cables are terminated correctly to transciever devices
checkpoint-status |  |  | checkpoint | Check the fibre optic cables are glanded correctly.
checkpoint-status |  |  | checkpoint | Check that the commissioning/test records for the trancievers are avilable on site
checkpoint-status |  |  | checkpoint | Check that the transceivers are earthed correctly
checkpoint-group |  |  | section | cables
checkpoint-status |  |  | checkpoint | check cables are right type and size as per design
checkpoint-status |  |  | checkpoint | Check that the cable ends have been correctly capped
checkpoint-status |  |  | checkpoint | Check that the cable test records are available on-site.
checkpoint-group |  |  | section | Cable Entry Points/Cable Containment
checkpoint-status |  |  | checkpoint | Check all cable entries are correct to design
checkpoint-status |  |  | checkpoint | If installed at high level, check that the cables are installed correctly on tray
checkpoint-group |  |  | section | CCTV network
checkpoint-status |  |  | checkpoint | Check that the CCTV hardware model and spec matches designs
checkpoint-status |  |  | checkpoint | Check that the wiring of the CCTV network matches the design
checkpoint-status |  |  | checkpoint | Check that the wiring is terminated correctly at the transceiver module
checkpoint-status |  |  | checkpoint | Check that the wiring is glanded correctly.
checkpoint-status |  |  | checkpoint | Check that all the commissioning documents are present on site
holdpoint |  |  | signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist-flat |  |  | checklist | Cable Test Record |  |  |  |  | Yes | Cable Test Record | b3aedf58-ed42-461d-8387-f6eac1b85671
checkpoint-status |  |  | checkpoint | Upload completed ITR scans
checklist-sectioned |  |  | checklist | Electrical checklist - EV Charger |  |  |  |  | Yes | Electrical checklist - EV Charger | be74036d-dca0-4ed5-98bb-8fb158df7b97
checkpoint-group |  |  | section | EV Charger
checkpoint-status |  |  | checkpoint | Check the charger is free of any damage
checkpoint-status |  |  | checkpoint | Check the internal arts are free of any damages
checkpoint-status |  |  | checkpoint | Check the unit s correctly located as-per layout drawing
checkpoint-status |  |  | checkpoint | Check the unit is installed correctly and is level
checkpoint-status |  |  | checkpoint | Check the charger rating matches the purchase order
checkpoint-status |  |  | checkpoint | Check the type of sockets match the purchase order
checkpoint-status |  |  | checkpoint | Check the payment terminal matches the purchase order
holdpoint |  |  | signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist-flat |  |  | checklist | JHA - Job Step |  |  |  |  | Yes | JHA - Job Step | d8d7dbab-1a6b-485b-94de-b65ea497e4d4
checkpoint-no-status |  |  | checkpoint | Task Step - add task step for each individual task
date | e6cb0ae4-3907-5603-8613-3e9e40919c35 |  | date | Date:
text | 29df3865-1487-5e9c-9d9c-1b4cbd4350f8 |  | textbox | Task step number (eg. Step 1, Step 2 etc):
text | 21b02b36-c21d-5193-9f9c-229da97b11a3 |  | textbox | Task details:
text | f7d1b8e2-bb32-5af2-8c80-f6cd0640b01f |  | textbox | Hazards:
select | 8f92a6ca-4bfd-5bd7-9467-95bf5981a0c0 |  | dropdown | Initial score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
text | 796124a3-1d6e-5a30-8b19-81438afd19bd |  | textbox | Potential consequence:
text | afcbd5a7-4efa-5c22-8256-280cb5066942 |  | textbox | Controls:
text | 82422819-f93b-5ced-b59e-7b2f231d074b |  | textbox | Recovery steps:
select | 7eea1a50-e092-527a-b473-644d596504e1 |  | dropdown | Residual score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
checklist-flat |  |  | checklist | Record of Inspection (ROI) |  |  |  |  | Yes | Record of Inspection (ROI) | dc358282-ed04-426e-992b-fb24d4c27d61
checkpoint-status |  |  | checkpoint | Please upload Record of Inspection here when complete (ROI)
checklist-sectioned |  |  | checklist | Isolation |  |  |  |  | Yes | Isolation | e493ed53-d67d-4d15-986d-1f0828642427
checkpoint-group |  |  | section | Isolation details
checkpoint-no-status |  |  | checkpoint | Isolation details
date | 52b93c1e-7ee6-5886-9b25-931dbce0519b |  | date | Date:
select | e5c37e39-a0b1-5c6f-9140-90472fff4e5f |  | dropdown | Type of Isolation | Electrical, Mechanical, Digital
text | 7ab7e0ef-cad2-52a0-b263-b3270217b50b |  | textbox | Duration of isolation:
label | 7e9e2703-6e56-5386-9988-6f231ba36e3c |  | note | All isolations must be done in accordance with the Entec Lockout - Tagout procedure H-P-1-037
checkpoint-group |  |  | section | Add Isolation
checkpoint-status |  |  | checkpoint | Isolation applied
text | 2730e156-d076-5461-8bea-fb6a147bf1fd |  | textbox | Isolated by:
checkpoint-status |  |  | checkpoint | Isolation checked
text | d7bed95a-c25b-5630-96a4-41579e90d6f0 |  | textbox | Checked by:
text | e4df0a55-5111-548a-8ebc-e54025b53cb2 |  | textbox | Isolation description
text | de8c3c44-7b4a-5b00-ace8-096393eb5adc |  | textbox | Personal Padlock No.
date | 9ce64bf2-b3bb-590e-b61c-13fb1bf5cfac |  | date | Date applied
checkpoint-group |  |  | section | Remove Isolation
checkpoint-status |  |  | checkpoint | Isolated equipment has been tested and is confirmed safe to liven
label | fb88f795-f850-50cf-af96-ad5597ae641a |  | note | Ensure there are no personnel working on equipment to be livened, do a full point-to-point test of the circuit to ensure the correct circuit is being re-livened.
checkpoint-status |  |  | checkpoint | Isolation removed
text | f1d2f164-f35d-5695-93b0-595ab0f24cff |  | textbox | Removed by:
checkpoint-status |  |  | checkpoint | Removal checked
text | 01610d5b-c927-566c-af43-45f17195583f |  | textbox | Checked by:
date | 2e424de8-0aac-5481-bc25-29f50f425afc |  | date | Date removed
holdpoint |  |  | signoff | Isolator and Checker signoff.
checklist-sectioned |  |  | checklist | Civil Checklist - Miscellaneous - Site Specific |  |  |  |  | Yes | Civil Checklist - Miscellaneous - Site Specific | e679832b-8c3a-40a3-92be-5f1610c96a3b
checkpoint-group |  |  | section | Corrosion Protection
checkpoint-status |  |  | checkpoint | Ensure all corrosion prone surfaces are covered
checkpoint-group |  |  | section | Sharp objects
checkpoint-status |  |  | checkpoint | Ensure no sharp edges/protrusions are present following the completion of work
checkpoint-group |  |  | section | Concrete slump test
checkpoint-status |  |  | checkpoint | Concrete slump test to be conducted prior to all concrete pour. Refer to concrete specification in drawings
holdpoint |  |  | signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist-flat |  |  | checklist | As-Built Drawings |  |  |  |  | Yes | As-Built Drawings | eb9b54e9-775c-4da4-ac85-75fd0fb76a3b
checkpoint-no-status |  |  | checkpoint | As-Built Drawings - attach scanned documents
text | 20340974-5be3-538e-b26d-0aee5ffcba10 |  | textbox | Drawing no.
checklist-sectioned |  |  | checklist | Electrical checklist - Earthing System |  |  |  |  | Yes | Electrical checklist - Earthing System | ef5f1c07-6267-4285-bde6-f6b9fccc56a9
checkpoint-group |  |  | section | Earthing System
checkpoint-status |  |  | checkpoint | Check earth electrode system is installed at the correct depth and as per the approved design
checkpoint-status |  |  | checkpoint | Earth bosses installed correctly
checkpoint-status |  |  | checkpoint | Check all earth cables/electrodes are correctly sized
checkpoint-status |  |  | checkpoint | Check that the equipment is bonded to the main earth
checkpoint-status |  |  | checkpoint | Check all the earth cable lugs and cable idents are fitted correctly
checkpoint-status |  |  | checkpoint | Check earth cable mechanical protection is installed
checkpoint-status |  |  | checkpoint | Location of earth rod as per the location drawing
checkpoint-status |  |  | checkpoint | Check any metal doors and louvres are bonded to earth correctly
checkpoint-status |  |  | checkpoint | Earth pit installed properly according to finish ground level without any damages and connection facilities are installed
checkpoint-status |  |  | checkpoint | Earth pit tagging complete and is as-per the drawings
checkpoint-status |  |  | checkpoint | If the site is a hot site (EPR > 430V), check that the HV/LB earthing systems are fully segregated (HV/LV earth link removed in the LV Pillar)
checkpoint-status |  |  | checkpoint | Check the earthing system of the EV charger is as per the approved design.
checkpoint-group |  |  | section | Earthing System Test
checkpoint-status |  |  | checkpoint | Test certificate to be provided with a detailed SOW and test results
holdpoint |  |  | signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist-sectioned |  |  | checklist | Electrical checklist - FO Install |  |  |  |  | Yes | Electrical checklist - FO Install | f4289465-288b-454e-a472-63bb428c50e3
checkpoint-group |  |  | section | FO Equipment
checkpoint-status |  |  | checkpoint | Verify the install is per the agreed design
checkpoint-status |  |  | checkpoint | Provide test results for the FO cable and associated equipment (separate test sheet)
holdpoint |  |  | signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist-flat |  |  | checklist | JHA - Job Hazard Analysis |  |  |  |  | Yes | JHA - Job Hazard Analysis | fae7be6d-4f22-44dd-a35b-7fe9029436fe
checkpoint-no-status |  |  | checkpoint | Job details
date | 31d01585-c072-5215-9bed-ae92bb0f9372 |  | date | Date:
text | a5d9d5c9-13fd-5c0f-aa2f-c567d8c65a38 |  | textbox | Permit No.
text | 8ee949fd-f3f5-57dd-aea4-86a048f3f265 |  | textbox | Job No.
text | 5a792352-a12d-507e-8592-3282ae8b2501 |  | textbox | Site
text | 54acab0c-e9c8-5fa2-a62d-531c21e6f489 |  | textbox | Activity Location
text | ef4dfc63-72f3-56a8-8ce2-6d136a331c1a |  | textbox | Asset:
text | b0971af1-0eaa-55e6-9a78-84d199a47acd |  | textbox | Work Details:
checkpoint-no-status |  |  | checkpoint | Prompts for Hazards - Mark all that apply.
button | a6d00a74-c371-507b-b752-dd24c66aea79 |  | button | Sparks/Open flame | YES,NO
button | afbd82ca-e276-511f-9545-015dcf775ed6 |  | button | Disabled safety device(s) | YES,NO
button | b1cfd986-24f2-59e3-a76c-b00f38d0c221 |  | button | Uneven surfaces | YES,NO
button | fe7e7f32-5fd3-5f6c-ae0b-1ec3c12fc38b |  | button | Fatigue, over-exertion | YES,NO
button | 1e25ec8f-c4cc-57dd-b92d-9651aa16d4b4 |  | button | Crane movements | YES,NO
button | 96eb1f82-a41c-5627-9ed1-e732138a1aa2 |  | button | Moving/Rotating parts | YES,NO
button | 82ff87a0-4957-5d51-a3d4-070bcfd620e6 |  | button | Remote area, working alone | YES,NO
button | 94c48079-377e-5ac1-8aac-d0050162b922 |  | button | Conflicting work/SIMOPS | YES,NO
button | 6df42ee6-c61f-562a-bb46-70a2506ccff2 |  | button | Electrical arc flash | YES,NO
button | 4174b113-c7f2-5d36-a0b6-ce668df1efa7 |  | button | Sharp objects/materials | YES,NO
button | 1dec00ec-f7b2-5e05-8052-7f6b2b7dde30 |  | button | Restricted/Difficult Entry/Exit | YES,NO
button | 4b090c24-bd84-535d-9afd-de337a469337 |  | button | Overhead obstacles | YES,NO
button | 0af5447c-f131-5790-949f-eb51cc8a534b |  | button | Ignition sources (other) | YES,NO
button | 60191c57-20e1-5672-a7ba-918e4697c5bc |  | button | Access/Egress | YES,NO
button | 0762dae5-c579-5798-a5b1-b30d8b600109 |  | button | Water body | YES,NO
button | f988f69b-69f8-576b-b724-a872ac414825 |  | button | Live equipment | YES,NO
button | 623597a1-6859-5419-8729-f7cc7887d5c9 |  | button | Slippery surfaces | YES,NO
button | 8be24065-4276-536c-bf86-defe9867e5f0 |  | button | Suspended loads | YES,NO
button | 1eab96b1-69b2-580e-a9d5-3a2293a0ce15 |  | button | Hazardous substances (chemicals) | YES,NO
button | 36970398-f197-5e59-bf45-ee6f8010456a |  | button | Use of non-intrinsically safe equipment | YES,NO
button | b8cf036e-4cfa-5dfd-8c76-364b6a8bff53 |  | button | Weather extremes | YES,NO
button | d07dd881-f531-5cdc-9795-cef15a4ee3b4 |  | button | Moving vehicles | YES,NO
button | e36cfdb6-8fb8-55c7-bf6d-e247cde9c9e0 |  | button | Task related noise | YES,NO
button | 45195989-77c6-5dd0-a77c-4ed60f8b8e6e |  | button | Engulfment | YES,NO
button | b0eb0c5f-78ae-5b8b-938c-8b30cc8d41eb |  | button | General waste | YES,NO
button | c1af46d3-8162-55d2-a8c6-32162392b05a |  | button | Hazardous waste | YES,NO
button | 51a48e4b-e9a5-5ca8-8946-7c717dd9d4e7 |  | button | Hazardous/toxic substance, fumes, gas | YES,NO
button | ae3d2c1c-9ae1-53d2-9386-00edc724d988 |  | button | Flammable materials - Gas, liquids, solids | YES,NO
button | 92ac86e4-255d-5d60-b3bf-00f9c27281f8 |  | button | Reduced visibility, lighting | YES,NO
button | 3dced337-61e6-5cf2-9b49-df5bcdf322a5 |  | button | Electricity | YES,NO
button | babab312-f10a-5b04-ab1b-c7c0c5f18067 |  | button | Static electricity | YES,NO
button | d8811248-aa21-567c-b1c9-d2392d8efda3 |  | button | Work at height | YES,NO
button | 8fca298e-34fc-5b0c-ad9a-ac2491e0341f |  | button | Underground services | YES,NO
button | d4f70a0c-0483-54ee-a00d-4fe62f1c134c |  | button | O2 Deficiency/Excess | YES,NO
button | 98a4ab4f-3f26-5ad7-8a87-5f197299d9ae |  | button | Temperature extremes | YES,NO
button | 4275a348-9053-55c4-b18c-c4a92e0c2e11 |  | button | Heavy objects | YES,NO
button | ed7f537c-ebb4-5a7f-948f-bd82253c693f |  | button | Radiation | YES,NO
button | f383a834-dbba-5134-a9d3-e14a261fa894 |  | button | Potential energy - Tension/Compression | YES,NO
button | 40d9c829-64f7-5157-af9b-499d0baa00c8 |  | button | Flying particles/Dust/Objects | YES,NO
button | 602446d9-e9af-5078-96ba-71d374d0497d |  | button | Vehicle entry | YES,NO
button | 2b85f6bd-a9b6-5de5-9ca1-b7629997e19b |  | button | Exposure to process temperatures. | YES,NO
checkpoint-no-status |  |  | checkpoint | Prompts for Initial Consequences - Mark all that apply
button | 67702b6b-00f6-550f-abb5-c35480ef757b |  | button | Falling/Dropped objects | YES,NO
button | 10347eab-c6bf-5dc1-9a4e-44fd0a1b685e |  | button | Fall from height | YES,NO
button | 0912b5d4-71d1-52d8-879c-263869b78c53 |  | button | Trip/Slip/Fall | YES,NO
button | 348c6df3-b325-5239-b957-dd64d746fe4e |  | button | Gas release | YES,NO
button | ce7f3b1a-3f25-5c3e-9dc9-48b835a32e02 |  | button | Pressure release | YES,NO
button | e85acabb-055b-515a-8b87-1d5ecb0d9911 |  | button | Struck by object | YES,NO
button | d3115e6d-e9e1-5e2e-acce-9764cdf65367 |  | button | Exceeding tool limits | YES,NO
button | a28a7bcf-cb45-5a04-b589-2602bbc0f103 |  | button | Overloading people | YES,NO
button | 7af057be-c307-59ce-81e7-c52c61e682ca |  | button | Unplanned shutdown | YES,NO
button | adabd743-e88e-5d5c-9808-1ff7a6e78467 |  | button | Exposure to O2 deficiency/excess | YES,NO
button | 1335b771-7d57-5e6b-837a-a78aa0951e08 |  | button | Exposure to hazardous substance | YES,NO
button | e3affc83-c1d2-54aa-ac1a-1aff4de67a88 |  | button | Entanglement | YES,NO
button | 89fbde6b-6bc2-5ad6-8a85-553f0b970dec |  | button | Flying objects | YES,NO
button | 11f07ad0-5305-5072-8c4d-b893bbadf79f |  | button | Loss of control | YES,NO
button | 7c299d3c-dc45-5c7f-b3ff-488d0fad16cf |  | button | Loss of containment | YES,NO
button | e758953e-8059-57e3-88c7-445dc2200fe7 |  | button | Excess exposure to Emissions, dust, fumes, noise, fibres, heat | YES,NO
button | 6493d3a0-5d4c-54ec-9adb-641b7776892c |  | button | Loss of structural integrity | YES,NO
button | 862e7986-ebb9-579b-b6f6-0ee0439e41bd |  | button | Equipment failure | YES,NO
button | d97ad912-3f7f-575a-9651-9c136faef4a8 |  | button | Uncontrolled ignition source | YES,NO
button | 0f40804d-e247-5f5c-8cbe-84e54be6c532 |  | button | Collision | YES,NO
button | 63e8debc-147b-5219-8b42-5b0c3197743b |  | button | Ignition/Fire | YES,NO
button | 8988194e-5661-538e-b5a9-5de4f913962a |  | button | Back strain/Injury | YES,NO
button | 1555ad16-c376-5d54-b68c-f338ea28e9c0 |  | button | Burns | YES,NO
button | 871d1406-27dd-51ae-90c6-16daef1d20d5 |  | button | Heat exhaustion | YES,NO
checkpoint-no-status |  |  | checkpoint | Initial controls - Mark all that apply.
label | 4bd5b95b-c75e-581f-9043-b75c013e8bd8 |  | note | People controls | YES,NO
button | 03adada5-8409-5d5b-a944-901f2f3ab4a2 |  | button | Safety/Fire watch person | YES,NO
button | 1cf2fb89-5f16-5be6-b4d5-81cf01f970fc |  | button | Barriers/Flagging | YES,NO
button | 94e5625b-5e70-518e-9775-16b39e0f9cc1 |  | button | Warning signs | YES,NO
label | b46373e6-b270-5396-9254-638c0d49242c |  | note | Equipment controls | YES,NO
button | d9aa39f1-1676-5f2e-8aad-1fea38ef11ba |  | button | Master tags and locks | YES,NO
button | 2b596db7-27f9-5983-988b-63ff4df17f5b |  | button | Scaffolding for access | YES,NO
button | d1ec978c-3c8f-5878-83dc-6b376737aa32 |  | button | Radio communication | YES,NO
label | 65bebf9f-7c2e-592d-a3bd-1a84ddd623cd |  | note | Environmental controls | YES,NO
button | 7749312a-340a-57e2-bbad-9c1c9fbdcd86 |  | button | Ventilation | YES,NO
button | 486ded77-f317-554f-b255-5d4dbfeb768f |  | button | Lighting | YES,NO
button | be68c886-4d7d-5d4e-ac4a-0d698e096e9b |  | button | Gas Testing | YES,NO
label | 06f9787b-0da5-5798-b2de-cd90e079faa2 |  | note | High risk controls | YES,NO
button | d2e94c48-93d9-5f70-ace2-a75af9bf38c4 |  | button | WSCS Work permit | YES,NO
button | bfafb585-0f99-59cd-866a-9ab13fda41a9 |  | button | WSCS Certificates | YES,NO
button | b6a96595-8dcd-5c09-8f41-cf0e426c0544 |  | button | Critical lift/Fall protection plan | YES,NO
button | f4d1e5b8-d526-56ee-bce3-c3305cf847fe |  | button | Specialised PPE | YES,NO
button | 7cebee55-5502-5fa1-8b18-1b2fca9a3a5a |  | button | Spill kit | YES,NO
button | 6f9b9adc-9eb1-506e-9405-6390c22a9c23 |  | button | Fire extinguisher | YES,NO
checkpoint-no-status |  |  | checkpoint | Signatures
text | ce9bc7f9-e362-5a46-8dd4-c573e12a5545 |  | textbox | Applicant name
holdpoint |  |  | signoff | Signatures