## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP-109-CIV-BRUNT-Street Lighting (Supply and Install) | itp |  |  |  | Yes | ITP-109-CIV-BRUNT-Street Lighting (Supply and Install)
section | 1. Referenced Documentation
checkpoint-no-status | 1. Referenced Documentation
label | Document Title: ITP-109-CIV-BRUNT-Street Lighting (Supply and Install)
label | ITP Description: Street Lighting (Supply and Install)
label | Document Number (in Teambinder): MRP-0000-MRPA-ALT-ITP-00XX
label | Discipline (e.g. CIV/STR/RAIL): CIV
label | Revision Number: 0
label | Revision Date: 24/11/2023
label | ITP created by: Crystal D’Mello
label | ITP approved for use by: Jon De Castro
checkpoint | 1.1 - Non Dependent
label | Reference - IFC Drawings
checkpoint | 1.2 - Non Dependent
label | Reference - AusNet Services
checkpoint | 1.3 - Non Dependent
label | Reference - VR Section 733
checkpoint | 1.4 - Non Dependent
label | Reference - AS/NZS 3000
checkpoint | 1.5 - Non Dependent
label | Reference - AS/NZS 1158.3.1
section | 2. Preliminaries - Preliminaries - Materials
checkpoint | 2.1 - Material Compliance - Obtain and review manufacturer documentations for the supply of materials.
note | Reference - IFC Drawings Section 733
note | Acceptance Criteria - Materials comply with IFC Drawings,VESI Standards.
note | All materials shall comply with the standards and specifications shown on the drawings. All structural steel, associated components and welding consumables shall be manufactured by companies that hold quality systems certification to AS/NZS ISO 9001.
textbox | Enter: Teambinder Hold Point Release Number
note | Method - Document Review
note | Frequency - Per Source
note | Category - HP
note | Responsibility - Nominated Authority
note | Verifying Documents - ConQA HP Release
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.2 - Inspection of supplied items upon delivery.
note | Reference - IFC Drawings VR Std Dwg TC1064, TC1065
note | Acceptance Criteria - Supplied items are to correct spec, class, size, undamaged and brand new.
note | Luminaires: At the time of delivery, the supplier shall provide hard copies of the following:
note | ○ Installation Instruction Manual
note | ○ Operation Instruction Manual
note | ○ Storage, handling, loading and off–loading instructions
note | ○ Test Certificates
note | ○ Warranty Information
note | Attach Delivery Dockets & Records Required
note | Method - Visual /Site Inspection & Document Review
note | Frequency - Per Delivery
note | Category - IP
note | Responsibility - SE/PE/SPE
note | Verifying Documents - This ITP Signed Off
section | 3. Preliminaries - Procedures & Documentation
checkpoint | 3.1 - ACCC Form (Australian Competition and Consumer Commission)
note | Reference - AusNet Services MRPA Quality Management Plan
note | Acceptance Criteria - Before any works commence, the accredited contractor shall obtain an "ACCC Form" from AusNet Services representative for permission to commence works.
textbox | Enter: Teambinder Hold Point Release Number
note | Method - Document Review
note | Frequency - Once prior to works commencing
note | Category - HP
note | Responsibility - Nominated Authority
note | Verifying Documents - ConQA HP Release
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.2 - Subcontractor Prequalification
note | Reference - AusNet Services MRPA Quality Management Plan
note | Acceptance Criteria - Subcontractor to be a VEDN (Victorian Electrical Distribution Networks) accredited contractor.
textbox | Enter: Teambinder Hold Point Release Number
note | Method - Document Review
note | Frequency - Once prior to works commencing
note | Category - HP
note | Responsibility - Nominated Authority
note | Verifying Documents - ConQA HP Release
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3 - VESI (Victorian Electricity Supply Industry) Auditor
note | Reference - AusNet Services MRPA Quality Management Plan
note | Acceptance Criteria - VEDN approved civil auditor. (VESI Auditor Register)
textbox | Enter: Teambinder Hold Point Release Number
note | Method - Document Review
note | Frequency - Once prior to works commencing
note | Category - HP
note | Responsibility - Nominated Authority
note | Verifying Documents - ConQA HP Release
holdpoint | AUTHORITY HOLDPOINT
section | 4. Pre-installation Activities
checkpoint | 4.1 - IFC Drawings
note | Reference - MRPA Quality Management Plan
note | Acceptance Criteria - Check the revision of the IFC drawings are current as per the drawing register (on Teambinder)
note | Method - Document Review
note | Frequency - Prior to starting Works and at regular intervals
note | Category - HP*
note | Responsibility - SE/PE/SPE
note | Verifying Documents - This ITP Signed Off
checkpoint | 4.2 - Survey set out
note | Reference - IFC Drawings AusNet Services Technical Specifications
note | Acceptance Criteria - Set-out survey carried out by a surveyor and within the tolerances as per IFC Drawings and AusNet drawings/specs.
note | Method - Visual Survey
note | Frequency - Each Element
note | Category - IP
note | Responsibility - SE/PE/SPE
note | Verifying Documents - This ITP Signed Off
section | 5. Installation Activities
checkpoint | 5.1 - Pit and Conduit Installation
note | Reference - IFC Drawings
note | Acceptance Criteria - Conduits and pits to be installed as per IFC Drawings
note | Attach: Subcontractor Installation Checklist
note | Method - Document Review Visual
note | Frequency - Prior to commencement
note | Category - WP
note | Responsibility - SE/PE
note | Verifying Documents - This ITP Signed Off
checkpoint | 5.2 - Conduit and Cable Detailing
note | Reference - AusNet Services Technical Specification
note | Acceptance Criteria - Trench inspection detailing all conduits and cables being installed by a AusNet services approved detailer.
note | Attach: Verification Document (As-Builts)
note | Method - Site Inspection
note | Frequency - Upon completion of each section
note | Category - IP
note | Responsibility - SE/PE/SPE Services Engineer
note | Verifying Documents - This ITP Signed Off
checkpoint | 5.3 - Prepare the plinth foundation (Excavation & levels)
note | Reference - IFC Drawings
note | Acceptance Criteria - Check levels conform to relevant drawing depending on type of pole to be installed.
note | Method - Visual Survey
note | Frequency - Per Lot
note | Category - IP
note | Responsibility - SE/PE/SPE
note | Verifying Documents - This ITP Signed Off
checkpoint | 5.4 - Installation of Light poles
note | Reference - IFC Drawings
note | Acceptance Criteria - Light Poles to be installed as per IFC drawings in accordance with VESI requirements.
note | Method - Visual /Site Inspection & Document Review
note | Frequency - Per Lot
note | Category - IP
note | Responsibility - SE/PE/SPE
note | Verifying Documents - This ITP Signed Off
checkpoint | 5.5 - Asset Labelling
note | Reference - IFC Drawings
note | Acceptance Criteria - Pole Labelling to be as per IFC Drawings.
note | Method - Visual Inspection
note | Frequency - Per Lot
note | Category - IP
note | Responsibility - SE/PE/SPE
note | Verifying Documents - This ITP Signed Off
checkpoint | 5.6 - Commissioning & Testing (Civil Audit)
note | Reference - AusNet Services Technical Specification
note | Acceptance Criteria - Upon completion of all trenching and conduit install, a Civil audit by a VEDN approved Civil auditor will be completed and approved before procceding.
note | Method - Commissioning & testing
note | Frequency - Upon completion of each section
note | Category - IP
note | Responsibility - SE/PE/SPE Services Engineer
note | Verifying Documents - This ITP Signed Off
checkpoint | 5.7 - Commissioning & Testing (Trench Inspection)
note | Reference - AusNet Services Technical Specification
note | Acceptance Criteria - Trench inspection detailing all conduits and cables being installed by a AusNet services approved detailer
note | Verification document: As-Builts
note | Method - Commissioning & testing
note | Frequency - Upon completion of each section
note | Category - IP
note | Responsibility - SE/PE/SPE Services Engineer
note | Verifying Documents - This ITP Signed Off
checkpoint | 5.8 - Commissioning & Testing (Pre-commissioning)
note | Reference - AusNet Services Technical Specification
note | Acceptance Criteria - Passing of the pre-commissioning audit with all non-conformances rectified.
note | Method - Commissioning & testing
note | Frequency - Upon completion of each section
note | Category - IP
note | Responsibility - SE/PE/SPE Services Engineer
note | Verifying Documents - This ITP Signed Off
checkpoint | 5.9 - Commissioning & Testing (Final Audit)
note | Reference - AusNet Services Technical Specification
note | Acceptance Criteria - Passing of the final audit will be completed by AusNet Services to inspect the completed works with all non-conformances rectified.
note | Method - Commissioning & testing
note | Frequency - Upon completion of each section
note | Category - IP
note | Responsibility - SE/PE/SPE Services Engineer
note | Verifying Documents - This ITP Signed Off
checkpoint | 5.10 - Testing and Certificate of Electrical Safety
note | Reference - AusNet Services Technical Specification IFC Drawings
note | Acceptance Criteria - Prior to final acceptance, the contractor shall test all distribution cabinets, circuits, switches, PE Cells, luminaires, and all other electrical and electronic components for correct installation and operation
note | Attach Documentation: Certificate of Electrical Safety for electrical installation
note | Method - Document Review
note | Frequency - Upon completion/ Work area
note | Category - IP
note | Responsibility - SE/PE/SPE Services Engineer
note | Verifying Documents - This ITP Signed Off
checkpoint | 5.11 - PC Cert of AusNet Agreement
note | Reference - AusNet Services Technical Specification IFC Drawings
note | Acceptance Criteria - To be accepted and signed-off by MRPA and AusNet
note | Method - Document Review
note | Frequency - Upon completion/ Work area
note | Category - IP
note | Responsibility - SE/PE/SPE Services Engineer
note | Verifying Documents - This ITP Signed Off
section | 6. Post-installation Activities
checkpoint | 6.1 - Verification of Subcontractor conformance records / signed ITPs including any relevant verification sheets.
note | Reference - IFC Drawings Notes
note | Acceptance Criteria - Check conformance report against project conformance criteria.
note | Attach Verification Docs: QA Records, Signed ITP including any verification documents, Commissioning & Testing Certificates.
note | Method - Visual /Site Inspection & Document Review
note | Frequency - Per Lot
note | Category - IP
note | Responsibility - SE/PE/SPE
note | Verifying Documents - This ITP Signed Off
checkpoint | 6.2 - As-Built Drawings
note | Reference - IFC Drawings Notes
note | Acceptance Criteria - As built drawings for the metered lighting installations to be provided to the satisfaction of MRPA & Cardinia Shire Council.
note | Attach: As Constructured Plans / As-Builts
note | Method - Document Review
note | Frequency - Upon completion/ Work area
note | Category - IP
note | Responsibility - SE/PE/SPE
note | Verifying Documents - This ITP Signed Off
checkpoint | 6.3 - Non-conformance Report (NCR) Closure
note | Reference - MRPA Quality Management Plan
note | Acceptance Criteria - Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed in TeamBinder.
note | Method - Document Review
note | Frequency - Once, prior to closure of this lot / element / Work area
note | Category - WP
note | Responsibility - SE/PE/SPE
note | Verifying Documents - This ITP Signed Off
checkpoint | Final Inspection
note | On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
textbox | Name:
textbox | Position:
date | Date Completed:
signoff | Sign ITP