## QA Folder Structure
QA Folder Structure |  |  |  | Enviro Systems | Checklists
BASEMENT AND PODIUM | [5 empty] | Enviro 700X - Balconies
| Bathroom |  |  |  |  | Enviro 700X - Balcony Set Downs & Window Reveals
|  | Retail Bathroom |  | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas | Enviro 200P Ultra - Internal Wet Areas
|  | End of Trip Bathroom |  | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas | Enviro 700X + 250NS
|  | Cleaners Room |  | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
Wet Plant Rooms
|  | Basement B3 Recycled Water Tank Room |  | Enviro Epoxy B-LV + Enviro 700X + Aggregate
|  | B2 Sprinkler Tank Room (Domestic Pump Room) |  | Enviro Epoxy B-LV + Enviro 700X + Aggregate
|  | Basement B1 Fire Booster Pump Room |  | Enviro Epoxy B-LV + Enviro 700X + Aggregate
|  | Level 1 Fire Booster |  | Enviro Epoxy B-LV + Enviro 700X + Aggregate
|  | Basement B1 Retail Condenser Water Pump Room |  | Enviro Epoxy B-LV + Enviro 700X + Aggregate
|  | Basement B1 Hydraulic Plant Room |  | Enviro Epoxy B-LV + Enviro 700X + Aggregate
|  | Level 1 Amenities Hydraulic Plant |  | Enviro Epoxy B-LV + Enviro 700X + Aggregate
|  | Basement B1 Hot Water Room |  | Enviro Epoxy B-LV + Enviro 700X + Aggregate
|  | Level 1 Main Switch Room |  | Enviro Epoxy B-LV + Enviro 700X + Aggregate
Tanks
|  | Basement 1 OSD 2 - Base |  | Enviro HP1200 (Incl working in confined space)
|  | Basement OSD 1 - Base |  | Enviro HP1200 (Incl working in confined space)
|  | Basement 2 - OSD Retention Tank / Sprinkler Tank - Base |  | Enviro HP1200 (Incl working in confined space)
Epoxy flooring rooms
|  | B1 waste and garabge rooms |  | Enviro Epoxy RC
Level 1 Waste & Garbage Rooms
|  | B1 Grease arrestor rooms |  | Enviro Epoxy RC
|  | Car Wash Bay |  | Enviro Epoxy RC
|  | dogwash |  | Enviro Epoxy RC
Paved Paths Movement Joints
|  | level 1 |  | Enviro Elastoflex
|  | level 2 |  | Enviro Elastoflex
| Level 1 Podium Paved Paths |  |  | Enviro Epoxy B-LV + Enviro 700X
| Level 2 Podium Paved Paths |  |  | Enviro Epoxy B-LV + Enviro 700X
| Level 1 Planter boxes |  |  | Enviro Epoxy B-LV + Enviro 700X
| Level 2 Planter boxes |  |  | Enviro Epoxy B-LV + Enviro 700X
| Capping Beam Joint Treatment |  |  | Enviro Flex FC (up to 20mm joint) + Enviro 700X (ne 300mm coverage) incl coreflute
Building A
Slab edges
Cantilever Slab Under GRC Planters
|  |  | level2 | Enviro 700X
|  |  | level3 | Enviro 700X
|  |  | level4 | Enviro 700X
|  |  | level5 | Enviro 700X
|  |  | level6 | Enviro 700X
|  |  | level7 | Enviro 700X
|  |  | level8 | Enviro 700X
|  |  | level9 | Enviro 700X
|  |  | level10 | Enviro 700X
Slab Edge - Roof under Pebbles
|  |  | level 9 | Enviro 700X
|  |  | level 11 | Enviro 700X
Slab Edge - Roof under GRC Planters
|  |  | level 11 | Enviro 700X
Façade Bandage for window wall install
|  |  | level 2 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 3 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 4 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 5 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 6 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 7 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 8 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 9 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 10 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 11 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 12 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 13 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 14 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 15 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 16 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 17 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 18 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 19 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 20 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 21 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 22 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 23 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 24 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
Façade Cladding ( precast cladding )
|  |  | lvl 02 | Enviro Prime WB + EnviroClad
|  |  | lvl 03 | Enviro Prime WB + EnviroClad
|  |  | lvl 04 | Enviro Prime WB + EnviroClad
|  |  | lvl 05 | Enviro Prime WB + EnviroClad
|  |  | lvl 06 | Enviro Prime WB + EnviroClad
|  |  | lvl 07 | Enviro Prime WB + EnviroClad
|  |  | lvl 08 | Enviro Prime WB + EnviroClad
|  |  | lvl 09 | Enviro Prime WB + EnviroClad
|  |  | lvl 10 | Enviro Prime WB + EnviroClad
|  |  | Elevation metal clad south | Enviro Prime WB + EnviroClad
|  |  | Elevation metal clad east | Enviro Prime WB + EnviroClad
|  |  | Elevation metal clad north | Enviro Prime WB + EnviroClad
Apartment balconies
Stage 1 - setdowns
|  |  | level 02 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 03 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 04 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 05 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 06 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 07 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 08 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 09 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 10 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 11 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 12 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 13 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 14 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 15 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 16 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 17 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 18 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 19 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 20 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 21 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 22 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 23 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
Stage 2 - Complete balcony
|  |  | level 02 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 03 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 04 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 05 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 06 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 07 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 08 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 09 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 10 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 11 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 12 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 13 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 14 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 15 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 16 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 17 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 18 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 19 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 20 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 21 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 22 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 23 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
In situ bathrooms/ laundries
|  |  | level 02 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 03 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 04 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 05 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 06 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 07 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 08 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 09 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 10 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 11 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 12 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 13 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 14 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 15 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 16 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 17 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 18 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 19 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 20 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 21 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 22 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 23 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
Water Meter Cupboards
|  |  | level 02 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 03 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 04 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 05 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 06 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 07 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 08 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 09 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 10 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 11 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 12 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 13 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 14 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 15 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 16 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 17 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 18 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 19 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 20 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 21 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 22 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 23 | Enviro Epoxy B-LV Primer + Enviro 700X
Roof
Cantilever Slab Under GRC planters
|  | ` | level 02 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 03 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 04 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 05 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 06 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 07 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 08 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 09 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 10 | Enviro Epoxy B-LV + Enviro 700X
Roof Slab under Pebbles
|  |  | level 09 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 11 | Enviro Epoxy B-LV + Enviro 700X
|  | slab under GRC Planters | level 11 | Enviro Epoxy B-LV + Enviro 700X
|  | Roof Top- Roof Slab / Lift and Stair Lid | level 25 | Enviro 700X + 800TC
Plant room
External plant room
|  |  | level 23 | Enviro 700X + 800TC
Plant level
|  |  | level 24 | Enviro 700X + 800TC
Building B
Slab Edges
Slab Edge - BAL-01
|  |  | level 2 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 3 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 4 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 5 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 6 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 7 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 8 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 9 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 10 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 11 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 12 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
Slab Edge - BAL-02
|  |  | level 02 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 03 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 04 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 05 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 06 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 07 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 08 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 09 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 10 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 11 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 12 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
Slab Edge - BAL-03
|  |  | level 02 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 03 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 04 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 05 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 06 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 07 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 08 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 09 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 10 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
Roof Edge Precast
|  |  | level 11 | Enviro 700X
Hob to vertical screen
|  |  | Level 11 | Enviro 700X + 800TC
|  |  | Level 12 | Enviro 700X + 800TC
Roof Edge Precast Upstand
|  |  | Level 13 | Enviro Epoxy B-LV + Enviro 700X
Façade Bandage for window wall Install
|  |  | level 02 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 03 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 04 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 05 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 06 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 07 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 08 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 09 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 10 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 11 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 12 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
Apartment Balconies
Stage 1 Setdowns
|  |  | level 02 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 03 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 04 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 05 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 06 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 07 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 08 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 09 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 10 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 11 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 12 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
Stage 2 - Complete balcony
|  |  | level 02 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 03 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 04 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 05 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 06 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 07 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 08 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 09 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 10 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 11 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 12 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
Bathrooms and Laundries
|  |  | level 06 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 07 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 08 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 09 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 10 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 11 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 12 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
Water meter cupboards
|  |  | level 02 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 03 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 04 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 05 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 06 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 07 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 08 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 09 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 10 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 11 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 12 | Enviro Epoxy B-LV Primer + Enviro 700X
Roof
Non- trafficable roof/slab
|  |  | level 02 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 05 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 11 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 13 | Enviro Epoxy B-LV Primer + Enviro 700X
Membrane to service Drain Access
|  |  | level 11 | Enviro Epoxy B-LV Primer + Enviro 700X
PlantRoom
External Plant Room
|  |  | level 13 | Enviro 700X + 800TC
Planters
|  |  | level 02 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 05 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 11 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 13 | Enviro Epoxy B-LV + Enviro 700X
Precast Joints- Negative membrane wokers
|  |  | level 01 | Enviro Flex FC + 700X ne 200mm bandage
|  |  | level 02 | Enviro Flex FC + 700X ne 200mm bandage
|  |  | level 03 | Enviro Flex FC + 700X ne 200mm bandage
|  |  | level 04 | Enviro Flex FC + 700X ne 200mm bandage
|  |  | level 05 | Enviro Flex FC + 700X ne 200mm bandage
|  |  | level 06 | Enviro Flex FC + 700X ne 200mm bandage
|  |  | level 07 | Enviro Flex FC + 700X ne 200mm bandage
|  |  | level 08 | Enviro Flex FC + 700X ne 200mm bandage
|  |  | level 09 | Enviro Flex FC + 700X ne 200mm bandage
|  |  | level 10 | Enviro Flex FC + 700X ne 200mm bandage
|  |  | level 11 | Enviro Flex FC + 700X ne 200mm bandage
|  |  | level 12 | Enviro Flex FC + 700X ne 200mm bandage
Building C
Slab edges
|  |  | level 03 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 04 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 05 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 06 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 07 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 08 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 09 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 10 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 11 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 12 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 13 | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
Slab under GRC Planter
|  |  | level 2 | Enviro Prime WB + EnviroClad
|  |  | level 3 | Enviro Prime WB + EnviroClad
|  |  | level 4 | Enviro Prime WB + EnviroClad
|  |  | level 5 | Enviro Prime WB + EnviroClad
|  |  | level 6 | Enviro Prime WB + EnviroClad
|  |  | level 7 | Enviro Prime WB + EnviroClad
|  |  | level 8 | Enviro Prime WB + EnviroClad
|  |  | level 9 | Enviro Prime WB + EnviroClad
|  |  | level 10 | Enviro Prime WB + EnviroClad
|  |  | level 11 | Enviro Prime WB + EnviroClad
Window seal
|  |  | level 02 | Enviro Epoxy B-LV Primer + Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 03 | Enviro Epoxy B-LV Primer + Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 04 | Enviro Epoxy B-LV Primer + Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 05 | Enviro Epoxy B-LV Primer + Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 06 | Enviro Epoxy B-LV Primer + Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 07 | Enviro Epoxy B-LV Primer + Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 08 | Enviro Epoxy B-LV Primer + Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 09 | Enviro Epoxy B-LV Primer + Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 10 | Enviro Epoxy B-LV Primer + Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 11 | Enviro Epoxy B-LV Primer + Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 12 | Enviro Epoxy B-LV Primer + Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
apartment balconies
Stage 1 - setdowns
|  |  | level 02 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 03 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 04 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 05 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 06 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 07 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 08 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 09 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 10 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 11 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 12 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  | Stage 2 - slab | level 02 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 03 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 04 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 05 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 06 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 07 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 08 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 09 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 10 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 11 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 12 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
Apartment Bathrooms / laundries
|  |  | level 02 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 03 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 04 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 05 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 06 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 07 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 08 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 09 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 10 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 11 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | level 12 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
Water Meter cupboards
|  |  | level 2 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 3 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 4 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 5 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 6 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 7 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 8 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 9 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 10 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 11 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 12 | Enviro Epoxy B-LV Primer + Enviro 700X
Roof
WPS-501 - Membrane to non-trafficable roof/slab
|  |  | level 03 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 05 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | level 13 | Enviro Epoxy B-LV Primer + Enviro 700X
|  |  | Roof | Enviro Epoxy B-LV Primer + Enviro 700X
Slab under GRC Planter
|  |  | level 02 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 03 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 04 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 05 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 06 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 07 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 08 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 09 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 10 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 11 | Enviro Epoxy B-LV + Enviro 700X
Plantroom
level 13
Enviro 700X + 800TC
Planters/ Green Walls
|  |  | level 02 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 05 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 013 | Enviro Epoxy B-LV + Enviro 700X
Building D
| Slab Edge |  |  | Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
| Façade and façade cladding |  |  | Enviro Epoxy B-LV Primer + Enviro 700X | Enviro 700X - Balcony Set Downs & Window Reveals
Balconies
part 1- setdowns
|  |  | level 2 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | level 3 | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
|  |  | roof terrace | Enviro Flex FC + 700X | Enviro 700X - Balcony Set Downs & Window Reveals
part 2 - balcony slab
|  |  | level 2 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | level 3 | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
|  |  | roof terrace | Enviro Epoxy B-LV + Enviro 700X | Enviro 700X - Balconies
Bathrooms/laundries
|  |  | Level 2 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | Level 3 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | Level 4 | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
|  |  | Roof terrace | Enviro Prime WB + Enviro 200P Ultra | Enviro 200P Ultra - Internal Wet Areas
Roof
|  |  | level 2 | Enviro Epoxy B-LV + Enviro 700X
|  |  | level 3 | Enviro Epoxy B-LV + Enviro 700X
|  |  | roof Terrace | Enviro Epoxy B-LV + Enviro 700X
Planters
|  |  | level 2 | Enviro Epoxy B-LV + Enviro 700X
|  |  | roof terrace | Enviro Epoxy B-LV + Enviro 700X
| Secondary waterproofing above screed to podium paved areas |  |  | Enviroshield

## ITPs Checklists
type | name | values
checklist-flat | Enviro 700X - Balconies
Label | Specification / Standard Manufacturer's Technical Data Sheet / AS4654.1 - 2012
checkpoint | Batch Number
Label | Record batch number
checkpoint | Substrate crack and falls inspection
Label | Fill cracks less than 1.6mm with filler compatible (Enviro-Flex Pro) with the membrane system.Live cracks to be reffered to engineers for treatment methodolgy. Builder to approve falls on substrate(Min 1:100) prior to application of membrane.
holdpoint | Hold Point (Mandatory) - work not to proceed without approval
checkpoint | Moisture Content
Label | Note. min. 3 tests per 15m2 Enviro Epoxy B-LV up to 6.9% Enviro Prime P2 up to 5%
holdpoint | Hold Point (Mandatory) - work not to proceed without approval
checkpoint | Ambient temperature and RH
Label | Reading twice a day- every 4 hours Mirvac to confirm temperature between the ranges of 5-35 degrees celcius prior to application of membrane. RH must be greater than 50%
holdpoint | Hold Point (Mandatory) - work not to proceed without approval
checkpoint | Mechanical Mixing
Label | If applying Enviro Epoxy B-LV: Mix Part B, liquid hardener, to the Enviro Epoxy B-LV Part A base. Thoroughly mix with a mechanical mixer at low speed for not less than 5 minutes and until uniform.
checkpoint | Applying primer
Label | Using a brush or roller apply the chosen primer. Allow to cure prior to over coating with sealants and/or membrane coats."Primer should be dry to touch and not be tacky when applying pressure to it. Enviro-Epoxy B-LV will take around 16-48 hrs @ 25 degrees C to dry (but could be longer depending on ambient temp and RH)
checkpoint | Seal/apply bondbreaker at junctions hob/floor
Label | Apply Enviro Flex Pro to form smooth 15mm flexible cove to all internal corners, penetrations and joints.
checkpoint | Application of Enviro-700X
Label | Mix Bucket at low speed( 400RPM) unitl thouroghly mixed. Apply two coats of 700X. Where membrane is terminated on a building element: Ensure that the termination height of the membrane above the FFL and/or invert level of a correctly placed overflow/spitter satisfies the Façade engineer's advice
checkpoint | QA Testing
Label | Inspect after installation of reinforcement/finishes to check for any damage to waterproofing and rectify as required. Thickness testing of application to the recommended DFT of 1.5mm to manufacturers instructions. 5 tests per 15m2 Holiday/ spark testing of area.
holdpoint | Hold Point (Mandatory) - work not to proceed without approval
checkpoint | Protection of membrane edge
Label | Ensure vertical terminations of membranes on a building element are provided with a pressure seal, reglet or by being overcoated with a waterproof or water resistant material to protect the membrane edge. Ensure vertical membrane termination junctions are caulked with Enviro FC pro.
holdpoint | Builder Sign Off
checklist-flat | Enviro 700X - Balcony Set Downs & Window Reveals
Label | Specification / Standard Manufacturer's Technical Data Sheet / AS4654.1 - 2012
checkpoint | Batch Number
Label | Record batch number
checkpoint | Substrate crack and falls inspection
Label | Obtain clearance for work to commence. Clean substrate so that is free of mould, paint, sealers, coatings, curing agents, loose particles, and other contamination or foreign matter that may interfere with the adhesion. for non metal surfaces: ICRI CSP-4 to CSP-6 for metal surfaces: ICRI CSP-1 to CSP-2.
checkpoint | Moisture Content
Label | Note. min. 3 tests per 15m2 Enviro Epoxy B-LV up to 6.9% Enviro Prime P2 up to 5% Enviro Prime 789 up to 5%
holdpoint | Hold Point (Mandatory) - work not to proceed without approval
checkpoint | Ambient temperature and RH
Label | Reading twice a day- every 4 hours Mirvac to confirm temperature between the ranges of 5-35 degrees celcius prior to application of membrane. RH must be greater than 50%
holdpoint | Hold Point (Mandatory) - work not to proceed without approval
checkpoint | Mechanical Mixing
Label | If applying Enviro Epoxy B-LV: Mix Part B, liquid hardener, to the Enviro Epoxy B-LV Part A base. Thoroughly mix with a mechanical mixer at low speed for not less than 5 minutes and until uniform.
checkpoint | Applying primer
Label | Using a brush or roller apply the chosen primer. Allow to cure prior to over coating with sealants and/or membrane coats."Primer should be dry to touch and not be tacky when applying pressure to it. Enviro-Epoxy B-LV will take around 16-48 hrs @ 25 degrees C to dry (but could be longer depending on ambient temp and RH)
checkpoint | Application of Enviro-700X
Label | Mix Bucket at low speed( 400RPM) unitl thouroghly mixed. Apply two coats of 700X. Where membrane is terminated on a building element: Ensure that the termination height of the membrane above the FFL and/or invert level of a correctly placed overflow/spitter satisfies the Façade engineer's advice
checkpoint | Protection of membrane edge
Label | Ensure vertical terminations of membranes on a building element are provided with a pressure seal, reglet or by being overcoated with a waterproof or water resistant material to protect the membrane edge. Ensure vertical membrane termination junctions are caulked with Enviro FC pro.
checkpoint | QA Testing
Label | Inspect after installation of reinforcement/finishes to check for any damage to waterproofing and rectify as required. Thickness testing of application to the recommended DFT of 1.5mm to manufacturers instructions. 5 tests per 15m2 Holiday/ spark testing of area.
holdpoint | Completion of Work Element
checklist-flat | Enviro 200P Ultra - Internal Wet Areas
Label | Specification / Standard Manufacturer's Technical Data Sheet / AS4654.1 - 2012
checkpoint | Batch Number
Label | Record batch number
checkpoint | Substrate crack and falls inspection
Label | Obtain clearance for work to commence. Clean substrate so that is free of mould, paint, sealers, coatings, curing agents, loose particles, and other contamination or foreign matter that may interfere with the adhesion. for non metal surfaces: ICRI CSP-4 to CSP-6 for metal surfaces: ICRI CSP-1 to CSP-2. Ensure all fixings and joints have been set and junction between wall and floor does not exceed more than 10mm. Ensure Puddle flanges reccessed in concrete.
checkpoint | Substrate crack and falls inspection
Label | Fill cracks less than 1.6mm with filler compatible (Enviro-Flex Pro) with the membrane system.Live cracks to be reffered to engineers for treatment methodolgy. Builder to approve falls on substrate(Min 1:100 outside shower and 1:80 in showers ) prior to application of membrane.
checkpoint | Moisture Content
Label | Note. min. 3 tests per bathroom Enviro Epoxy B-LV up to 6.9% Enviro Prime WB up to 6.9%
holdpoint | Hold Point (Mandatory) - work not to proceed without approval
checkpoint | Ambient temperature and RH
Label | Reading twice a day- every 4 hours Mirvac to confirm temperature between the ranges of 5-35 degrees celcius prior to application of membrane. RH must be greater than 50%
holdpoint | Hold Point (Mandatory) - work not to proceed without approval
checkpoint | Mechanical Mixing
Label | If applying Enviro Epoxy B-LV, thoroughly mix with a mechanical mixer at low speed for not less than 5 minutes and until uniform. If applying Enviro Prime WB, mix at low speed (400RPM) until thouroghly mixed.
checkpoint | Applying primer
Label | Using a brush or roller apply the chosen primer. Allow to cure prior to over coating with sealants and/or membrane coats."Primer should be dry to touch and not be tacky when applying pressure to it. Application range: 5-40 degrees celcius.
Seal/apply bondbreaker at junctions hob/floor | Apply Enviro Flex Pro to form smooth 12mm flexible cove to all internal corners, penetrations and joints.
Application of 200P ultra | Mix Bucket at low speed( 400RPM) unitl thouroghly mixed. Apply two coats of 200p Ultra to wet area in accordance with Australian Standards Application range 5-40*C
QA Testing | Inspect after installation of reinforcement/finishes to check for any damage to waterproofing and rectify as required. Thickness testing of application to the recommended DFT to manufacturers instructions. 0.6mm walls 1.0mm floors 3 tests on floor/ 3 tests on walls. 24 hour Flood testing.
holdpoint | Completion of Work Element
checklist-flat | Enviro 700X + 250NS
Label | Specification / Standard Manufacturer's Technical Data Sheet / AS4654.1 - 2012
checkpoint | Batch Number
Label | Record batch number
checkpoint | Substrate crack and falls inspection
Label | Obtain clearance for work to commence. Clean substrate so that is free of mould, paint, sealers, coatings, curing agents, loose particles, and other contamination or foreign matter that may interfere with the adhesion. for non metal surfaces: ICRI CSP-4 to CSP-6 for metal surfaces: ICRI CSP-1 to CSP-2.
checkpoint | Substrate crack and falls inspection
Label | Fill cracks less than 1.6mm with filler compatible (Enviro-Flex Pro) with the membrane system.Live cracks to be reffered to engineers for treatment methodolgy. Builder to approve falls on substrate(Min 1:100) prior to application of membrane.
checkpoint | Moisture Content
Label | Note. min. 3 tests per 15m2 Enviro Epoxy B-LV up to 6.9% Enviro Prime P2 up to 5%
holdpoint | Hold Point (Mandatory) - work not to proceed without approval
checkpoint | Ambient temperature and RH
Label | Reading twice a day- every 4 hours Mirvac to confirm temperature between the ranges of 5-35 degrees celcius prior to application of membrane. RH must be greater than 50%
holdpoint | Hold Point (Mandatory) - work not to proceed without approval
checkpoint | Mechanical Mixing
Label | If applying Enviro Epoxy B-LV: Mix Part B, liquid hardener, to the Enviro Epoxy B-LV Part A base. Thoroughly mix with a mechanical mixer at low speed for not less than 5 minutes and until uniform.
checkpoint | Applying primer
Label | Using a brush or roller apply the chosen primer. Allow to cure prior to over coating with sealants and/or membrane coats."Primer should be dry to touch and not be tacky when applying pressure to it. Enviro-Epoxy B-LV will take around 16-48 hrs @ 25 degrees C to dry (but could be longer depending on ambient temp and RH)
checkpoint | Seal/apply bondbreaker at junctions hob/floor
Label | Apply Enviro Flex Pro to form smooth 15mm flexible cove to all internal corners, penetrations and joints.
checkpoint | Application of Enviro-700X
Label | Mix Bucket at low speed( 400RPM) unitl thouroghly mixed. Apply two coats of 700X. Where membrane is terminated on a building element: Ensure that the termination height of the membrane above the FFL and/or invert level of a correctly placed overflow/spitter satisfies the Façade engineer's advice
checkpoint | QA Testing
Label | Inspect after installation of reinforcement/finishes to check for any damage to waterproofing and rectify as required. Thickness testing of application to the recommended DFT of 1.5mm to manufacturers instructions. 5 tests per 15m2 Holiday/ spark testing of area.
holdpoint | Hold Point (Mandatory) - work not to proceed without approval
checkpoint | Application of 250N-S Top Coat
Label | Mix Bucket at low speed( 400RPM) unitl thouroghly mixed. Apply 1 coats of 250N-S Where membrane is terminated on a building element: Ensure that the termination height of the membrane above the FFL and/or invert level of a correctly placed overflow/spitter satisfies the Façade engineer's advice
checkpoint | Protection of membrane edge
Label | Ensure vertical terminations of membranes on a building element are provided with a pressure seal, reglet or by being overcoated with a waterproof or water resistant material to protect the membrane edge. Ensure vertical membrane termination junctions are caulked with Enviro FC pro.
holdpoint | Completion of Work Element
checklist-flat | Enviro Clad |  | `
Label | Specification / Standard Manufacturer's Technical Data Sheet / AS4654.1 - 2012
checkpoint | Batch Number
Label | Record batch number
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections.
label | Attach Photo
checkpoint | Primer Application - Pending Substrate Condition, Apply Enviro Prime WB using a brush or roller
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Membrane Application (1st coat) - Mix and Apply Enviro Clad as a first coat to the thicknesses prescribed by the specifications
checkpoint | Membrane Application (2nd coat) - Mix and Apply Enviro Clad as a second coat to the thicknesses prescribed by the specifications
checkpoint | Curing - Allow to cure in accordance with Manufacturers Specifications
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
checklist-flat | Enviro Hydrostatic 1
Label | Specification / Standard Manufacturer's Technical Data Sheet / AS4654.1 - 2012
checkpoint | Batch Number
Label | Record batch number
checkpoint | Prepare surface to accept primer using scraper (and/or light grind) and vacuum/sweep residual debris. Remove all concrete/mortar projections.
label | Attach Photo
checkpoint | Caulking - Apply Enviro Flex FC / PRO to the junction between floor slab and walls
label | Attach Photo
checkpoint | Primer application - Lightly Spray areas with water to receive Hydrostatic 1
label | Attach Photo
checkpoint | Membrane Application (1st coat) - Mix Enviro Hydrostatic 1 thoroughly using a mechanical mixer. Apply first coat of Enviro Hydrostatic 1 by brush or roller Use Enviro Joint Band in floor-wall junctions and general movement joints
checkpoint | Membrane Application (2nd coat) - Mix Enviro Hydrostatic 1 thoroughly using a mechanical mixer. Apply second coat of Enviro Hydrostatic 1 by brush or roller
checkpoint | Curing - Allow to cure in accordance with Manufacturers Specifications
checkpoint | Final Inspection and Sign-off. Visually inspect and ensure adequately cured - DO NOT PASS UNTIL HOLDPOINT COMPLETE BELOW
holdpoint | HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF

## Sheet1 (hidden)
Enviro 700X application
Batch Number
Record batch number of product(s)
Yes | No | N/A
attach photo
Substrate Preparation
Obtain clearance for work to commence.
Yes | No | N/A
Clean substrate so that is free of mould, paint, sealers, coatings, curing agents, loose particles, and other contamination or foreign matter that may interfere with the adhesion. Must achieve CSP-1 to CSP-2
Yes | No | N/A
Attach Photos reference of swatch next to substrate
Cracks in substrate
Fill all cracks in substrates wider than 1.0 mm (but not more than 1.6mm) with filler compatible (Enviro-Flex Pro) with the membrane system.
Live cracks or greater than 1.6mm to be referred to engineers for treatment methodology
Yes | No | N/A
Attach photos
Moisture content of susbtrate
3 tests per 15m2 Must be less than 4% and AS4654 (1 and 2). If greater refer to Mirvac for special instruction for change of primer to Hydro-epoxy
Yes | No | N/A
Attach photos of moisture readings( mark area and full shot of area
HOLD POINT - CLICK HERE TO REQUEST BUILDER SIGN OFF
Ambient temperature and RH (Reading twice a day - every 4 hours)
Mirvac to record temperature and provide reading. Temp must be applicable to membrane application
Yes | No | N/A
Notes of temperature day and time
Mirvac to confirm temperature suitable for application. Sign off
Application of Primer
If using epoxy, Enviro Epoxy B-LV should be thoroughly mixed with a mechanical mixer at low speed for not less than 5 minutes and until uniform.
yes | No | N/A
If using Enviro 789- Mix at low speed (400RPM) until thouroghly mixed
Yes | No | N/A
Using a brush and roller, apply primer.Primer should be dry to touch and not be tacky when applying pressure to it. Enviro-Prime 789 will take around 1-5 hrs @ 20 degrees C (but could be longer depending on ambient temp and RH). Enviro-Epoxy B-LV will take around 16-48 hrs @ 25 degrees C (but could be longer depending on ambient temp and RH)
Yes | No | N/A
Attach Photos
Application of sealant to Australian Standard
Apply Enviro Flex Pro to form smooth 12mm flexible cove to all internal corners, penetrations and joints.
Yes | No | N/A
Attach Photos
first coat Application of Enviro-700X
Mix bucket at low speed ( 400RPM) until thouroghly mixed. Record ambient temperature, day and time using a brush for cutting and roller for surface, apply the first coat of 700x. Where membrane is terminated on a building element: Ensure that the termination height is 150mm of the membrane above the FFL and/or invert level of a correctly placed overflow/spitter satisfies the Façade engineer's advice.
Yes | No | NA
attach photos
second coat application of Enviro- 700X
Allow first coat to fully cured prior to application. Mix bucket at low speed ( 400RPM) until thouroghly mixed. Record ambient temperature, day and time using a brush for cutting and roller for surface, apply the first coat of 700x. Where membrane is terminated on a building element: Ensure that the termination height is 150mm of the membrane above the FFL and/or invert level of a correctly placed overflow/spitter satisfies the Façade engineer's advice.
Application of 250 N-S Top coat
Allow membrane to fully cured prior to application.Mix bucket at low speed ( 400RPM) until thouroghly mixed.If final coat has been exposed greater than 48 hours, refer to Mirvac for special instructions.Using a brush and roller apply 250 NS as final U.V protection coat. Where membrane is terminated on a building element: Ensure that the termination height of the membrane above the FFL and/or invert level of a correctly placed overflow/spitter satisfies the Façade engineer's advice.
Yes | No | N/A
attach photos
Protection of Membrane edge
Ensure vertical terminations of membranes on a building element are provided with a pressure seal, reglet or by being overcoated with a waterproof or water resistant material to protect the membrane edge. Esnure vertical membrane termination junctions are caulked with Enviro FC pro.
Yes | No | N/A
attach photos
QA Testing
Inspect after installation of reinforcement/finishes to check for any damage to waterproofing and rectify as required
Yes | No | N/A
attach photos
Thickness testing of application to the recommended dft of 1.5mm to manufacturers instructions. 5 tests per 15m2
Yes | No | N/A
Attach photos
24hours flood testing to mark out if applicable
Yes | No | N/A
Attach photos
Holiday/ spark testing of area if flood testing is not applicable
Yes | No | N/A
Attach photos
CLICK HERE TO REQUEST BUILDER SIGN OFF