## Cover Page
Mechanical Completion - Electrical Installation - OTG
Applicability: | C&P - bp pulse
Approver: | Alam Abboud
Approval Date: | 2025-01-28
Author: | Michael Skyrme
Checker: | John Wood
Checker Date: | 2025-01-28
Security Classification: | General
Document Number | EV001-QA-ITR-000-ANZ-0024
Revision Code: | B02
Next Review Date: | 2025-06-30

## Revision Info
Revision History
Rev | Reason for Issue/Revisions | Author | Checker | Checker Date | Approver | Approval Date
B01 | Approved for Use | Andrew Maddams | Gareth Jones | 2022-12-12 | Shane Wilson | 2022-12-12
B02 | Inclucion of ANZ requirements | Michael Skyrme | John Wood | 2025-01-28 | Alam Abboud | 2025-01-28
Hold References
Hold Reference |  | Description / Reason for Hold |  | Relevant Section(s) of this Document
Operating Management System
OMS Sub-Element |  | OMS Sub-Element Title
4.1 |  | Practices and Procedures
Reviewers
Name |  | Role |  | Date Reviewed | Type of Review
Informative References/Related Documents
Document Number |  | Document Title
EV001-CG-PRO-000-0002 |  | Electric Vehicle Charging Execution Procedure - System handover and acceptance
Unless stated otherwise in the content of this document, reference to the documents above is for information. Specific sections of the referenced documents will be given in the content of this document if conformance is required.
Scope and Exclusions
This document does not include any new mandatory requirements. Any reference to a mandatory requirement in this document cites the source bp Requirement Document. Thus, you should exercise care when relying upon mandatory requirements cited in this document by confirming they have not been modified in a subsequent version of the cited bp Requirement Document.
Use and Interpretation of this document
This document is classified as General unless labelled otherwise. It contains bp proprietary information. bp’s Code of Conduct requires you to protect that information. Refer to the Protecting our Information Policy for more details.
Outside bp, you can only distribute and use this document in accordance with the terms of any agreement under which it was supplied or received. BP accepts no liability or responsibility for the use of this document outside bp, unless an agreement with bp says otherwise.
This document applies only if it is consistent with applicable legal and regulatory requirements. If you are within BP and you identify an apparent conflict with those requirements, you should consult bp Legal.
This document has been approved for BP’s purposes only and not to describe or establish an industry standard or practice. Any recommendations or guidance are to help users to consider and evaluate potential options. Another approach may be appropriate. The authoritative, English version of this document is held online at https://bp-eb.bentley.com/CIS/Framework/Default.aspx. It takes precedence over any prior version and any non-English version.
Copyright © 2022 bp International Ltd. All rights reserved. All rights reserved.

## Electrical OTG ANZ
Project Title:
Site ID, Name & Address:
Mechanical Completion - Electrical Installation
HOLD POINT – Before energisation of electrical systems occurs, contractor to notify BP who will arrange an electrical engineering inspection & report. This will then be used to assist in completion of the Pre-Start Safety Review (PSSR) by BP (refer to BP PSSR template). Electrical systems shall not be energised until PSSR is completed and BP has provided approval to proceed.
Item # | Information/ Action Needed | Description of Check | Complete (Y / N / N/A) | Verification Signature (Contractor/ Subcontractor) | Acceptance Criteria (I/T/W/H/R) I – Inspection; T – Test; W – Witness Inspection Point; H – Hold Point for Inspection; R – Document Review |  |  |  | Comments
[5 empty] | Contractor | Contractor Signature& Date | Client | Client Signature& Date
SMSB
1 | SMSB - Set-up & Installation (1) | Record Serial Number |  |  | I |  | I |  | Serial Number:
1 | SMSB - Set-up & Installation (2) | Confirm SMSB has been installed as per manufactuers installation instructions (IOM) |  |  | I |  | I
1 | SMSB - Set-up & Installation (3) | Confirm SMSB is free from damage and paintwork is in good order with no scratches. |  |  | W |  | I
1 | SMSB - Set-up & Installation (4) | Required padlocks fitted with correct code applied. If applicable, client keys handed to bp PM. |  |  | I |  | I
1 | SMSB - Set-up & Installation (5) | Confirm cubicle doors can be fully opened without obstruction and door hinges are installed correctly. Confirm door seals are free from damage. |  |  | I |  | I
1 | SMSB - Set-up & Installation (6) | Confirm internal equipment is clean and dry. Check that all preservation (i.e. silica gel) has been removed (require prior to energisation) |  |  | I |  | I
1 | SMSB - Set-up & Installation (7) | Confirm all equipment carries the correct label identification |  |  | I |  | I
1 | SMSB - Set-up & Installation (8) | Confirm LV cable terminations are completed correctly and are torqued as per IOM with torque markings present |  |  | W |  | I
1 | SMSB - Set-up & Installation (9) | Confirm lifting lugs have been removed from SMSB and stowed inside panel |  |  | I |  | I
1 | SMSB - Set-up & Installation (10) | Confirm all warning labels and customer information labels are present on the SMSB. |  |  | I |  | I
1 | SMSB - Set-up & Installation (11) | Thermographic inspection of switchboards has been completed |  |  | I |  | I |  | Once PSSR Complete and LV Pillar under load
LV Pillar
1 | LV Pillar - Set-up & Installation (1) | Record Serial Number |  |  | I |  | I |  | Serial Number:
1 | LV Pillar - Set-up & Installation (2) | Confirm LVP has been installed as per manufactuers installation instructions (IOM) |  |  | I |  | I
1 | LV Pillar - Set-up & Installation (3) | Confirm LVP is free from damage and paintwork is in good order with no scratches. |  |  | W |  | I
1 | LV Pillar - Set-up & Installation (4) | Required padlocks fitted with correct code applied? |  |  | I |  | I
1 | LV Pillar - Set-up & Installation (5) | Confirm cubicle doors can be fully opened without obstruction and door hinges are installed correctly. Confirm door seals are free from damage. |  |  | I |  | I
1 | LV Pillar - Set-up & Installation (6) | Confirm internal equipment is clean and dry. Check that all preservation (i.e. silica gel) has been removed (require prior to energisation) |  |  | I |  | I
1 | LV Pillar - Set-up & Installation (7) | Confirm all equipment carries the correct label identification |  |  | I |  | I
1 | LV Pillar - Set-up & Installation (8) | Confirm LV cable terminations are completed correctly and are torqued as per IOM with torque markings present |  |  | W |  | I
1 | LV Pillar - Set-up & Installation (9) | Confirm lifting lugs have been removed from LV pillar and stowed inside panel |  |  | I |  | I
1 | LV Pillar - Set-up & Installation (10) | Confirm the 24VDC battery fuse is present and is in the stowed position (socket provided at the right hand end of the battery) |  |  | I |  | I
1 | LV Pillar - Set-up & Installation (11) | Confirm all warning labels and customer information labels are present on the LV pillar. |  |  | I |  | I
1 | LV Pillar - Set-up & Installation (12) | Thermographic inspection of switchboards/LV Pillar has been completed |  |  | I |  | I |  | Once PSSR Complete and LV Pillar under load
Cables/Cable Entry Points/Cable Containment
2 | LV Pillar - Cable Entry Points/Cable Containment (1) | Cable entries and ducts are correct to design requirements and entries are correctly blanked off/sealed with Rayflates/Foam or other approved method |  |  | H |  | I |  | Cross check to Civils to ensure depths and clearances of conduits have been achieved.
2 | LV Pillar - Cable Entry Points/Cable Containment (2) | Confirm all cable containment (Trays/Ladders) and cable cleats match the approved design, have no sharp edges and are installed to an acceptable standard with all metallic items earthed/bonded as required. Ensure bonds between tray joints are installed. |  |  | I |  | I |  | Cross check with Civils that the appropriate indicator tape has been installed as per standards.
2 | LV Pillar - Cable Entry Points/Cable Containment (3) | Cable tray lids/covers are installed as per design |  |  | W |  | I
3 | Cables (1) | All cables installed are the correct type/size, as per the approved design |  |  | W |  | I
3 | Cables (2) | Confirm the cable identifiers match the approved cable schedule |  |  | I |  | I
3 | Cables (3) | Minimum bending radius of cables have not been compromised throughout their installation. |  |  | W |  | I
3 | Cables (4) | Confirm cables are appropriately supported where required |  |  | I |  | I
3 | Cables (5) | Confirm cables have been appropriately dead tested after installation and prior to terminating to the LV pillar (continuity & insulation resistance test) and record values |  |  | T |  | R
3 | Cables (6) | Cable ends have been wrapped or covered after installation in ducts, to avoid water ingress in the cable (unless terminated directly after installation and testing) |  |  | W |  | I
Network Earthing System
4 | Network Earthing System | Check earthing system is installed as per the approved design, (including any footing earthing bonding) test and record earth loop impedence. |  |  | W |  | I
Metering
5 | Metering (1) | Confirm metering cabinet is free from damage and locked with padlock |  |  | I |  | I
5 | Metering (2) | Confirm Meter is installed and operational |  |  | I |  | I
Lighting and Small Power
6 | Lighting Columns (1) | Verify the number of lighting columns is as per the detailed design |  |  | W |  | I
6 | Lighting Columns (2) | Confirm lighting heads are facing the correct way as per the Detailed design and into EV bays as required |  |  | W |  | I
6 | Lighting Columns (3) | Confirm lighting is fully operational |  |  | W |  | I
|  | Name |  |  | Signature |  |  |  | Date
CONTRACTOR
bp Pulse