## Master List Templates
Id | Type | Name | Values | Prompting Name | Prefix | Postfix
38f7b193-f498-4cb4-a36f-155cc5378a88 | checklist | As-Built Drawings |  | As-Built Drawings
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
6d9a76c3-0a69-4449-b1e7-11ce6b7f2835 | checkpoint-no-value | As-Built Drawings - attach scanned documents
17517af2-db4a-45b7-8883-f495d7b7f393 | checklist | Certificate of compliance (COC) |  | Certificate of compliance (COC)
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
85c1dfac-a6c1-4c34-99e6-d95ecb814741 | checkpoint | Please upload Certificate of Compliance here when complete (COC)
d3d640a6-f0e5-4dbe-a426-bbdfbd9e88f1 | checklist | Entec Daily Report |  | Entec Daily Report
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
dfe33494-f1f3-416d-b200-985468c449e7 | checkpoint | Daily Report
aa373969-8b60-5d14-ae15-1d6c7fac2904 | date | Date:
4309b494-9321-536c-9669-b5bc5278607c | textbox | Site:
2afe42e3-2bd3-57c9-b2b9-374ad261339b | textbox | Work completed:
6dcd5e0d-0473-5824-8763-de1db794e25a | textbox | Issues:
5599a652-8b14-57c2-b35e-1f30796f07f0 | textbox | Weather:
419ec26a-ceb3-50a3-9ab8-b04b2aeb95db | textbox | Labour:
22314894-b51d-5b55-b048-3270208b4497 | textbox | Plant & Equipment used:
b64aca17-4380-4800-aa48-02e9df10ac6f | signoff | Signed/Approved:
8c25b346-2037-4ba0-ac1d-507cf1d62187 | checklist | HAZARDOUS AREA INSPECTION SHEET Ex t and tD |  | HAZARDOUS AREA INSPECTION SHEET Ex t and tD
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
1a322616-60da-4703-965a-ff33de867565 | checkpoint | Details
f8cbc461-0e4d-5996-9d87-109e8458d02c | textbox | Tag Number:
a4f0b95b-0a5f-5951-8ca7-b4902e5b2d91 | textbox | Site:
6137aff6-a8fe-51dc-b351-33e0cbd612c7 | textbox | Make:
a1ccedbc-48fe-545e-bcba-96810c036e07 | textbox | Model:
4594b4e8-9cf9-5b3e-a6fd-697800a42d29 | textbox | Model:
e642259d-a2ea-5a90-af49-8915d855ceaa | textbox | Serial Number:
ef7bc02d-320a-50aa-bfb1-b16237245798 | textbox | Protection type (nameplate):
c76b9e71-b7d8-5f1d-998c-01e24d845b9d | textbox | Protection Type (as installed):
180588da-7bcc-58bd-baea-ae7b1289b72c | textbox | Device Type:
1deaf32b-2e1d-5428-a043-ccb22a8ab158 | textbox | Location:
2c98d2f3-76ce-5dcf-8fea-ac50f10fc4c8 | textbox | Location Zone:
0a0d944d-5513-5ebc-a9ae-b6daf290fef6 | textbox | Location Dust Group:
909f07a0-43d7-5095-b0b8-6c9416a129db | textbox | Location Temp Class:
d1438089-c936-5d1b-af0c-ffca585004cb | textbox | Access Requirements:
8ccbe7b1-04aa-55a9-926c-ede8e9373c34 | textbox | HAC Drawing:
94e33a1c-41a7-556b-bfc7-e5ba584640b2 | textbox | Cause & Effects:
da8c40e6-a4cf-523b-b6e2-1790c4bf3f5a | textbox | Dust Group:
52092654-f2b4-55d3-9593-88d20e71d584 | textbox | Temp Class:
96a1dd65-1428-52ba-98cb-8f80a0b6ec40 | textbox | IP Rating:
73dac772-a536-5fc4-bde8-fbf06c50aad6 | textbox | Cert #:
dcdee7a9-e022-52e6-b816-da962566ef4f | textbox | Cable #:
227ef564-8058-5770-be0d-9fb72c1b4b24 | textbox | Loop Drwg:
70005884-ade7-5457-87de-41f4b4fadeac | textbox | P&ID Drwg:
1532cdf7-e9e7-42a9-ac80-3849e0e1a2b6 | checkpoint | General
d4136c9d-d318-5a63-a25e-c2a371e40e38 | button | Equipment is appropriate to the EPL/ Zone requirements of the location | YES, N/A
05644674-0107-5ed2-b03a-56920ceac588 | button | Equipment group is correct | YES, N/A
dd575170-9054-5dfb-be8c-f7bd9e2987c5 | button | IP grade of equipment is appropriate to conductivity of dust | YES, N/A
2f4e0b49-e6fe-598b-8839-4d0704685cf6 | button | Maximum surface temperature is correct | YES, N/A
825421be-d1ca-5bdd-af75-50bb72be9fe1 | button | Equipment circuit identification is available and correct | YES, N/A
a9729dd3-2445-5daf-87f8-b69ad9b9c45c | button | Enclosure, glass parts and glass to metal sealing gaskets and or compounds are satisfactory | YES, N/A
1e27edf5-ffa5-57ea-a35e-3f27f0f3e3f8 | button | There is no evident damage or unauthorised modifications | YES, N/A
4ff87ea7-b7ce-5433-acf1-9c72a802a688 | button | Bolts, cable entry devices (direct and indirect) and blanking elements are of the correct type and are complete and tight. | YES, N/A
857f9f1a-2ef5-5475-9a34-c4451f54f875 | button | Condition of enclosure gaskets is satisfactory | YES, N/A
ee4a78fc-ce43-5ef8-a895-638a02a6fbe4 | button | There is no evidence of ingress of water or dust in the enclosure in accordance with the IP rating | YES, N/A
fc8140f7-d645-5336-b4e3-33dc2efb8388 | button | Electrical connections are tight | YES, N/A
c05dffe8-fa07-520a-900c-53f009d2ccb2 | button | Lamp rating, type and position are correct and are not displaying EOL effects | YES, N/A
d3b6f152-c965-5632-b3a3-7675aab89e35 | button | Motor fans have sufficient clearance, cooling systems are undamaged and ventilation airflow is not impeded | YES, N/A
549631f8-af84-4153-9859-17b3dff15377 | checkpoint | Installation
82071346-4f87-582a-9709-12ec968fefc7 | button | Type of cable is appropriate, is adequately supported , and undamaged | YES, N/A
ec1515d3-1135-5d6f-85ee-ebecf24dce51 | button | There is no obvious damage to cables | YES, N/A
7429d27f-8b18-5bef-8fbf-270acdc74514 | button | Sealing of trunking, ducts, pipes and/ or conduits is satisfactory | YES, N/A
15a387f4-484f-50fb-8d86-2d2dd8f0cc7b | button | Integrity of conduit system and interface with mixed system maintained | YES, N/A
1825d024-d62a-5e43-9199-8c9f8285e798 | button | Earthing connections, including any supplementary earthing bonding connections are satisfactory | YES, N/A
e35ab899-79c6-5538-9c28-faa2c547c2fc | button | There is no evident damage or degradation that indicates that the fault loop impedance (TN systems) or earthing resistance (IT systems) is not satisfactory | YES, N/A
8697eb72-e955-5834-a524-61115f0ef522 | button | Automatic electrical protective devices are set correctly and operate within permitted limits | YES, N/A
ef8b23c4-5b34-5e7e-89e4-2b97aea95cd4 | button | Specific conditions of use (if applicable) are complied with. | YES, N/A
4b23e56a-2e9e-52d1-849f-e445bc8a2983 | button | Cables not in use are correctly terminated | YES, N/A
5b0e7f98-d4f5-5fd0-a72a-369f59aaf221 | button | Insulation resistance is satisfactory | YES, N/A
4ec969bd-afaf-5684-88e5-7c8422e9a2e2 | button | Temperature sensors/ safety cut offs function according to manufacturers instruction | YES, N/A
63e2d84c-2aa1-418e-9dbb-f3dd1a2f9378 | checkpoint | Environment
4d46567d-46de-5df1-b9a0-81010c02d263 | button | Equipment is adequately protected against corrosion, weather, vibration and other adverse factors | YES, N/A
8dff9c88-dd68-5991-919a-9d6e4b133dd5 | button | No undue accumulation of dust and dirt | YES, N/A
dc7ba13f-ebf9-5fbf-bff5-817e1a7ee6eb | button | Electrical insulation is clean and dry | YES, N/A
50c11e22-899f-41ac-b86a-2b3ebaece304 | checkpoint | Installation Details
52906b1f-04dd-5f73-8c67-99aeb017f9da | note | 1.Glands, 2.Stopping Plug, 3. Adaptor, 4. Breather, 5.Terminal, 6. Associated equipment
313fbd99-7f3b-5a5b-88b9-946026a3976e | dropdown | Select Type from Numbers Above: | 1,2,3,4,5,6
8c13f4e4-f0fb-590a-99ee-abf8f32f0dac | dropdown | Select Quantity: | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20
34a6fd3f-230b-57ab-912d-df1b902174e3 | textbox | Model:
bd4f7ce8-23bb-58d9-8f9b-8109af8b56bb | textbox | Make:
209a7e99-002d-5b8e-9528-1a207a0bf4a7 | textbox | Protection type, Gas grp, T-class, IP, Certificate
e7ab9faf-4d15-5dd9-b123-0322f63720dc | dropdown | Select Type from Numbers Above: | 1,2,3,4,5,6
f7a999f3-966b-5838-a4ab-cab6d23fc1bd | dropdown | Select Quantity: | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20
4550be6a-77b4-5b3b-bc5e-1062e4a4eaef | textbox | Model:
ef715c11-3078-5dcb-8dbb-db3c1792509d | textbox | Make:
3adb2755-b0ce-5055-8cd3-4fb4e7faeed6 | textbox | Protection type, Gas grp, T-class, IP, Certificate
b7a4b929-87f9-52e5-90e7-7dc3986c82d8 | dropdown | Select Type from Numbers Above: | 1,2,3,4,5,6
0bda0edc-aa6d-5dca-bb65-395dd0d0fca2 | dropdown | Select Quantity: | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20
55eead20-75a2-52ed-a4a9-02a503861750 | textbox | Model:
60cafd94-cf95-5033-92c3-4953facd8804 | textbox | Make:
4b0d45d0-9aad-582c-bfa3-856fca0b4b0f | textbox | Notes
ea20a024-f04c-597e-a1e5-cbfd379075bd | textbox | Enter notes and Comments Below:
47f2efda-5900-4cf0-ad7a-2cc28e5deff0 | signoff | Add signature from Inspector
58976db0-7bbc-430f-a43f-626be5bd5127 | checklist | HAZARDOUS AREA INSPECTION SHEET Exd |  | HAZARDOUS AREA INSPECTION SHEET Exd
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
eee1383c-9206-482f-b769-1f8dc2c0f6c1 | checkpoint | Details
1ddfc0ba-dd9c-51bf-80a7-948f85232efa | textbox | Tag Number:
b00788b2-232a-5a9b-903c-e0264ab91ca6 | textbox | Site:
9b1732ab-c3e2-5c26-b514-fa99e1f3a522 | textbox | Make:
12f69208-4bfd-5c5b-a362-411e0816cb8b | textbox | Model:
bafe9957-9db4-511d-bb35-d6542063c951 | textbox | Model:
bcb411f2-5a2d-54d6-9643-daf7d1510c97 | textbox | Serial Number:
1709fa5b-e57a-5791-a8c9-c421c052a95c | textbox | Protection type (nameplate):
b76cf62b-ab91-5ad0-9330-5e270ec8e430 | textbox | Protection Type (as installed):
b1f2fed6-4272-5d09-b0fe-d7efbe86c07f | textbox | Device Type:
e48f1236-cb4c-57ac-ba68-0ca3258ff713 | textbox | Location:
20473cf5-f104-5f18-852e-3b63b6107b11 | textbox | Location Zone:
a73be521-36ca-5739-bdba-9fb5da669579 | textbox | Location Dust Group:
4f91e02e-5bf9-5760-aff7-d29870430e8c | textbox | Location Temp Class:
f591ed15-ac37-50fb-8349-0a01a0c5ac35 | textbox | Access Requirements:
28083555-7d45-5651-ac2d-de48d81d7ebe | textbox | HAC Drawing:
e840d783-946f-58c7-889d-afea8196961d | textbox | Cause & Effects:
419220a4-2224-5f98-be1b-369008550928 | textbox | Dust Group:
8a7ba6bd-e1a5-5d49-83cc-4421653b1a57 | textbox | Temp Class:
9f54207a-9815-560a-859e-916abb175d6a | textbox | IP Rating:
809b97d4-547c-5614-993e-67f617f02914 | textbox | Cert #:
0ff34f4b-9673-53ce-90f7-c1d5bedde4ad | textbox | Cable #:
7a57052e-f549-5ff4-9fd0-cb056beee462 | textbox | Loop Drwg:
3d3cd99e-77bf-5a0b-917b-79fe61ee14ec | textbox | P&ID Drwg:
3b4a4734-3abf-4c8a-a3d4-ab64360b08db | checkpoint | General
cef38489-7742-5c02-afd7-c67ec194fa1e | button | Equipment is appropriate to the EPL/ Zone requirements of the location | YES, N/A
94b4d118-c1ad-5f40-b8ee-72911637a820 | button | Equipment group is correct | YES, N/A
2b7f592f-5595-53ac-a1d5-6b5072021d88 | button | Equipment temperature class is correct | YES, N/A
cb1cadc1-fcdb-584b-b756-f99baabbe035 | button | Degree of protection (IP) of equipment is appropriate for the level of protection/group/conductivity | YES, N/A
950f8d3b-f5f6-5aab-89b6-80ac6c25f5be | button | Equipment circuit identification is correct | YES, N/A
696a85a0-e88f-5b9c-85ba-f4e7814de19e | button | Equipment circuit identification is available | YES, N/A
6b7d3295-5a62-597c-a0bd-77e790f3fa43 | button | Enclosure, glass parts, and glass to metal sealing gaskets and or compounds are satisfactory | YES, N/A
e5942188-7509-5b8e-b840-1e1971d84d1a | button | There is no damage or unauthorised modifications | YES, N/A
1a46d9c7-44c4-52cc-873b-0684f23284eb | button | Bolts, cable entry devices, and blanking elements are of the correct type and are complete and tight | YES, N/A
9bd2ccaf-c7f1-518e-95ce-2b41402a1785 | button | Threaded covers on enclosures are of the correct type, are tight and secured | YES, N/A
6115b38b-16d5-551d-adbf-ff837694e4e0 | button | Joint surfaces are clean and undamaged and gaskets, if any, are satisfactory and positioned correctly | YES, N/A
c869f36a-8ff4-50fd-b1ba-cd98c14b8e8d | button | There is no evidence of ingress of water or dust in the enclosure in accordance with the IP rating | YES, N/A
e449f1cc-5b6b-5c90-a0b0-cc98003ef669 | button | Dimensions of flanged joint gaps are within the limits permitted by manufacturers documentation or relevant construction standard at time of installation | YES, N/A
e149a79f-78a7-5a8f-a171-89ba27ced3da | button | Breathing and draining devices are satisfactory, and operating effectively | YES, N/A
68bec521-3afa-50ff-8f92-1f9d6f580437 | button | Type of cable is appropriate is adequately supported and undamaged | YES, N/A
020f0030-1700-5152-aeb7-5ffba5ccf950 | button | Sealing of trunking, ducts, pipes and/or conduits is satisfactory | YES, N/A
0565de7e-d32c-5841-9d2b-c1a179451dbb | button | Stopping boxes and cable boxes are correctly filled | YES, N/A
c19ee724-fc13-5cfe-a861-ec9378b40bcf | button | Integrity of conduit system and interface with mixed system maintained | YES, N/A
e0245aa4-9b26-521e-892b-a8e8e6203888 | button | Earthing connections, including any supplementary earthing bonding connections are satisfactory | YES, N/A
f5a497bb-e7e7-59f2-ae56-76f552422e71 | button | There is no evident damage or degradation that indicates that the fault loop impedance (TN system) or earthing resistance (IT system) is not satisfactory | YES, N/A
fd63c2c4-9def-5428-b0ad-2884e6547331 | button | There is no evident damage or degradation that indicates that the insulation resistance is not satisfactory. | YES, N/A
cc00b5ba-7640-5ad5-850f-2646baa3749a | button | Automatic electrical protective devices are set correctly (auto reset not possible) and operate within permitted limits | YES, N/A
c1f3917f-8b08-5d44-b4b4-de8938d583a2 | button | Specific conditions of use (if applicable) are complied with | YES, N/A
014334dc-0d48-54fc-9126-c6ce0139b24c | button | Cables not in use are correctly terminated | YES, N/A
42aeeda2-b066-5a17-9e02-9b2207240590 | button | Obstructions adjacent to flameproof flanged joints are in accordance with AS/NZS 60079-14 | YES, N/A
86155653-bd9e-5755-933e-8d986fc0a4dc | button | Variable voltage/frequency installation complies with documentation | YES, N/A
31973af8-1300-5401-9c61-ae3f1abb721c | button | Equipment is adequately protected against corrosion, weather, vibration and other adverse factors | YES, N/A
2c9278a6-2940-5700-8550-527eb732e9f8 | button | No undue accumulation of dust and dirt | YES, N/A
477aa1ce-a2c9-4f9b-a75f-2be07f68cd0a | checkpoint | Lighting
3881d30c-f4f4-5872-8d35-ff85d35e98f3 | button | HID Lamps are not indicating EOL effects | YES, N/A
a52b5aff-e5d3-5a14-bced-58adffa6c839 | button | Lamp type, rating, pin configuration and position are correct | YES, N/A
67d3db2a-6c7e-4bfa-bbb7-c248d7203ebb | checkpoint | Motors
c346e8f5-45ce-51f4-9140-64c162b29a52 | button | Motor fans have sufficient clearance to the enclosure and or covers, cooling systems are undamaged, motor foundations have no indentations or cracks | YES, N/A
b72f16a5-9f4d-5076-b9da-5ce7db3d42c2 | button | The ventilation airflow is not impeded | YES, N/A
2e27fce0-c605-5c18-a7aa-4030dd584202 | button | Insulation resistance (IR) of the motor windings is satisfactory | YES, N/A
0e1a45e2-0e52-427a-a9af-5b63fde3c220 | checkpoint | Heating Systems
633e2b86-26e9-5c47-8af2-917aeb613b9e | button | Temperature sensors function according to manufacturers documents | YES, N/A
69b19c1c-b9b3-59d9-bca9-04e413fc3b7b | button | Safety cut off devices function according to manufacturers documents | YES, N/A
cd99cab1-da48-5d46-abf0-3a9d55950976 | button | The setting of the safety cut off is sealed | YES, N/A
7c6b6c71-ece1-559f-978e-326c321cf473 | button | Reset of a heating system safety cut off possible with tool only | YES, N/A
38900236-90d7-58f5-bd2e-8bc5e641d2d9 | button | Auto-reset is not possible | YES, N/A
9aad0618-c030-52e9-a345-cd908c79177a | button | Reset of a safety cut off under under fault conditions is prevented | YES, N/A
6f52d2f4-d92a-55c6-bcc3-3a4f9a24036d | button | Safety cut off independent from control system | YES, N/A
eeb35069-3a9c-5de0-b772-85f571dee389 | button | Level/Flow switch is installed and correctly set if required | YES, N/A
c159fa46-6ebc-46ba-82e1-0927133bedb2 | checkpoint | Installation Details
942f5572-2da3-594f-8a8d-3d2c20e1961c | note | 1.Glands, 2.Stopping Plug, 3. Adaptor, 4. Breather, 5.Terminal, 6. Associated equipment
eef4d33b-0a3d-515c-8e6a-2c5f64c3efc6 | dropdown | Select Type from Numbers Above: | 1,2,3,4,5,6
ac9922fd-0acc-5d40-8258-bd46117679b0 | dropdown | Select Quantity: | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20
9c2d8fe3-e7d6-552a-b430-53ce1f7f4cd9 | textbox | Model:
5f8f9ea2-2c2e-5d94-9696-a896386893d4 | textbox | Make:
0f871e2d-ee94-523e-a250-d7200653f327 | textbox | Protection type, Gas grp, T-class, IP, Certificate
376e2228-2278-5a44-9d4f-45f07792a87b | dropdown | Select Type from Numbers Above: | 1,2,3,4,5,6
d5cedd1b-9a53-5e17-ad22-d4ecca0a0de7 | dropdown | Select Quantity: | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20
ec7e0ff5-9137-55a3-af87-77519986b980 | textbox | Model:
955e4b86-d529-58df-ac14-a1d1478805a7 | textbox | Make:
5008c49f-c1a0-56b8-9072-64e76e486cd6 | textbox | Protection type, Gas grp, T-class, IP, Certificate
9811b7db-22d3-5bc6-b67d-968beb68e602 | dropdown | Select Type from Numbers Above: | 1,2,3,4,5,6
3448e00b-ca17-5109-96d8-9085189d44a1 | dropdown | Select Quantity: | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20
f26d4639-c73c-5e2a-8a0b-b870c43acb52 | textbox | Model:
eb35ffc1-de0f-581e-b2d6-4b33536d1fcf | textbox | Make:
5c06c248-de18-527e-a2b2-7a3d313dd85a | textbox | Notes
c43bc6ce-5751-5f67-a59f-c5bef643dbe2 | textbox | Enter notes and Comments Below:
6493e556-8ab2-45ac-bc68-057510741385 | signoff | Add signature from Inspector
728dc08a-a996-4c10-bc84-b6cfcaf5fd7a | checklist | HAZARDOUS AREA INSPECTION SHEET Exe |  | HAZARDOUS AREA INSPECTION SHEET Exe
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
491df83e-2781-4a01-9469-5309f072658d | checkpoint | Details
95576cb5-9068-5a97-a9e1-2846a38d91e8 | textbox | Tag Number:
eecb25aa-428a-5ccc-83af-0660aed8b9cc | textbox | Site:
659bd04e-df44-50d9-a9c3-61f32b1a63db | textbox | Make:
4ecbea56-888e-53e8-8066-ae1ea60f0288 | textbox | Model:
1cf554ed-4a5f-50ac-9ee6-6ceac97e9d03 | textbox | Model:
98a4f14d-aada-54f1-9302-8fda5b05a363 | textbox | Serial Number:
2ea0967f-f70d-53c9-828b-4c9b7ba41c3b | textbox | Protection type (nameplate):
6c994d88-6af2-5c55-959b-a8020bc50ef2 | textbox | Protection Type (as installed):
2e5e37f0-0b0a-5afc-a02d-7e522fbd467a | textbox | Device Type:
d2d38724-1d28-5028-b3a5-f502ca05e847 | textbox | Location:
4dbb654c-0775-5024-8bad-d4558491aae7 | textbox | Location Zone:
231c4f36-1e9d-5385-a5e6-4025c462ff4a | textbox | Location Dust Group:
625e1847-e768-51cb-bd93-5dc6d4e30a3c | textbox | Location Temp Class:
82b9d9fe-d262-5dad-90b5-21bde03521f3 | textbox | Access Requirements:
4b7676e9-f79f-51eb-9a01-9657b4c3a24e | textbox | HAC Drawing:
06688f84-3b2e-5194-90ce-9a4659d68003 | textbox | Cause & Effects:
55f8f836-f1dd-5a12-b388-9fd85dfb7435 | textbox | Dust Group:
30535fef-7a2b-5fb7-a105-682fe003e951 | textbox | Temp Class:
323e6dd4-81b0-5e0f-9432-9dead3a80739 | textbox | IP Rating:
2cdbfa1a-4fb2-58b9-ae73-210adbadd8c4 | textbox | Cert #:
6193c661-e3c8-5f27-b32b-4bbc61667c25 | textbox | Cable #:
3140d256-2a2b-5437-be10-05fff9fe7211 | textbox | Loop Drwg:
83ab7bae-cec9-5332-9f47-662caa7c272c | textbox | P&ID Drwg:
dcadc9d7-377a-420f-8ee6-50031c592224 | checkpoint | General
f86c4d20-40bb-508c-ac66-7fedee39bbf7 | button | Equipment is appropriate to the EPL/ Zone requirements of the location | YES, N/A
9bd759b3-6a7b-56f6-bfa2-0c0feaa8f781 | button | Equipment group is correct | YES, N/A
7c65b77e-e107-52d8-ae93-19863aedbafd | button | Equipment temperature class is correct | YES, N/A
566f8a37-b76d-54d0-9545-bc6ca104a391 | button | Degree of protection (IP) of equipment is appropriate for the level of protection/group/conductivity | YES, N/A
2083f22e-0a14-520e-a7a7-8760687411e0 | button | Equipment circuit identification is correct | YES, N/A
fe0d486e-98ef-57d8-bc42-81db6b09836c | button | Equipment circuit identification is available | YES, N/A
ea0e175c-3750-512e-9ba2-d85378efc519 | button | Enclosure, glass parts, and glass to metal sealing gaskets and or compounds are satisfactory | YES, N/A
3b897fad-c08a-507d-ae95-5d5faf820bf1 | button | There is no damage or unauthorised modifications | YES, N/A
dd0c590c-f754-5637-85f5-f47eb698f53e | button | Bolts, cable entry devices, and blanking elements are of the correct type and are complete and tight (physical check) | YES, N/A
8ab1c8c7-3e04-541f-9c92-c9d52958ed11 | button | Condition of enclosure gaskets is satisfactory | YES, N/A
9520a47b-68c8-564c-8eb3-f7246684a2b0 | button | There is no evidence of ingress of water or dust in the enclosure in accordance with the IP rating | YES, N/A
a1a2221f-ede2-5083-8046-6ac1af8a2f28 | button | Electrical connections and unused terminals are tight | YES, N/A
2e9ddae1-1f76-5c52-93e9-2a82324d1fd6 | button | Encapsulated and/or flameproof components are undamaged | YES, N/A
5b7a46e5-c970-555a-9dda-f2fd55128ee6 | button | Breathing and draining devices are satisfactory, and operating effectively | YES, N/A
9baea339-3c7e-53a8-98c0-55d2107ef8c3 | button | Type of cable is appropriate is adequately supported and undamaged | YES, N/A
5e72c0cd-f14f-5364-9f72-5ad4b60d067e | button | Sealing of trunking, ducts, pipes and/or conduits is satisfactory | YES, N/A
e2820eda-28d1-5794-a09c-69dd34721290 | button | Integrity of conduit system and interface with mixed system maintained | YES, N/A
9bd7aac2-a7ab-5487-841e-962fda2a852f | button | Earthing connections, including any supplementary earthing bonding connections are satisfactory | YES, N/A
9c3d0dc5-1b30-5911-94a8-fb9270f51b10 | button | There is no evident damage or degradation that indicates that the fault loop impedance (TN system) or earthing resistance (IT system) is not satisfactory | YES, N/A
7cf99bf7-9127-52f3-be78-8ba7fb0cc884 | button | There is no evident damage or degradation that indicates the insulation resistance is not satisfactory. | YES, N/A
4b126baa-5ba3-5bd8-a756-a0528a9f3db4 | button | Automatic electrical protective devices are set correctly (auto reset not possible) and operate within permitted limits | YES, N/A
e6854892-178b-5189-8c22-62b4dda01403 | button | Specific conditions of use (if applicable) are complied with | YES, N/A
3792af4e-3c85-5c2c-8e00-d9ce62084980 | button | Cables not in use are correctly terminated | YES, N/A
980759ae-aed6-54db-8ae6-0d266251e0f5 | button | Variable voltage/frequency installation complies with documentation | YES, N/A
662b4d59-022b-5852-9e6e-e2fa8901ad71 | button | Equipment is adequately protected against corrosion, weather, vibration and other adverse factors | YES, N/A
3d1df306-a396-57e7-afd2-37e95776b3a7 | button | No undue accumulation of dust and dirt | YES, N/A
230bcc9d-8658-5bc9-829f-91592bf63348 | button | All equipment housings are clean and dry | YES, N/A
1aaa4bf1-dc52-41ff-8f4d-a1c7d300f23c | checkpoint | Lighting
3b9cdb21-c13a-5352-8101-b4da75e5b158 | button | Fluorescent lamps are not indicating EOL effects | YES, N/A
778f59ee-a7b4-53df-a65d-f9ec3a2568b2 | button | HID Lamps are not indicating EOL effects | YES, N/A
f8440298-055c-5431-a418-dfa7a112483e | button | Lamp type, rating, pin configuration and position are correct | YES, N/A
dc2e50ed-b30b-4e5d-bfa2-f5f640b0f184 | checkpoint | Motors
c6f1ce48-3148-51a6-aea2-18b5dae37c94 | button | Motor fans have sufficient clearance to the enclosure and or covers, cooling systems are undamaged, motor foundations have no indentations or cracks | YES, N/A
c128cec5-b211-56e1-9cd6-36ac1fcc270c | button | The ventilation airflow is not impeded | YES, N/A
40d1a128-2587-568c-97ee-e91dfc1f1eb4 | button | Insulation resistance (IR) of the motor windings is satisfactory | YES, N/A
15c6b50a-7e75-55d2-86bb-8f38d314e1c6 | button | Motor protection devices operate within the permitted Te or Ta time limits | YES, N/A
956e575c-ae4c-421f-a4d4-cd9423e19ba0 | checkpoint | Heating Systems
48c34c84-3214-5f42-9052-c6236855a5dc | button | Temperature sensors function according to manufacturers documents | YES, N/A
2cf55bdf-dedf-544b-b879-e409f41626b5 | button | Safety cut off devices function according to manufacturers documents | YES, N/A
81f3071b-2dbc-5908-bb8f-15527fadbc17 | button | The setting of the safety cut off is sealed | YES, N/A
748f7820-ca37-5318-afbb-8046afc90ae9 | button | Reset of a heating system safety cut off possible with tool only | YES, N/A
58ee2d27-2a38-5266-9f53-40a19485d955 | button | Auto-reset is not possible | YES, N/A
1b1a8e95-3106-53c3-848d-b55ef5ca144b | button | Reset of a safety cut off under under fault conditions is prevented | YES, N/A
2ee62ee3-b169-592e-b850-0d135a672f49 | button | Safety cut off independent from control system | YES, N/A
d2a3bc22-f8cb-51f5-aa4f-0c6b53242a0e | button | Level/Flow switch is installed and correctly set if required | YES, N/A
aa0f0767-cb4e-49f4-93c3-a315f9840cd2 | checkpoint | Installation Details
238ada6d-128f-5a2e-9722-9a87b888bb23 | note | 1.Glands, 2.Stopping Plug, 3. Adaptor, 4. Breather, 5.Terminal, 6. Associated equipment
177a901c-dcb2-5b26-80c0-6f13424d6f87 | dropdown | Select Type from Numbers Above: | 1,2,3,4,5,6
da620967-56d1-590c-8682-22abd9878acd | dropdown | Select Quantity: | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20
5b7e3de9-a144-550d-bb84-5528fad84282 | textbox | Model:
d2ec2947-81e2-52a4-b68a-96f3e3e491ab | textbox | Make:
ee771f12-18c7-58e2-a1ff-1e023a06d998 | textbox | Protection type, Gas grp, T-class, IP, Certificate
fb3d6b88-a8ed-52ea-9849-95c9b6a16389 | dropdown | Select Type from Numbers Above: | 1,2,3,4,5,6
82062fa5-20e6-5d72-b42d-345977e11046 | dropdown | Select Quantity: | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20
12590f56-f707-522a-a24f-291c603c7f0e | textbox | Model:
680bac9c-a139-5f9e-a79f-2848f16454ab | textbox | Make:
f1c68a6c-b581-556d-b75c-d6d0175e59a5 | textbox | Protection type, Gas grp, T-class, IP, Certificate
d07fe026-f93f-54e2-8a52-7ee58ba0e5ec | dropdown | Select Type from Numbers Above: | 1,2,3,4,5,6
5d24e239-6f11-55bf-bd2f-32904db9893f | dropdown | Select Quantity: | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20
61919174-e1ae-5d3e-8484-17fd7f035658 | textbox | Model:
0e83aa06-c8b8-563c-be3b-92e9285217a8 | textbox | Make:
545710bc-1035-5746-accc-ae8b0f2514a2 | textbox | Notes
d13701a8-91d6-55df-8e0d-fcd50e0b707a | textbox | Enter notes and Comments Below:
4016b2ef-e71f-4b4d-ba48-66aba89d2b0d | signoff | Add signature from Inspector
83e5da18-5b04-4a86-a574-de27728ca2c2 | checklist | HAZARDOUS AREA INSPECTION SHEET Exi |  | HAZARDOUS AREA INSPECTION SHEET Exi
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
58f460df-c44a-4b68-8b4a-6f311cfed5ba | checkpoint | Details
791e9258-98eb-5dd1-926f-da2c8e5e6b14 | textbox | Tag Number:
4bd9c2f4-b716-5055-b8d9-ca58c1275abf | textbox | Site:
6950af5a-45c3-5942-b281-1754688236da | textbox | Make:
55d7cf13-534a-5545-a8c4-4ea6b6f2c0eb | textbox | Model:
ed76fb51-533f-5fd2-bc60-1c7718b9ea69 | textbox | Model:
b505bf2e-c7c6-544c-ab1f-d80c5b6d54f1 | textbox | Serial Number:
bdb3e316-e3f1-5c99-9f4f-1aa15c5f4805 | textbox | Protection type (nameplate):
00a8e79d-cbd6-5f82-8f29-c79707fc49f0 | textbox | Protection Type (as installed):
e563e3cf-709e-5dd4-8dc0-dc8f0afec78e | textbox | Device Type:
8b5b1515-4d38-581b-952e-b9c1b37508c8 | textbox | Location:
1ccb1a77-3637-5f91-b1d1-b0648c66af87 | textbox | Location Zone:
27cd0e73-1373-57c5-8cf7-38ff7d7146df | textbox | Location Dust Group:
faadc76f-9e98-5e82-ae55-26efb1f16cc0 | textbox | Location Temp Class:
18d76267-3e7f-50d2-81e3-c6c6f470c3ff | textbox | Access Requirements:
e54d7036-7e58-54eb-87a6-ecc7977184e4 | textbox | HAC Drawing:
cd363299-fdfe-5361-98a4-1082b14f80f7 | textbox | Cause & Effects:
fd47e717-3ef7-5e56-a91c-d307d2b7f936 | textbox | Dust Group:
51faf71d-8e62-5aa9-84b0-0bfc8e26578b | textbox | Temp Class:
fb1f2399-2d39-546d-b893-326ff95a7980 | textbox | IP Rating:
a6db1b4f-b3f3-53cd-9cb2-d91e9be3f5e2 | textbox | Cert #:
bac587ff-3188-5d73-bbb6-6c312a7fd512 | textbox | Cable #:
38fd8eea-db9d-532d-9216-c36d6b819f33 | textbox | Loop Drwg:
4536aa51-57ca-5709-9150-e0bfe901c0b1 | textbox | P&ID Drwg:
09549c31-7b7a-4073-8320-a96f18fef1fe | checkpoint | General
610f8d7f-084c-5497-bd4a-65a5ef84cf73 | button | Equipment is appropriate to the EPL/ Zone requirements of the location | YES, N/A
ce09ae8e-e0fc-5993-8199-ef86427abbe2 | button | Equipment installed is that specified in the documentation | YES, N/A
cfdea04b-83f2-5b3a-9834-0a11c993fbde | button | Circuit and/or equipment category and group correct | YES, N/A
e0c7d86e-9830-57d0-9128-9616592a6117 | button | Equipment temperature class is correct | YES, N/A
2a5043fa-30f7-5d5a-a74d-ef7adcd7ce9b | button | Ambient temperature range of the apparatus is correct for the installation | YES, N/A
eeae6908-f1c2-515f-8c38-ba48eb204da0 | button | Service temperature range of the apparatus iscorrect for the installation | YES, N/A
7f396a9a-5e38-5c3a-8fe1-85c4d2017a70 | button | Installation is clearly labelled | YES, N/A
edf348e9-43a1-5dbc-b1dc-6e992c04432e | button | Enclosure, glass parts, and glass to metal sealing gaskets and/or compounds are satisfactory | YES, N/A
837c909a-807c-5a64-92a6-f5f539b4b9ee | button | Cable glands and blanking elements are the correct type, complete and tight | YES, N/A
6bb6788f-af90-5c18-89a2-60b6764b6312 | button | There is no damage or unauthorised modifications | YES, N/A
14132d38-8153-5b63-b719-33f2f1785532 | button | Diode safety barriers, galvanic isolators, relays and other energy limiting devices are of the approved type, installed in accordance with the certification requirements and securely earthed where required | YES, N/A
83a4d4b4-4f82-5242-a4c2-70cdffc2bcfc | button | Condition of enclosure gaskets is satisfactory | YES, N/A
bba55357-1704-5a94-8cd7-92533487b274 | button | Electrical connections are tight | YES, N/A
df4a5a0e-bbc1-54f3-bbaf-14fb87c434ee | button | Printed circuit boards are clean and undamaged | YES, N/A
ea998aef-76da-51ce-993f-876f574e73f7 | button | The maximum voltage Um of the associated apparatus is not exceeded | YES, N/A
b4b1e5ec-e6d8-4feb-9a10-ae9c5029886e | checkpoint | Installation
a340bd93-e587-5e80-ac41-d6cbf7cc4fb2 | button | Cables are installed in accordance with the documentation | YES, N/A
aefbf045-b57e-56d4-9ae6-cd5ea57d3ae3 | button | Cable screens are earthed in accordance with the documentation | YES, N/A
a609c86b-95aa-590b-ae3d-d6ab832874ca | button | The cables are adequately supported and there is no obvious damage to cables | YES, N/A
34000926-2e2b-5f57-abc0-4a45eb3cd44f | button | Sealing of trunking, ducts, pipes and/or conduits is satisfactory | YES, N/A
8a09a9d0-c97e-5352-84e0-aa7eb5f70633 | button | Point to point connections are all correct (Initial Inspection Only) | YES, N/A
3f5e3f24-e606-5209-ae8b-ed043998f4ae | button | Earth continuity is satisfactory for non galvanically isolated circuits | YES, N/A
d2cc1f3d-f95b-55af-be1b-516552bababb | button | Earth connections maintain the the integrity of the type of protection | YES, N/A
d1827f43-86d1-5a63-af09-f71b7476b3c8 | button | There is no evident damage or degradation that indicates that the intrinsically safe earthing is not satisfactory | YES, N/A
0b9c2cd7-9602-569c-918f-143c2230a89e | button | Insulation resistance is satisfactory | YES, N/A
f507f37d-05ce-57c4-b67c-cbfc1a43888c | button | Separation is maintained between intrinsically safe and non intrinsically safe circits in common distribution boxes or relay cubicles | YES, N/A
861407c6-2d42-572c-8d23-543fa3dc0c3c | button | Short circuit protection of the power supply is in accordance with the documentation | YES, N/A
887af61f-bbfa-5d22-ae58-780afa2e6525 | button | Specific conditions of use (if applicable) are complied with | YES, N/A
32e96a8a-e2da-5fd5-a6a5-08ae3a7d226e | button | Cables not in use are correctly terminated | YES, N/A
344c06fd-2803-45b4-a1ab-e0946109efc2 | checkpoint | Environment
fe0ed92e-5514-5daf-a909-f8db66040281 | button | Equipment is adequately protected against corrosion, weather, vibration and other adverse factors | YES, N/A
ff74d0a3-7f5a-53bb-bd2a-b643b5eb2e05 | button | No undue accumulation of dust and dirt | YES, N/A
79df1a13-1941-462a-94b6-49449942097c | checkpoint | Installation Details
180122c1-359b-5448-98b8-5ef2b6f5bbb6 | note | 1.Glands, 2.Stopping Plug, 3. Adaptor, 4. Breather, 5.Terminal, 6. Associated equipment
d280affb-5c88-5039-883e-2a38da2ad1a8 | dropdown | Select Type from Numbers Above: | 1,2,3,4,5,6
b3f133bd-e948-50f1-a801-88961e90e0b4 | dropdown | Select Quantity: | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20
29706a60-2ea9-5176-9639-e2da9d83b9c8 | textbox | Model:
cbb6b05a-3a05-5d8b-bc69-8cde42b97166 | textbox | Make:
d8aad257-b1a1-517e-a55d-d8d7eadf5459 | textbox | Protection type, Gas grp, T-class, IP, Certificate
7b3c1324-e37f-5f23-a932-f50cdf3ad47e | dropdown | Select Type from Numbers Above: | 1,2,3,4,5,6
8d2a4cfc-00fd-52f5-a62d-e198224ab42e | dropdown | Select Quantity: | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20
3333ee7e-a380-57ef-b62a-8fb2a41bd919 | textbox | Model:
7cebabd0-cc5c-57cd-8969-e1daed30db37 | textbox | Make:
3281c613-3d01-5fc1-914c-fdf45e4f419e | textbox | Protection type, Gas grp, T-class, IP, Certificate
22f6caa7-ba57-531f-8ae6-c7b7e6a25cdb | dropdown | Select Type from Numbers Above: | 1,2,3,4,5,6
fbe4dde4-7357-50d7-b0f8-010b32dee0f0 | dropdown | Select Quantity: | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20
98680052-e6de-53cd-a3e2-d0a923066ff5 | textbox | Model:
7b520601-7ca3-5fe7-9b90-9cb502b07c8a | textbox | Make:
feabd836-00ef-5e36-afc8-d4a07e9c77a3 | textbox | Notes
605b3e76-ffb1-5d09-bd50-60b43450ad43 | textbox | Enter notes and Comments Below:
e1eba342-72b6-4a51-85ef-d9ff465e06f2 | signoff | Add signature from Inspector
bde3468c-b2c7-4b21-ac81-35dd89ad437a | checklist | HAZARDOUS AREA INSPECTION SHEET Exn |  | HAZARDOUS AREA INSPECTION SHEET Exn
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
818a2963-2b65-4382-a244-eae87292d46e | checkpoint | Details
e0f0cb7a-c6d6-57ca-a0e6-3249bec2c870 | textbox | Tag Number:
d2326e57-7aad-5025-b12b-cba2fad48292 | textbox | Site:
6f3193bb-a6ba-59a2-8734-7a52cd819b52 | textbox | Make:
181334bc-fd56-5bae-994e-50e92b103d70 | textbox | Model:
5fdd22f4-51e2-5b1c-8457-aec0d8b84041 | textbox | Model:
5503a87f-1d87-5d42-8180-450923794591 | textbox | Serial Number:
0db9228b-2a4c-509f-821c-f5b8f3a2afe4 | textbox | Protection type (nameplate):
74655f20-317e-5e70-9d55-7ff1126abeb1 | textbox | Protection Type (as installed):
b35e8069-1b2a-5536-a7a2-4b9de20e725a | textbox | Device Type:
07eebbc6-2bd5-50ee-a299-edfb85e57024 | textbox | Location:
2ffe0b01-6620-5819-ad35-e3e5e6b4eb56 | textbox | Location Zone:
49fadb76-4cf2-5e44-ac31-49e2f7e5611a | textbox | Location Dust Group:
1ecf6432-931a-5765-8e01-3ce0f56c8d4c | textbox | Location Temp Class:
3da61c77-c1ae-54ba-85c1-dc9e9de1cad1 | textbox | Access Requirements:
0449961e-9165-5c02-820a-09ddeb83df1d | textbox | HAC Drawing:
553ce88a-0f4b-5f61-b7ed-2ed69eed3426 | textbox | Cause & Effects:
05d830ca-4334-59bc-8961-a2f3026f7a61 | textbox | Dust Group:
d7a362fb-e5b6-5a65-91de-cbc5507e8f8c | textbox | Temp Class:
3ddec7ce-d6bb-5997-8ae5-ea6af52fda65 | textbox | IP Rating:
db8f81cf-791f-5214-acf3-ae7118df6188 | textbox | Cert #:
f214c3a3-66dc-5df2-a91d-1bfa3360ab4d | textbox | Cable #:
a0d1e1e1-d160-5b05-8bff-77148a63abd0 | textbox | Loop Drwg:
7459e54c-c823-5b10-8d89-904db8469384 | textbox | P&ID Drwg:
29b18d07-2e3a-4195-8f3c-d6497dffc705 | checkpoint | General
b37c6bd6-f525-5d11-a75c-46340ace7fd0 | button | Equipment is appropriate to the EPL/ Zone requirements of the location | YES, N/A
7d10c3cd-ea58-5d3e-a6e5-502dc3518bd8 | button | Equipment group is correct | YES, N/A
cf7e054c-80ac-5b73-a4cd-2af873d41d11 | button | Equipment temperature class is correct | YES, N/A
dd00b8fc-8aac-5203-a500-0a527b6e8b13 | button | Degree of protection (IP) of equipment is appropriate for the level of protection/group/conductivity | YES, N/A
342f7c55-526c-5037-b317-eafb8ea8ff04 | button | Equipment circuit identification is correct | YES, N/A
b950cace-a2b6-5489-b7c5-774dd8fdf0ff | button | Equipment circuit identification is available | YES, N/A
8aaa5ec9-5a8a-5590-b00d-82e7049ef67c | button | Enclosure, glass parts, and glass to metal sealing gaskets and or compounds are satisfactory | YES, N/A
d5b02ef3-ea4b-5ce5-a98d-1758dae59846 | button | There is no damage or unauthorised modifications | YES, N/A
18236df7-c2bd-5adf-bddc-5d600d09f74a | button | Bolts, cable entry devices, and blanking elements are of the correct type and are complete and tight (physical check) | YES, N/A
86383f36-6dc5-5d8e-a542-258f736a0e48 | button | Condition of enclosure gaskets is satisfactory | YES, N/A
b957c013-8cb6-56fe-879f-dd7576850067 | button | There is no evidence of ingress of water or dust in the enclosure in accordance with the IP rating | YES, N/A
58a5120a-1b43-5397-8855-23a2509fa83d | button | Electrical connections and unused terminals are tight | YES, N/A
4784dcbb-64e5-5823-8943-2416f48b6fee | button | Enclosed break, Hermetically sealed, Encapsulated and/or flameproof components are undamaged | YES, N/A
95cb880f-6ea1-5c80-880f-c213c6ef0d4c | button | Restricted breathing enclosure is satisfactory and test port, if fitted, is functional (Type nR only) | YES, N/A
29b51da3-b3cc-516f-87d4-b5af24cb798a | button | Test port, if fited, is functional - (type "nR"only) | YES, N/A
ba95937d-469f-5333-8ed6-79beea3e52b0 | button | Breathing operation is satisfactory (Type nR only) | YES, N/A
a6d1a3dd-1610-5684-95aa-a347020275fb | button | Breathing and draining devices are satisfactory, and operating effectively | YES, N/A
1291d045-7f1a-5f89-86be-864178481258 | button | Type of cable is appropriate is adequately supported and undamaged | YES, N/A
e6880e5b-bc16-5ba4-ad22-0383959f0692 | button | Sealing of trunking, ducts, pipes and/or conduits is satisfactory | YES, N/A
378c9424-7d03-5db5-8400-fb7c7bdd0f2c | button | Integrity of conduit system and interface with mixed system maintained | YES, N/A
594b36f4-ea82-53c7-946d-e23efc545167 | button | Earthing connections, including any supplementary earthing bonding connections are satisfactory | YES, N/A
b32714db-a68c-5297-9f95-cecc7545f70f | button | There is no evident damage or degradation that indicates that the fault loop impedance (TN system) or earthing resistance (IT system) is not satisfactory | YES, N/A
377eee22-bdbb-555a-8eee-e9de2a809482 | button | Automatic electrical protective devices are set correctly (auto reset not possible) and operate within permitted limits | YES, N/A
2bc47735-89d9-5746-898a-c3642c5c602f | button | Specific conditions of use (if applicable) are complied with | YES, N/A
e54a5404-6b9a-5e94-a244-e84f312eebdd | button | Cables not in use are correctly terminated | YES, N/A
c093c501-aa0a-57c9-8b45-0fd83c6d8cff | button | Variable voltage/frequency installation complies with documentation | YES, N/A
e38a3c3a-bb30-547a-b154-6b20de6a40a2 | button | Equipment is adequately protected against corrosion, weather, vibration and other adverse factors | YES, N/A
960db80e-f395-5c4c-ac23-d943b06fd38b | button | No undue accumulation of dust and dirt | YES, N/A
87904318-bbdd-5acd-88c3-5c932a5f6596 | button | All equipment housings are clean and dry | YES, N/A
8aed1404-99e6-407c-861a-94e457422d62 | checkpoint | Lighting
c6a2c878-4b20-5979-b96d-52130c0632b6 | button | Fluorescent lamps are not indicating EOL effects | YES, N/A
c779e80d-7226-5474-bc77-bf0a5e2f2742 | button | HID Lamps are not indicating EOL effects | YES, N/A
d736f228-f1fa-5c6d-8e16-cb56d2b8f988 | button | Lamp type, rating, pin configuration and position are correct | YES, N/A
ea25eb8a-f326-4a53-9ee4-d991c71acf17 | checkpoint | Motors
b1fecbe9-005b-5968-9761-45fd483f12e2 | button | Motor fans have sufficient clearance to the enclosure and or covers, cooling systems are undamaged, motor foundations have no indentations or cracks | YES, N/A
61548e0c-77b0-5412-86d0-c1a1620a841d | button | The ventilation airflow is not impeded | YES, N/A
d6560d3a-87bb-509d-b176-875c78224f20 | button | Insulation resistance (IR) of the motor windings is satisfactory | YES, N/A
e40de3d0-c35a-40b1-b4f6-6c38ccaa94c1 | checkpoint | Installation Details
13c0e5e6-4c22-580e-a663-19190dcd6213 | note | 1.Glands, 2.Stopping Plug, 3. Adaptor, 4. Breather, 5.Terminal, 6. Associated equipment
511b31bb-51e6-5e72-94ec-21e7b6a73a36 | dropdown | Select Type from Numbers Above: | 1,2,3,4,5,6
51a00a41-86ae-50b1-9d19-85ad1245371d | dropdown | Select Quantity: | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20
db05c617-145d-5965-bb69-476654cfa096 | textbox | Model:
efc2a544-79d7-56b1-a7a4-26014323389b | textbox | Make:
2bde0f60-a550-59eb-8ba3-df53191adc08 | textbox | Protection type, Gas grp, T-class, IP, Certificate
caad3dbf-2d79-51fe-a0a5-88e6fdb57de1 | dropdown | Select Type from Numbers Above: | 1,2,3,4,5,6
a7dd2c74-9b3d-5404-b2a1-7461a3fdeed7 | dropdown | Select Quantity: | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20
6e570862-ca32-5231-bd07-7b3b6f5388c5 | textbox | Model:
0274661a-698d-5f29-929d-52643970105b | textbox | Make:
40a4952f-f416-52a3-9996-617f5a384729 | textbox | Protection type, Gas grp, T-class, IP, Certificate
773c011c-b35d-5acb-986d-79412fbe0523 | dropdown | Select Type from Numbers Above: | 1,2,3,4,5,6
fbe90beb-9def-529c-ac22-f3e0b2db30f0 | dropdown | Select Quantity: | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20
a0bb42ef-67d8-5f04-9599-53294c07f497 | textbox | Model:
3f8a89e8-b892-54d7-9923-73c85ea219ac | textbox | Make:
ee9ff99f-31f7-541f-9e15-c46ae791e76e | textbox | Notes
e3a71741-3ee1-5505-9638-0e8e1ad94f17 | textbox | Enter notes and Comments Below:
eac97585-1f23-49f8-9c71-123ce8e5f179 | signoff | Add signature from Inspector
4f49fe48-4995-4afe-94de-4eb6a69cbde6 | checklist | HAZARDOUS AREA INSPECTION SHEET Exp |  | HAZARDOUS AREA INSPECTION SHEET Exp
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
5a5281b1-5321-4e06-9970-fdbc667c779b | checkpoint | Details
cc27dcf8-467b-5c5f-8c16-408e37f6ee50 | textbox | Tag Number:
1e130eb1-afc7-593d-ba2a-60b59092f436 | textbox | Site:
eae655c6-8667-5ed0-8ffb-9658755d7e3a | textbox | Make:
7f06bae6-d9dd-5c5f-af03-5531ad912e8d | textbox | Model:
7335bfe0-a033-59f6-80dc-2fde534b5aef | textbox | Model:
91cd4f18-df55-5897-bab9-b1c73c9f0ac2 | textbox | Serial Number:
a0271ba5-690c-5173-8c29-4a36677fcf4b | textbox | Protection type (nameplate):
fee4a142-bdab-5192-ba9d-bfaeb3a31b22 | textbox | Protection Type (as installed):
3b78681f-8486-539c-951a-337c4e5e6ced | textbox | Device Type:
9915c27b-a665-57ee-b310-72f341c4bd3f | textbox | Location:
2240bedf-08ea-58f3-a96d-62fc654b1505 | textbox | Location Zone:
3fc3e855-e61d-544d-9afb-cc38305f3741 | textbox | Location Dust Group:
2720d985-0dde-5465-bbee-e0d800ec85ed | textbox | Location Temp Class:
30dcf36d-37b2-5558-97d7-c984257fd723 | textbox | Access Requirements:
16b1855f-d2ef-594b-a532-89ccfb84b72b | textbox | HAC Drawing:
65fe9273-11d1-51c7-8875-806047dafcaf | textbox | Cause & Effects:
deaf9ffb-9e86-5e1f-8a5a-96a82b6f657b | textbox | Dust Group:
e171052f-f44f-5fe2-9c03-c712554a99a3 | textbox | Temp Class:
4e51cbac-96f7-5e13-88ea-6e9fa1fabd9d | textbox | IP Rating:
26a85b63-7cf2-5c17-807b-10c6dfb1aa17 | textbox | Cert #:
849a090c-31ec-5e59-a0a0-c5fd49c5a4ff | textbox | Cable #:
cdeba495-94a3-5481-9311-efe9a2929376 | textbox | Loop Drwg:
e78bf2f5-8848-5f28-a022-5456b2ab018a | textbox | P&ID Drwg:
2ee977ff-48a0-4e4c-b92c-9c94537599bd | checkpoint | General
6720dc2b-b38f-5c34-af21-e7166dc895b3 | button | Equipment is appropriate to the EPL /zone requirements of the location | YES, N/A
d3aee986-fb57-5f7f-9903-4e0265f79897 | button | Equipment group is correct | YES, N/A
c573e81d-dc47-5a46-8b50-b3326f52c974 | button | Equipment temperature class or surface temperature is correct | YES, N/A
2b7960f7-8832-5bd0-b7a9-7b27100c7dad | button | Equipment circuit identification is correct | YES, N/A
c3440fdf-4ba8-53be-a7a0-ce13086b3d18 | button | Equipment circuit identification is available | YES, N/A
ca81012f-5c53-5815-a476-2176c04aba8f | button | Enclosure, glasses and glass to metal sealing gaskets and or compounds are satisfactory | YES, N/A
ddfdd27d-c74f-56e7-abe9-05d07bdf78aa | button | There is no evident damage or unauthorised modifications | YES, N/A
9a16ba92-2b30-54b9-95ea-b41852d1b58f | button | Lamp type, rating, and position are correct | YES, N/A
c36c2fad-96af-45ee-ac19-c22daf18770e | checkpoint | Installation
5851c14a-89be-580d-8a93-e167e4d825c8 | button | Type of cable is appropriate, is adequately supported , and undamaged | YES, N/A
9de0596b-346f-58bf-b22c-3fbf5ce7f7f9 | button | Earthing connections, including any supplementary earthing bonding connections are satisfactory | YES, N/A
856a596f-a567-539e-9ce4-78a08e37df69 | button | There is no evident damage or degradation that indicates that the fault loop impedance (TN systems) or earthing resistance (IT systems) is not satisfactory | YES, N/A
1323b960-9dc9-5525-9930-7ad1ad248f7c | button | Automatic electrical protective devices are set correctly and operate within permitted limits | YES, N/A
18b084ef-41c6-5679-a8d4-aaba76269893 | button | Protective gas inlet temperature is below maximum specified | YES, N/A
182d9639-c3ec-5997-91ef-574fe5e470b6 | button | Ducts, pipes, and enclosures are in good condition | YES, N/A
4f781a5a-669e-541b-bfcf-b3d13ef088e4 | button | Protectiive gas is substantially free from contaminants | YES, N/A
e56e86ef-495c-5aa3-9434-0f7e8be07516 | button | Protective gas pressure and/or flow is adequate | YES, N/A
fa2fafbb-b782-5d3a-997d-090f415f08da | button | Pressure and/or flow indicators, alarms and interlocks function correctly | YES, N/A
0dc20bf7-9bdf-5329-a0ed-aad1f983cb54 | button | Conditions of spark and particle barriers of ducts for exhausting the gas in hazardous area are satisfactory | YES, N/A
6ad5b052-d5f5-5802-a49a-298bc6ccad72 | button | Specific conditions of use (if applicable) are complied with | YES, N/A
e6c1be67-648c-4f28-afdb-e44d765bddd7 | checkpoint | Environment
2ac27b7f-4108-54c6-9fcb-0ca947dc4f9e | button | Equipment is adequately protected against corrosion, weather, vibration and other adverse factors | YES, N/A
10c66a26-b03c-56f0-8cd1-c583cff8d14b | button | No undue accumulation of dust and dirt | YES, N/A
d6ee3613-18db-4a7b-8565-1f00d23ebfd2 | checkpoint | Installation Details
3a8efcbc-af38-5247-bcd6-6faf529cee0f | note | 1.Glands, 2.Stopping Plug, 3. Adaptor, 4. Breather, 5.Terminal, 6. Associated equipment
075e97ca-4e75-583a-a595-97f8c6e9032a | dropdown | Select Type from Numbers Above: | 1,2,3,4,5,6
65c86307-dae8-592b-8bfa-46be922bfddc | dropdown | Select Quantity: | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20
5c45b9fc-299c-5e21-b590-6befdf0ad963 | textbox | Model:
5fb81457-87f2-5956-a950-4a050f7c1c91 | textbox | Make:
eab3a432-6c54-5740-b753-b800d3cb4250 | textbox | Protection type, Gas grp, T-class, IP, Certificate
f9e3ebe9-1452-54f3-a8d7-1e507327b873 | dropdown | Select Type from Numbers Above: | 1,2,3,4,5,6
51127deb-9353-5ec7-852f-25b04c22e815 | dropdown | Select Quantity: | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20
894143dc-157a-5891-8a82-e46f03b3876c | textbox | Model:
ea5446b0-c91c-5ed7-92bb-4fecf11e4cfb | textbox | Make:
064ed709-91ca-5edc-b448-c2beca27bff5 | textbox | Protection type, Gas grp, T-class, IP, Certificate
591248c1-a8d9-5f7c-9501-e05d01cde5f5 | dropdown | Select Type from Numbers Above: | 1,2,3,4,5,6
055897bd-8603-5cb3-920b-9babfc65bf4d | dropdown | Select Quantity: | 1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20
73df9245-de90-5548-a6ec-6eeecdc3c076 | textbox | Model:
24ae1cbd-a1fe-5301-86f7-5c5085f49614 | textbox | Make:
0f96e60a-af12-5c89-ac73-c9e912013454 | textbox | Notes
887c8bf0-e3fa-50c2-93f6-57fad6df84e5 | textbox | Enter notes and Comments Below:
86e3d926-f30e-4e97-9559-0fdde2bc550a | signoff | Add signature from Inspector
22492a47-d8b8-4ca4-be1c-b6a80625d3c0 | checklist | High Voltage Cable - Drum Test |  | High Voltage Cable - Drum Test
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
1ffe7bce-28e8-4891-845a-add04146891c | checkpoint | HV Cable Install
8bc6b67a-8c9c-5993-8127-50655e43995d | date
a7c9e50d-498d-5e33-9665-c6adaa9594fd | dropdown | Cable Voltage | 11kV,33kV
bd13a968-f02e-5186-bfcc-85f00c6df9aa | button | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Yes,N/A
d277bd56-8f60-4ee9-bf30-1c8efa998591 | checkpoint-no-value | Cable legth:
30720890-5262-5611-9e62-79c477bad8ce | button | Cable undamaged - Visual inspection | Yes,N/A
de05778f-261f-5e76-abbe-541e55e62cdc | textbox | Temperature:
7b7eca24-97c8-47e3-b149-265a7a774d8c | checkpoint | Electrical Tests
d9d6b8bb-d3fb-5df0-8ce1-6a08e8f05054 | note | Testing for the below should be done at 5kV for 10 minutes. If result is below 1.25GΩ this indicates a low test and will need to be re tested. A brand new cable should have a result above 2GΩ. Please insert photo of test results. | Testing for the below should be done at 5kV for 10 minutes. If result is below 1.25GΩ this indicates a low test and will need to be re tested. A brand new cable should have a result above 2GΩ. Please insert photo of test results.
56649a51-4a91-5f4d-8daa-48e1709111cd | textbox | Core to screen
bef7e11a-da21-4fa0-ac61-e02e2f8574f4 | checkpoint-no-value | Sheath Integrity Test
61813862-e5f7-59f2-a210-6eee85a71d7d | textbox | Test Duration:
9c2b3893-8706-5752-b859-c85990358257 | textbox | Test Voltage:
811044f8-6fcf-588b-89fe-169acda67e51 | textbox | Result (GΩ):
a16753d8-54f7-415f-9edd-77f3bdd6c389 | checkpoint-no-value | Test Equipment Details
95d7eff1-84b6-5340-ac8e-5025d5020b35 | textbox | Make
5b1aff2d-f72c-5022-b092-dd3c5b548d01 | textbox | Model
bf3d3542-c9df-528a-be48-683e32bf28d8 | textbox | Serial No
e80f496d-2d51-5d0d-900a-45fd66991f60 | textbox | Calibration Expiry Date
286475cb-9fce-41be-8c0c-0944817d5089 | checkpoint-no-value | Installer Sign-off
bfadb6cc-74ec-49a5-b056-95169daf10c5 | signoff | Installed by:
33eeb655-8fc5-4587-8848-ab5f145d0d04 | checklist | ITR-E-01 General Electrical Equipment |  | ITR-E-01 General Electrical Equipment
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
d139f885-6b04-4b13-bf57-d43946c82785 | checkpoint | General Electrical Equipment
f24a6d46-064d-5007-89b6-08e5a6aa5b81 | textbox | Type of Electrical Equipment:
526a1dc9-2115-5588-901c-e088f357a407 | textbox | Make, Model, Manufacturer, Serial No. (if applicable):
a80bedce-6442-558f-8500-f31bff171804 | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
851d3207-0dfb-553b-8bd5-2f03ff90f6fd | button | No mechanical damage and paintwork in good condition. | Yes,N/A
00affb01-bea6-54e3-845e-a0095ff5c0a6 | button | Installation is clean and tidy | Yes,N/A
dcd02f0c-34e6-51d0-97bb-5c8c4b93024d | button | Mounting arrangement correct | Yes,N/A
7e02d73a-f7df-5bc8-96b2-ea31007f7d98 | button | All internal cabling and wiring correctly installed and labelled. | Yes,N/A
4bcd63bd-b13b-5193-ad6b-82b095c805e8 | button | External cabling is correctly installed and labelled. | Yes,N/A
ddec469b-3dcb-59c9-a0b6-27fe97260a6f | button | Check that Equipment is correctly earthed. | Yes,N/A
4125063c-912b-52fd-9dea-349915d1fdc7 | button | Check gland, plate, frame & door earth continuity | Yes,N/A
8615a7f4-0844-5b7a-823a-03af29f1e0f1 | button | All spare entries blanked off with correct plugs. | Yes,N/A
e8d1c308-0754-5074-937b-ac6399de82f4 | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
ab993f4d-92d7-5c37-b373-a94bcbce4bec | button | Conforms to Specifications and Drawings. | Yes,N/A
2f16a4a4-09bc-523e-bf3f-54b4cf5f8161 | button | As-builts complete. | Yes,N/A
62ecc20d-eb0b-43c8-8df6-3b4431f83c74 | checkpoint | Electrical Checks
eb13e9e1-28e4-5083-bed2-08682b9fe200 | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other. |  |  |  | MegaOhms
9e017e75-cd6e-4daf-b69c-9ab86497457f | signoff | Installed by:
dce2442e-473b-45e1-b4f4-f1db22abc700 | checklist | ITR-E-02A Conduit/Ducting Below Ground |  | ITR-E-02A Conduit/Ducting Below Ground
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
baa5c3a5-81ba-47c9-8796-77769f0b1520 | checkpoint | Conduit/Ducting Installation Below Ground
a3f53098-de4a-5654-ad6d-b5cd12693d12 | button | Check equipment details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
c33f3bf6-cd6f-5bd7-a4a4-9f5378af6039 | button | Check conduit cable enclosure installation is as-per design, layout drawings and specifications. | Yes,N/A
93b967f6-04f1-5e41-8870-d010f912e4f6 | button | Check conduit has been installed to the correct depth, "cable below" tape or Magslab installed. | Yes,N/A
097b091d-a31d-512e-b3a9-581c562bc8d9 | button | Confirm that there are no obstructions, and that the installation will be accessible for maintenance. | Yes,N/A
8e8d50ff-7db6-5a9d-bd03-4576cebad1e5 | button | Check all fixings are tight and secure. | Yes,N/A
fb2ff21c-612b-55e6-b6c6-c0b7697b63b2 | button | Check bends do not exceed the maximum cable bend radius. | Yes,N/A
21a8957a-0281-594e-a72b-985b277e7c70 | button | As-builts complete. | Yes,N/A
9fd3e0da-f083-46d4-a37e-b9d8c3ae83e9 | signoff | Installed by:
c5367bd5-57ee-430c-bc37-3b44c8c48918 | checklist | ITR-E-02B Cable Supports Above Ground |  | ITR-E-02B Cable Supports Above Ground
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
51b0cdf7-e7f7-4e01-a1e2-97de133014d8 | checkpoint | Cable Supports Above Ground
0ff06d0f-3927-5dec-bd26-a04d85b9fc86 | button | Verify cable support has been installed as per relevant drawings, and is correct size and type. | Yes,N/A
7d16f92d-00ba-5dd2-bd5e-43023b4d6fe2 | button | Check all machined parts cut or drilled have no rough edges, have been de-burred & protected by cold galvanising to restore the previous protection. | Yes,N/A
305f9fff-80a4-535c-9f43-ca015b0e3f58 | button | All covers fitted if applicable. | Yes,N/A
2a9a9324-f2b0-5a64-9670-d9609bc59747 | button | Check cable support structures are adequately fixed and present no hazard to personnel. | Yes,N/A
9d0fe764-f105-51b9-93d5-5990a515f1b9 | button | Welded support brackets have been wire-brushed and painted to completion. | Yes,N/A
eb247cf2-5b63-53da-9806-24f61d632b70 | button | Splice plates, barriers, earthing system secure. | Yes,N/A
5398c8e4-0817-50d5-b80b-fa09616c94e3 | button | Trays / ladders, supports, brackets not interfering with other disciplines. | Yes,N/A
1ac061ad-b2d0-5d21-8d51-306c38ca001a | button | Check bends do not exceed the maximum cable bending radius. | Yes,N/A
bec04255-7273-546e-9b5f-11f086c19b81 | button | Cables have adequate mechanical protection as and where required. | Yes,N/A
96ee41e1-e167-5c58-8cd5-5a29b8555258 | button | Inspect for system rigidity, and check levels to correct plane. | Yes,N/A
ed83f13f-1928-58e2-8b76-3d21c77bdd2b | button | Earth bonding straps have been fitted to any sections that are split, hinged or flexible. | Yes,N/A
63fc5170-920e-5151-8e27-50535016068b | button | Tray bonded to structure at correct locations. | Yes,N/A
bd2871b7-90a8-5bc1-b72f-4719488e3858 | button | Earth bonding continuity tested – record result: | Yes,N/A
0f0f5eea-31fa-5827-8dd3-c5498217cd68 | button | As-builts complete. | Yes,N/A
942aa3a9-43c6-4d97-a50b-7b0c47b3c202 | signoff | Installed by:
80d3958b-a705-48a5-bfe9-bb7e7bcd591d | checklist | ITR-E-02C Cable Transits |  | ITR-E-02C Cable Transits
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
12d31784-91c5-44ee-b2e8-b90e9064fc94 | checkpoint | Cable Transits
b6c22cde-585b-5fb9-9677-546686ea9a96 | button | Transit frame installed as per drawings. | Yes,N/A
7f1d569b-d335-539a-a498-4c9133984e01 | button | Transit frame identification marked correctly and visible. | Yes,N/A
bb40e444-f59b-5bd1-949c-ffe285a7ed27 | button | Frame correctly packed with correct sized blocks and infills. | Yes,N/A
8a676f04-edc1-5b8b-be2a-2f6e671c9be3 | button | Correct stay plates fitted (non-ferrous for single core power cables.) | Yes,N/A
604af95a-67d9-5d4d-a305-e05d4d50ca0f | button | Rated insulation installed to transit (where required.) | Yes,N/A
7a009815-5646-5afb-98b2-227cae9c1207 | button | Cables entering and leaving transits adequately supported and protected. | Yes,N/A
fb9277f2-304f-5318-ad81-608e26af3d4a | button | Cables pass through frames without strain on blocks. | Yes,N/A
7f2a61b1-0609-57c9-b87b-f95b49e48223 | button | All cables identified on both sides of transit and visible. | Yes,N/A
d03997d8-5f3f-5228-ad48-f392a02e749f | button | As-builts complete. | Yes,N/A
dbca1073-d4f6-4823-b1e8-920f19ac2a5a | signoff | Installed by:
bf33efd7-7fdc-4ee8-ad94-85572ce1fad2 | checklist | ITR-E-03 Entec - Distribution Board Installation |  | ITR-E-03 Entec - Distribution Board Installation
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
caf98d32-47eb-406b-871b-f750aef6247b | checkpoint | Distribution Board Installation
f015421c-60bb-5bab-a3e7-a2964aad1fab | button | Inspect for mechanical damage from freight and handling | Yes,N/A
487ac857-464e-5b51-86cd-3a44cd879f44 | button | Check tag number is in accordance with Electrical Equipment List, Document No. and nameplate details correct. | Yes,N/A
f5c5967c-021d-5d79-9dde-2d1ff4712787 | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
628017af-39cc-54f5-884b-6dfdaea8e1fa | button | Check type, size and number of breakers is correct as per drawings | Yes,N/A
bfb1e5bd-15b7-514d-b598-7becdff5382d | button | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order. | Yes,N/A
bb796a9f-d2fe-5543-a811-b2dd12d64c4b | button | Confirm main isolator operates with associated switches and auxiliaries | Yes,N/A
6911bbff-0edd-5ff5-86a8-da3f65526ffc | button | Check equipment panel external and internal earthing connections are securely fitted and properly terminated on the cabinet protective earth bar. | Yes,N/A
00dee7bf-301b-571b-8405-702bfd85e681 | button | Check DB, sub circuits, DB Legend and internal cables correctly labelled. As Built drawings complete | Yes,N/A
d703aedf-5175-5b86-bc9e-16d4fcda3a54 | button | Check sealing of all cable penetration (where applicable). | Yes,N/A
496c9f9e-bc22-51c0-b8d9-5733598836fe | button | Active, Neutral and Earth bar properly identified and labelled | Yes,N/A
d422d809-4cdd-5a52-ae02-f5cf50125a62 | button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
9c082b80-594f-4e90-94b2-76cf1706e8cc | checkpoint | Test Results
a9602e32-074f-5d03-82fd-e2a68033cf02 | textbox | Insulation Resistance (Eg. P-P, P-N, P-E, N-E) |  |  |  | MegaOhms
8642df89-b8eb-5343-8059-efb9362fc8f9 | textbox | Earth Continuity |  |  |  | Ohms
e3e39187-6914-509f-a78a-69178b590797 | textbox | Earth Bond |  |  |  | Ohms
c72bd529-ccc2-5f86-b01f-bb1e63cebd38 | textbox | Fault Loop Impedance, PSSC.
b065b3c4-4820-5d69-b5b5-922b3ee1b034 | textbox | RCD Test results (1/2x I, 1x I, 5x I)
92c9acaa-6cda-5b6a-a3db-a702d16ae3b7 | textbox | Voltage and Phase Rotation
773bb8bf-b90e-5d26-8a45-a959c17269a8 | button | As-builts complete. | Yes,N/A
7d8a6516-3026-4763-a997-c0609824d887 | signoff | Installed by:
8e6b9c6f-617e-4d4b-8c90-5d48dff979ae | checklist | ITR-E-05 - Low Voltage Cable |  | ITR-E-05 - Low Voltage Cable
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
2f5ad445-c40c-4244-b687-84b3e699bb14 | checkpoint | Low Voltage Cable
c58d4d4a-3e99-59b2-b5da-82bca7220fb3 | textbox | Record test results: Insulation Resistance and Continuity
156bbd6c-8abf-51ca-8897-b7e7d186db1d | button | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Yes,N/A
bc027436-e8e4-50c5-828a-241d7e247b87 | button | Check dressing / cleating, cable undamaged | Yes,N/A
96e157b5-49aa-5fc6-be49-ce3119b8271d | button | Check cable cores correctly identified and labelled. | Yes,N/A
e4710480-8414-5c50-ab42-d48d32ebf32a | button | Cable terminated with correct lugs and crimped with the correct die. | Yes,N/A
52aa32ef-252f-54ee-80d1-72cbddfde3aa | button | Check Armour / Screen correctly made off. | Yes,N/A
cf28a489-676c-56b3-99fb-22555742179e | button | Check armour continuity / earthing is maintained by the correct use of serrated washers and / or earth tags (if applicable) | Yes,N/A
14875044-d55f-52f4-b072-68f6446107ff | button | Glanding / Locknuts correctly installed. | Yes,N/A
add83237-0b54-56dd-8fe8-2d015520732c | textbox | Gland type - from: |  |  | Haz. Area Rating
59639503-006f-5d1d-aaf1-2a0d29dffa48 | textbox | Haz. Area Cert Details.
2b1b4665-1d0f-5c53-9112-df825491aa27 | textbox | Gland type - to: |  |  | Haz. Area Rating
ec1216fd-bca8-560f-bbb6-b77b8b53f0fb | textbox | Haz. Area Cert Details.
75052bdf-97d3-4e40-8308-f190bcdf67ea | checkpoint | Electrical Checks
27be0295-fff4-5750-b0bc-d5a9f39f63a9 | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
3d2e034d-4031-4dd8-801a-6c67bc650b6a | signoff | Installed by:
c02734ea-0792-4ebd-a79a-3552c121d80f | checklist | ITR-E-06 Control Panel |  | ITR-E-06 Control Panel
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
7dd21e7b-e18b-4e99-82f5-270cd5b72450 | checkpoint | Control Panel
e22e4e0c-85b7-52bb-927e-accff231a3bb | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
277295f9-88e3-5f43-ad90-fefd99161849 | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
f2b72ebd-e39e-5bba-a3cd-2418daf6ff6a | button | Check holding down/mounting arrangement is correct. | Yes,N/A
3c15f2d9-ab55-5aa3-b892-d161bb288fb2 | button | Check for mechanical damage. | Yes,N/A
095aec2d-0071-5d3a-877a-2e3098b7c5ba | button | Check tightness of circuit connections. | Yes,N/A
0f517158-a955-5f09-bfa4-ea02380ec93d | button | All internal cabling and wiring is correctly numbered, colour coded and terminated | Yes,N/A
9881164c-9de5-54bc-895d-5582de684ce6 | button | Ammeter scale and current transformer correct. | Yes,N/A
ebb5cd6e-1af4-518b-85fe-7c961d587a1d | button | Check internals for cleanliness. | Yes,N/A
6e1c1811-1e48-5cef-8a04-65ab8aa36a73 | button | Check manual operation of selector switches, MCB, push buttons, etc. | Yes,N/A
5e13febe-f959-576f-9458-2edba4230f92 | button | Incoming cables correctly glanded, terminated and labelled. Unused entries sealed with correct plug | Yes,N/A
fae30941-0452-580e-bd1c-3f14c6787349 | button | Heaters correctly installed. | Yes,N/A
1c2c8b9b-08e5-5436-885f-9c8db97983e6 | button | Fuse rating correct. | Yes,N/A
836fe62e-6247-57c8-9b76-a803e7df8a96 | button | As-builts complete. | Yes,N/A
3f1bfa22-9a18-4658-8db5-0fc8391bc2c1 | checkpoint | Electrical Checks
5e1fcf0a-178f-5227-ae91-c04ab5049eae | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
ca4705cd-8031-4169-8dc2-f1886281bda7 | signoff | Installed by:
0eb01682-f406-4118-836a-f8b45e7a7bd3 | checklist | ITR-E-07 - Junction Box |  | ITR-E-07 - Junction Box
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
5e7c86f1-3cb2-4011-9302-25ab438d2627 | checkpoint | Junction Box
a2f145ed-b723-5db6-a0c1-0d1ae84eadc4 | button | Check Equipment and Nameplate details are correct in accordance with the data sheet and equipment schedule | Yes,N/A
22165f4c-4ae2-5418-93e7-023c90d230c2 | button | Check mechanical damage | Yes,N/A
e46008e8-1369-50f2-a2ad-1754a4761815 | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
9dd67505-4e59-5256-9754-5dbdbda4e0b7 | button | Earthing installed correctly and as per drawing | Yes,N/A
4dfb6921-76df-5fd9-b312-48e8be4e7cec | button | All internal cabling and wiring correct, (including segregation between ELV and LV, IS and Non IS circuits if applicable) | Yes,N/A
47813101-1c3c-5d6d-a1c5-04148fe67bf0 | button | Incoming cables glanded correctly, empty holes plugged using correct plug for area classification to maintain IP rating | Yes,N/A
114a00d0-ceb3-51df-96aa-577805cfcaa3 | button | Check all Cables & Cores are correctly identified | Yes,N/A
9a039a8e-761b-5ee0-a21b-baf6e29c57b5 | button | Check internals for cleanliness | Yes,N/A
701f9bbd-30c9-527b-b504-152f22118091 | button | Check manual operation of selector switch, MCB, push button, etc | Yes,N/A
2b4ca514-e2ec-5333-a588-fe5b81a6f7ba | button | Check MCB/Fuse ratings (If applicable) | Yes,N/A
bd6e9820-818a-412b-b178-6f193e1cd3a9 | checkpoint | Tests
7829a2cf-f522-54c6-a922-02ebf3d26e44 | textbox | Record earth bar resistance to earth bond
d52a9407-b5c5-5005-94fa-294257bac855 | textbox | All other relevant tests:
403506e1-e490-5861-8454-63364b7bdf93 | button | As-builts complete. | Yes,N/A
0f784c87-e73c-4a5a-adbb-e7327f34776a | signoff | Installed by:
2854bd88-ca5c-4f31-bd00-8845bed5babb | checklist | ITR-E-08 Heat Tracing Circuit |  | ITR-E-08 Heat Tracing Circuit
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
fd3b2d7b-803c-45e5-b6e3-93297f6b4504 | checkpoint | Heat Tracing Circuit
8cf6586a-805f-5119-8a4a-21ced91da719 | button | Circuit installed, connected & identified according to design drawings. | Yes,N/A
67711521-b5dd-51bd-b5e4-19ac65099dbf | button | End caps and connection kits correctly installed. | Yes,N/A
67477c64-570a-5f14-83e7-18c21018b895 | button | All junction boxes properly supported, and all cables protected against sharp edges. | Yes,N/A
d8663b86-3943-58f2-90fb-bd5dcf83e1bc | button | Cable termination and glanding at all junction boxes correct. | Yes,N/A
3676c4c2-2f6b-5d4c-af0f-d5535a7bc157 | button | All spare entries blanked off correctly. | Yes,N/A
b1f35cff-5531-5a77-a1b2-e57c978388e2 | textbox | IR test: Phase - Earth, Phase - Neutral
639d0575-4f8a-5d2b-bde8-c8498ec1623a | button | Equipment certification meets the area classification requirements. | Yes,N/A
1bc98040-51bb-5bbb-b190-8a7f437777d1 | button | Confirm warning labels are fixed on outside of pipe lagging | Yes,N/A
f3f8f40d-17aa-5f46-857d-099bf52573c2 | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
7257c0ec-837b-539a-8227-08f039c5f866 | button | As-builts complete. | Yes,N/A
a47c07cd-cac9-460a-9eee-ca49c3c1cc76 | checkpoint | Electrical tests
0eca3484-5828-5511-8882-87029f5bd5d5 | textbox | Insulation Resistance: Phase - Earth
fce475ea-571d-57d4-9ca2-1503ad84e60d | textbox | Insulation Resistance: Phase - Neutral
9a67b744-c537-496c-863a-fd3a149c2565 | signoff | Installed by:
0c454dbf-9750-4207-90dd-150c63a4a947 | checklist | ITR-E-09 Electrical Switch Rooms |  | ITR-E-09 Electrical Switch Rooms
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
812ec408-d112-4df0-9856-8ba137cffb3e | checkpoint | Electrical Switchroom
8cc332a5-0fa5-58b3-a5e1-2f3f4f455d39 | button | Ensure all equipment is installed in accordance with layout drawings and equipment schedule. | Yes,N/A
713c36d6-2ca0-504c-bba0-b36af1d88b0f | button | Ensure all equipment is installed as per manufacturers instructions. | Yes,N/A
ad0c857c-7bfb-5727-844b-ac31f044ed4a | button | Ensure there is no visible damage to installed equipment. | Yes,N/A
7d4d7738-721c-5a0b-bab8-bd8cc8761b07 | button | Confirm equipment panel has adequate air ventilation, as appropriate to its internal heat generation. | Yes,N/A
3564835e-6bb2-5a67-865f-ab94d0a6baf5 | button | Confirm any slide-in cards / modules are firmly fitted to the equipment panel and properly identified. | Yes,N/A
4aa0a1de-b88b-5bdc-bcef-83e6bcf95abe | button | Check equipment panel external earthing connections are securely fitted to and properly terminated on the cabinet protective earth bar. | Yes,N/A
8e7595d5-3eb4-5022-8ae6-349201d06695 | button | Where fitted, check instrument earth connections are securely fitted and properly terminated on the cabinet instrument earth bar. | Yes,N/A
003947d8-154f-5e29-9b00-839dcc3f5379 | button | Ensure any AC power connection(s) is securely fitted / identified different power sources and potentials and cabled to the appropriate Power Distribution Panel circuit breaker(s). | Yes,N/A
860c2e0f-1d7f-52ae-9bbc-6ba3522dc2e4 | button | Check sealing of all cable penetration (where applicable). | Yes,N/A
76a89181-4e17-5625-9878-ed4a603363c7 | button | Ensure all signal cables, including any RF coaxial cables, are correctly identified, and securely fitted to the equipment panel. | Yes,N/A
d948cbb3-2bdf-5d4a-8e9b-31eab9ede572 | button | Where fitted ensure panel sliding rails are operating smoothly and without risk of damage to external cables and connectors. Check alignment of false floor after panel installation (where applicable). | Yes,N/A
5ada87b2-3bb2-5237-a994-38e12832dd09 | button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
583d8273-d856-5bcf-a5ab-86a0cee181c3 | button | Equipment IP, Ex ratings correct. Check tightness for all circuit connections | Yes,N/A
f55e1351-2cb1-5589-9944-ac6d37553c3f | button | All internal cables and wiring is correctly numbered, colour coded and terminated | Yes,N/A
b5d19c4d-fc08-52e7-b244-23168e16cc60 | button | Check internals for cleanliness | Yes,N/A
ea2445f3-8345-5b8a-99f9-2af3635d5075 | button | Relays Metering and Protection ratings are correct as per design | Yes,N/A
2e705c39-8686-5bfd-9bda-1849a2d9f524 | button | As-builts complete | Yes,N/A
0e742957-1685-4137-a7ee-efe10b43c2cc | signoff | Installed by:
eb1f0dc3-6d8a-4528-b995-692460175685 | checklist | ITR-E-10 Electrical Equipment Package |  | ITR-E-10 Electrical Equipment Package
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
26430df5-1930-4b7e-abe8-99c68981d086 | checkpoint | Electrical Equipment Package
10c398a2-d13b-56a8-9e69-e3c08abbb33e | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
63108cb3-aa8f-50e5-9131-480874b0dfa3 | button | Check equipment is correctly rated for the area. | Yes,N/A
992215cf-d073-5e33-b083-8512a8ea17c8 | button | Check if package is complete with all accessories. | Yes,N/A
d459e985-ea3e-5507-b722-0cbfd5978b27 | button | No mechanical damage and paintwork in good condition. | Yes,N/A
68fee541-fa09-5337-987d-3dab075f3a8f | button | All transportation supports, stops and fastenings removed. | Yes,N/A
63a09c22-588c-5edb-8e1a-12935bfd25af | button | Package fixing down bolts/shims/washers installed and tensioned. | Yes,N/A
259b1420-2387-58b4-add7-6ac94edc9396 | button | Check package is installed on a level plane. | Yes,N/A
5583e30e-d33b-5640-8f42-cfc247ab27c8 | button | External cabling (if required) correctly installed. | Yes,N/A
a6986835-241e-5ae6-a1f8-e599517c244f | button | Internal equipment installed and all tests complete and accepted. | Yes,N/A
56d3d08b-405a-50e1-9cd9-9c3ab8bc0d6e | button | Verify package using vendor and/or project P&IDs. | Yes,N/A
feb625aa-f430-504b-b5e0-27248080fdac | button | Check that equipment is correctly earthed. | Yes,N/A
e4ad2a2c-df31-52b5-8c52-0d4d88398fa3 | button | As-Built drawings completed | Yes,N/A
2b19fbf1-cf5e-584c-8a88-a9ade6311cd0 | textbox | Test and confirm the earth resistance between equipment and local earth system is <1.0 Ohm |  |  |  | Ohm
2eebda35-7ba5-4be6-8afb-d36bea458cb1 | signoff | Installed by:
f9fe90f2-a208-4363-847f-c8b9d3cc5106 | checklist | ITR-E-11 Generator Package (LV) |  | ITR-E-11 Generator Package (LV)
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
61e18106-1fdd-4654-85e3-2bc9b016fccc | checkpoint | Generator Package (LV)
7ee98ff0-4c98-5682-89ee-74715b037c3f | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
6d9c42d4-b497-5a4d-8918-480b4557c99d | button | No mechanical damage and paintwork in good condition. | Yes,N/A
d562ee2c-3538-5e83-9af6-58378304ea3d | button | Check terminal boxes and glanding correct. | Yes,N/A
1abd9208-b4a0-5e3d-9ab2-3838296b0654 | button | Instruments correctly installed. | Yes,N/A
5037aee0-2ba8-5aa9-8804-5e87de4a4c88 | button | Heaters correctly installed. | Yes,N/A
3dd63d68-92a8-520f-adc0-eb2d1e649756 | button | Check unit for cleanliness. | Yes,N/A
6f825a3d-1c1b-5ad4-a0ac-112dd652cf48 | button | Check manual operation of selector switches, MCB, push buttons etc. | Yes,N/A
1deccbd9-87ca-56a5-99a0-51177a232337 | button | External cabling correctly installed. | Yes,N/A
ac2c3c52-ec07-593e-bf72-37b000e37e69 | button | Protection of live parts adequate. | Yes,N/A
4bec6530-e3c0-5120-864a-b6d160fc3cec | button | Main terminal box complete and terminations correct torque. | Yes,N/A
2ec7c859-40f4-5743-a2bc-e02ffb20c48e | button | Ensure direction of rotation is clearly marked. | Yes,N/A
e9c5ea46-dd93-53d3-a916-c4b713d72647 | button | Check gasket and seals are not damaged. | Yes,N/A
c59200dc-e9f1-5819-9358-09796dc48350 | button | Unused cable entries are correctly sealed. | Yes,N/A
e5a795b0-f5f1-5d87-94f1-9452f5b71869 | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
fbea4f4e-da96-5a3a-be21-59116eec06b4 | button | As-builts complete | Yes,N/A
c3c96b25-9cc6-4e11-8d88-d6cbcaf1ad44 | checkpoint | Electrical Checks
b5e7a400-01f4-5fc6-b581-6f332271361a | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
64d38cac-4b7f-590c-bffb-b3b48e8cdb2d | textbox | Heater circuit insulation resistance:
8f387beb-6c26-460b-a2e8-22fec3ebe881 | signoff | Installed by:
79b1c311-9734-4e06-b6b8-a03071d02204 | checklist | ITR-E-12 Electrical earthing |  | ITR-E-12 Electrical earthing
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
963491f5-16ba-4a4c-80ef-5f3f0eade886 | checkpoint | Earthing System
565f82de-bf50-5fbb-9b18-fc822d28b51d | textbox | Electrode Type:
6bb632d0-f36e-59db-87ad-265f703b4f8b | textbox | Electrode Length/Size:
2cf8c12e-5c14-5b83-a466-ad03a065d0af | textbox | Location of Electrodes:
3dcbfe74-28a6-592c-863c-6df57db7ee0d | textbox | Method of installing electrode:
e0aabd45-e4b3-599b-8cff-1de8747e8db2 | textbox | Method of attaching to electrode (E.g. Clamp, Cad Weld, Lug/Bolt):
52d4c870-75d0-5539-9e13-f2a56fd27746 | textbox | No. of electrodes:
67676f05-26b7-4eb1-871e-6ae28fe9a806 | checkpoint | General
0d4979d6-a84a-5c8f-9cf9-8f5f9295283e | button | Confirm earth grid layout, earth conductors/connections and number of earth electrodes is in accordance with drawings, drawings as-built | Yes,N/A
404f59f5-c9a4-541f-a28b-585b3104ace5 | button | Ensure that all metal work is earthed as required. | Yes,N/A
50c4c2f1-8a17-57f1-bb2e-37c2703f8e9a | button | Check welding of earth bosses and associated surface finish. | Yes,N/A
b3b45868-275c-56d8-9068-b7d047778f04 | button | Ensure that earth cables/conductors/electrodes have adequate mechanical protection i.e. conduits, tobys, kick-plates etc at points of high exposure. | Yes,N/A
f067b7e3-c599-5d85-ae91-fbdb6333f72d | button | Ensure that brazing or welding of all joints has been completed correctly. | Yes,N/A
2e6710ea-0a48-52f8-9a69-562614fb9924 | button | Ensure that adequate corrosion and weather protection has been installed around all connections, joints, lugs, cad (thermal) welds and earth bosses | Yes,N/A
e076c2ae-5005-5c14-a9cf-56f3cbf0c135 | button | All earth bosses and studs tight and fitted with shake proof washers and coated with protective coating. | Yes,N/A
56be7626-f798-51ed-9db6-6543d9d96fe7 | button | MEN Link installed: | Yes,N/A
6450751c-1b00-40a7-b4d1-413db37cbaa8 | checkpoint | Earthing Conductors
0263c6a9-de56-5f20-a80e-f373ff6cb706 | button | Check cable terminations/joints to ensure that all lugs/barrels have been crimped correctly. | Yes,N/A
a6453be3-4646-50ba-9229-53f8d66b6d5c | button | Check that all bi-metal connections have been performed correctly to manufacturer’s requirements. | Yes,N/A
1bf16bb6-5b4b-5b87-a5c7-039de680ccb0 | button | Ensure that the earth cables to the main earth electrodes are terminated at each end of the main earth bar. | Yes,N/A
8ffc6562-c26c-5393-8364-ce4d087e84a2 | button | Ensure that earth cable identification markings are in place. | Yes,N/A
fbbe3e60-16a7-56b0-ba6e-b3fcca1ead1a | button | Ensure that earth connections are not multi-coiled or ‘pig-tailed’ but are terminated as straight as possible. | Yes,N/A
6fcdeef6-4002-5963-8346-6692753da9a8 | button | Check earth bar fixings, mounting points and terminations are tight and secure and conform to project specification (if applicable) | Yes,N/A
c680d239-7b9f-4809-affc-97c18c0b2e39 | checkpoint | Test Results
2095a1f8-ee98-5ee8-a5f9-1113b88be300 | textbox | Earth continuity test results (Earth bar to Electrode, Grid, etc - please specify)
fec29192-41ee-561d-a1db-5a8633b0fa52 | textbox | 3-Wire earth test results (If applicable).
83162fea-7e46-5cad-88bd-4c19f5060687 | textbox | Earth grid test results (if applicable). (HV earth grid, LV earth grid, combined earth grids)
b760fbb8-ece3-568d-8f74-395d9897ce93 | button | As-builts complete | Yes,N/A
0c86c192-efe1-4681-86f8-71d7e60c9e43 | signoff | Installed by:
1cbbc953-43f4-4ac1-a785-506fe8cf2b24 | checklist | ITR-E-13 Motors |  | ITR-E-13 Motors
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
6e4532cf-3099-4be2-94e2-590c09582364 | checkpoint | Motors installation
61750882-4125-521b-b73c-b7051d3406dd | tickbox | Tag number, area classification, IP rating correct as per drawings and equipment schedule
e130c550-72c1-51f8-81b8-0219b954ace5 | button | Space heater | Yes,N/A
a559e828-7758-5db9-9d60-200ac0c46111 | textbox | Space heater specification (Power (Watts) and Voltage:)
34d1fd14-6726-42ad-aacd-31948501b13a | checkpoint | Nameplate details correct and in accordance with the data sheet
b97992de-183b-5143-a5b6-52cea09e05e3 | note | Upload clear photo of nameplate
da16705e-dabf-4188-b85b-f6356ce64d71 | checkpoint | Checklist items
711648ec-6edc-5299-ab2d-9686309b4661 | button | Equipment has been received in good condition and is the correct type as per the site drawings, specifications & data sheets | Yes,N/A
06c5534a-41e8-520d-b510-3224dd5b141d | button | Identification Tag and Rotation Plate correctly fitted | Yes,N/A
865238fb-7145-5f60-9f8d-9f9e2bb7be40 | button | Motor electrical coupling (Delta/Star) is correct. | Yes,N/A
7606fe02-d33d-5ae3-8cb4-62b2c335868d | button | Check for mechanical condition, air ducts and fan free of debris | Yes,N/A
60b81a0c-4625-53ec-a6ef-14f076c8786c | button | Correct glanding for area classification. | Yes,N/A
388db27f-efb4-5e44-8a12-2b41f84cc711 | button | Holding down bolts fitted correctly. | Yes,N/A
57f4a0f1-0a9f-592a-a7f3-3e108c273591 | button | Check bearing lubrication, free rotation with shaft uncoupled | Yes,N/A
1ac1fde7-7252-5a6d-bf77-c85724cb4eba | button | Cable(s) correctly terminated, labelled and colour identification | Yes,N/A
274fada2-247f-548b-bff8-8aae618ee11f | button | Terminations/connections torqued correctly to data sheets. | Yes,N/A
1d0db54f-2bc5-4db4-a768-1776a2e2b68e | checkpoint | Motor Installation Testing
e1da392d-f7db-5e38-84cb-6d9cab103b1c | textbox | LV Motor winding insulation resistance with supply cables disconnected; 1 minute test
c035618a-8630-5786-bbc5-c4f6dd08e27a | note | Insulation resistance U, V, W
a14001cc-8f70-529e-9c1b-9f34ba3b17f7 | textbox | LV Motor winding insulation resistance with supply cables disconnected; 10 minute test
33c015db-c880-5adb-8d3b-7e8bfe2ef0b3 | note | Insulation resistance U, V, W
c1178978-de0d-5ebf-bc20-17d5381b03c8 | textbox | Motor continuity between windings
41daeb51-2610-596f-9a67-f4e7524b2167 | note | Continuity U1-U2, V1-V2, W1-W2.
88febfce-c285-56e9-a5af-26d7f5101d46 | textbox | Space heater continuity & resistance check
d1720914-31bf-54c2-bcef-1e740890eebd | note | Continuity & Insulation resistance results:
10ea7776-d3c9-58a1-b1de-703a8c5b7d9a | textbox | Thermostat or RTD wiring resistance check
4397f33c-d36a-5fc5-973c-9931d8965486 | note | Resistance:
d70902e6-a19d-593a-9b9f-0308d8aee3c4 | textbox | Check motor is earthed correctly and record motor earth bond:
389779f6-b200-4eb0-99f6-bf4ad90dc6c5 | checkpoint | Additional checks
ca89657d-8274-5b54-90a8-84da7ae9711f | tickbox | Winding temperature detector
bd1fc1d9-c0db-52e5-a38e-0516b08a7c30 | tickbox | Air temp detectors
d0637198-bc05-5217-a05d-48ba0cc8adc2 | tickbox | Bearing temp indicators
f295dfc8-c2f6-5580-8223-5f5450847f2e | tickbox | Vibration Monitors
504a4890-9193-5aad-953e-600d1199849f | tickbox | Condensation detector
1de0af8b-e450-508d-a5a7-bcfc9d12fe15 | button | All spare entries in terminal boxes have been blanked off correctly (with certified plugs if applicable) | Yes,N/A
e42644f8-65bf-52ce-9d7e-9f8740c13e0c | button | Inspect all Ex "d" terminal box flange surfaces and apply approved grease (if applicable) | Yes,N/A
c83a97b3-cf6f-58ee-8732-b49b09c133ee | button | Installation conforms to specification and drawings | Yes,N/A
d31e85a1-a5a7-54ca-af23-6d073e938c85 | button | As-Builts complete | Yes,N/A
b19580dd-b596-4a2e-95e9-e0f9d10d8ae6 | signoff | Installed by:
7a5bbaef-38d2-4487-8e8a-bef08ed3ad22 | checklist | ITR-E-14 Motor Control |  | ITR-E-14 Motor Control
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
fd03434c-5f78-4e17-ba2c-8722e0cb18e0 | checkpoint | General Motor Control
ccb4081a-fb55-5dee-b67a-d0711d40dbe0 | button | Check all labelling and warning signs are correctly installed and visible | Yes,N/A
b4b13c23-1f1c-5ba4-8434-0905765a774c | button | Check control equipment is clean and free from dust, debris and tools, no mechanical damage | Yes,N/A
14347cdf-8b80-51a6-96ce-717884a64cb6 | button | Check preservation and transit items are removed | Yes,N/A
74479542-0f89-5032-b3ed-bbee38ee9f1d | button | Check correct earthing is installed as per design from earth grid to the controls, the cable trays and the motor | Yes,N/A
e3c382fe-0548-59da-962a-070f1617c62c | button | Check all cabling to control gear and motor is undamaged, supported and tidy | Yes,N/A
1db92ae3-c0a7-5543-aace-c4b53b30080e | button | Check earthing bar and connections are correct and tight | Yes,N/A
0c135c8d-802b-5e6b-ae33-bd7a95e65c1c | button | Check incoming and outgoing power cables are terminated and glanded correctly | Yes,N/A
335f5f55-db51-52a6-8c4b-e03f5f9c7aff | button | Check phase identification on power cables is correct and visible | Yes,N/A
265e105e-4595-5290-8963-8ad76e981387 | button | Check incoming connections U1, V1, W1, outgoing connections U2, V2, W2, busbars and connecting links are correct and tightened to required torque | Yes,N/A
6db44574-d2a8-5dc9-82c6-0bf1bb21372a | button | Check all other nuts and bolts are tight | Yes,N/A
62338469-1dd3-5f4f-90b2-718dfe6411b2 | button | Check spare gland entries are plugged with correct rated plugs | Yes,N/A
fe2c1d62-af2f-58da-bc6a-cb432af7b28d | button | Check all doors, drive cover, motor connection box and other protective guards are installed correctly and all live parts are protected | Yes,N/A
7a1a5ede-42c3-4db3-8b1b-367e09dc91ea | checkpoint | Variable Speed Drives (VSD)
2c824ae5-729f-5694-b03d-c1c59cc8cee7 | note | Record VSD Details
35149931-e067-5a50-9fbe-b3e5434a6dcb | textbox | Volts (Input) |  |  |  | V
aa7fc944-e808-52dc-abab-70b32996531b | textbox | Amps (Input) |  |  |  | A
54e75ea6-77cf-54c7-ad0a-05a64dc82994 | textbox | Amps (Output) |  |  |  | A
533a4361-f81c-5bbf-965d-3e7c1afbf157 | button | Check mains Voltage (usually 690VAC) matches VSD nominal voltage (input) | Yes,N/A
0b15a2de-075d-5d08-9b98-5f3828917084 | button | Check input power and motor cables are appropriate and capable of carrying the load current. For motors >30kW a symmetrical shielded motor cable must be used. | Yes,N/A
30b49193-3ae5-5f64-bd99-5cc14c470e72 | button | Check all internal cabling and auxiliary wiring is complete as per latest design drawing, properly supported, neat and undamaged | Yes,N/A
45422c23-0edb-5577-8b32-06b3df6cc9fb | button | Check control signal cables use twisted pairs | Yes,N/A
b1e66efc-3444-5130-99e5-d93ecce73b1d | button | Check control signal and profibus cables shield is earthed at one end | Yes,N/A
7de01878-e2e1-5a11-a664-874935d30da0 | button | Check analogue and digital signals are run in separate cables | Yes,N/A
2c48e9b4-74be-4bb3-8389-5e34acf8714c | checkpoint | Voltage segregation
a83cdd18-fead-5c8a-a41e-3b7a0ecadfdf | button | Distance between input power and motor cable >300mm | Yes,N/A
8eb1fd02-fc13-554e-846b-979d3409d46c | button | Distance between input power and control signal cable >200mm | Yes,N/A
5aa26150-5ca2-5718-b8e5-aa9199f26ae7 | button | Distance between motor cable and control signal cable >500mm | Yes,N/A
187f10bb-d5fa-5244-b94d-0a51356ca175 | button | Check there are no power factor compensation capacitors installed on the outgoing power cables | Yes,N/A
a6d9bcca-8fc7-55d1-b229-abab1bf8d352 | button | Check gland plates with single core power cables are non-magnetic at VSD and LIS | Yes,N/A
e94f5873-21db-5ab1-adc3-f5c1f67e21e7 | button | Check mains voltage cannot be applied to the VSD output by means of a bypass connection | Yes,N/A
206ca093-7416-5cf3-aefb-91b1930d3076 | button | Check appropriate auxiliary 24VDC fuse / circuit breaker is installed at MCC | Yes,N/A
9abe4b2f-00fd-57d8-b371-fea8405e2e6e | button | Check VSD Incoming Supply has appropriately rated fuse disconnection switch (that can be locked in opened position) | Yes,N/A
d7bf9fe1-d342-4a15-b696-ceb8ed614ef6 | signoff | Installed by:
283e8841-342e-4083-9b8c-95ea445fe6d2 | checklist | ITR-E-15 - UPS Installation |  | ITR-E-15 - UPS Installation
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
fd1b3421-ee2b-4887-96e2-49de5d69b3e3 | checkpoint | UPS Installation
ee74dfb4-5173-5b30-918b-15fd4dcbf3e9 | textbox | Make, Model, Manufacturer, Serial No. (if applicable):
5fda5ed0-2eb8-5d28-a8c3-9569c2c604af | button | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule. | Yes,N/A
c2819b3f-184d-5e11-a421-83f0adacb1ee | button | Check for mechanical damage. | Yes,N/A
5d0d10c2-f8a3-5b03-bf19-7f1888e4a650 | button | Panel IP rating is correct. | Yes,N/A
a9d753cd-19f1-5d75-8e4b-d3c801298831 | button | Holding down arrangement and seat alignment correct. | Yes,N/A
1ea722dd-1f38-5b3b-b8aa-dce6d9996a51 | button | Panels aligned correctly. | Yes,N/A
44d275cb-d9a8-5a3f-8f61-2770ea603c35 | button | External bonding correct | Yes,N/A
6bc83a0f-92c7-5650-8ecc-308844db006b | button | Phase identification correct. | Yes,N/A
f28650b9-bc97-5325-a4ad-d165c4a7cd18 | button | Instrument, indication lamps & interlocks correct. | Yes,N/A
48ea3162-ff9c-5a2b-b70d-c129c74e9580 | button | Main switches, contactors, fuses etc. sized & identified correctly as per Single Line Drawings. | Yes,N/A
d4a7329d-2367-59c0-ba77-f307c2404077 | button | Check Main Isolator and Bypass switch operation | Yes,N/A
be331f86-40e6-55c0-b56d-10d3bc2dfb73 | button | COM Interface & Mod Link. | Yes,N/A
722dd572-1032-5552-8252-a0993dc022a4 | button | Padlocking facilities correct. | Yes,N/A
2225f314-4bf1-585f-a646-0a3d29fcae34 | button | Check internals for cleanliness. | Yes,N/A
2362929e-a691-57c8-bb94-c8a8ad32d6f8 | button | Check manual operation of selector switch, MCB, push button, etc. | Yes,N/A
fb454ce3-f7c3-55e2-aca2-ffe72a629ea9 | button | Incoming cable correctly installed, terminated & supported. | Yes,N/A
544af1fb-3766-50d5-a3a4-49ed80b200d9 | button | All internal cabling & wiring neat, correct & tight. Unused cable entries sealed. | Yes,N/A
7937ff8b-3bf0-5d24-a87f-1a1bd9f41fc8 | button | Drawings marked up with relevant changes and As-builts complete. | Yes,N/A
00f5cc09-0a5a-456c-985d-8deb0629d1dc | checkpoint | Test results
32e3f623-a202-58ad-bc0a-05434e90a4ac | textbox | Earth Continuity, Insulation Resistance, Temperature, Phase Rotation, Polarity.
743ea08e-c504-4f08-9204-26a503a950f1 | signoff | Installed by:
9633db95-b606-4bdd-bc04-a65463f18517 | checklist | ITR-E-16 Lightning Protection |  | ITR-E-16 Lightning Protection
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
2bbf38c8-774b-495e-b428-f02bd3e34259 | checkpoint | Lightning Protection Earthing system
97a77683-4eb3-5818-a875-eeb5e4987b8e | button | All checks done in accordance with Client specification, drawings and AS/NZS 1768:2007 | Yes,N/A
dc47af06-0f52-5b94-8f23-f47cb32f2ef2 | button | Lightning conductor is 2 metres or more above the entire protected area | Yes,N/A
00bdd8f3-9829-570b-b76d-ba08244baed9 | button | Check the materials and equipment used for the down conductors are suitable | Yes,N/A
94ee2008-9ab5-5c1b-bb1e-32e0c3f58a90 | button | Check the down conductors are routed, located and electrically bonded as required | Yes,N/A
8f67d4b5-b41a-5819-ad80-efa1ebd9b97f | button | Check all installed components are firmly secured | Yes,N/A
94ca0927-1018-53fe-a278-24915e108dec | button | Check the method of protection against electric shock, including the measurement of distances | Yes,N/A
2c691269-3270-5a2c-aa0a-b0fe18eafaf3 | button | Check earth termination systems are interconnected | Yes,N/A
1d93cd4a-2feb-532c-b2c8-5a337b1724ce | button | Check isolating and switching devices correctly located | Yes,N/A
bb82a593-c701-5062-8a35-1ec8b3352a55 | button | Check warning signs and diagrams are installed | Yes,N/A
2eb9b452-7641-5e6f-b803-3a233ab14b66 | button | Check accessibility for operation and maintenance | Yes,N/A
bca6a705-69d3-4ba4-8c0e-b7f81f746e1e | checkpoint | Test Results
d7c62a0f-6b02-5b4c-9154-10602d18b9a4 | textbox | Resistance of all connections at the location of the connection. (The resistance of each connection shall not exceed 0.05 Ohm) |  |  |  | Ohm
fce6b836-ea9b-5588-a447-c07ab865e1b1 | textbox | Earth termination system resistance is correct and record value |  |  |  | Ohm
8ff597f6-dea0-518c-be94-8f1a8cdb5637 | textbox | Record the insulation resistance of the electrical installation |  |  |  | MegaOhm
d45e645a-e6ff-5f2b-b8ee-5534cf81d734 | textbox | Continuity of the main and supplementary equipotential bonding: |  |  |  | Ohm
a7d9a615-ff54-49e2-ba2a-d8539e7ae3cf | signoff | Installed by:
19efb3b5-56fe-471a-8f7c-6851d373a8a9 | checklist | ITR-E-17 Cable Test Record |  | ITR-E-17 Cable Test Record
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
f0ac3927-ad33-4de5-8eaa-8b62fb15c9e6 | checkpoint | Upload completed ITR scans
513fd42c-05fe-465d-a5a6-60e84336e1b1 | signoff | Installed by:
73616095-fd80-4247-9a4d-ebe3a0b85254 | checklist | ITR-E-18 Earth Fault Loop Impedance Testing |  | ITR-E-18 Earth Fault Loop Impedance Testing
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
46a3e14a-ab31-4288-b25e-bf17097d5e06 | checkpoint | Upload completed ITR scans
ff12af13-adc8-4349-941c-bbd3bdc32ca2 | signoff | Installed by:
0dc4e203-08f7-4c87-81ea-c1cf21ee20f3 | checklist | ITR-E-19 HV Cable Install |  | ITR-E-19 HV Cable Install
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
90ad256a-cc82-47b2-be68-9a9ef3ab8b3d | checkpoint | HV Cable Install
cc29fa55-5fe5-542d-aae6-b5a317818561 | button | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Yes,N/A
3733b5ca-b64f-54bd-ba7c-aed07846a861 | button | Check dressing / cleating, cable undamaged | Yes,N/A
2bbb5df0-4010-557e-b31d-498f09f1e5ce | button | Check cable cores correctly identified and labelled. | Yes,N/A
3cf74f56-d88c-5ab3-8481-56c37a833142 | button | Check cable is terminated correctly | Yes,N/A
b7192934-0b91-5863-a040-df3cc234946a | button | Cable has been installed as per client specification | Yes,N/A
db79cc67-bcee-5799-9eb7-63146f45bafc | button | No visible damage to sheath | PASS,FAIL
429d748c-2b60-5309-9d6f-cc4108496a9c | dropdown | Cable Voltage | 11kV,33kV
1d3abe04-a329-541d-ba46-ea69fd91659a | textbox | Temperature:
1b9d8cb2-e175-5a88-878b-c5f1b97638f3 | textbox | Cable Point to Point:
7591ec71-d9d8-40f4-9572-07a1a6b71781 | checkpoint | Electrical Tests
a598796e-f8b5-560f-8616-052299e798ea | note | Testing for the below should be done at 5kV for 10 minutes. If result is below 1.25GΩ this indicates a low test and will need to be re tested. A brand new cable should have a result above 2GΩ. Please insert photo of test results.
b23c38ff-795d-555a-9db5-6b118428b720 | textbox | R-WBE |  |  |  | GΩ
b58fc05a-668d-5951-9d0a-e0aa26497667 | textbox | W-RBE |  |  |  | GΩ
d3aee404-6d4b-545e-8f34-01439b4d5763 | textbox | B-RWE |  |  |  | GΩ
d920a905-8990-5944-98ae-7117035d7879 | textbox | One Core |  |  |  | GΩ
e522260b-45be-4509-97a6-67cc2cb9a311 | checkpoint-no-value | Sheath Integrity Test
a83836d2-51e2-5b6d-bcbf-973658a28930 | textbox | Test Duration:
ff9b4409-cb93-5d68-bb8a-2f8ec1f70f82 | textbox | Test Voltage: |  |  |  | GΩ
01dafb52-67d2-56bb-95ea-97d522e08cec | textbox | Result (GΩ):
17ec1322-89c4-48fa-8d02-aed878f0ef01 | checkpoint-no-value | Test Equipment Details
01c20c58-3ecd-59fd-b3f2-5af833fc28e4 | dropdown | Make | PHENIX
23d953f4-0d53-5dcc-9e1a-6456cb5f82cc | dropdown | Model | PM10A
d97c7ddc-da00-5bf1-aed1-7ae042f0ca07 | dropdown | Serial No | 20-4331
ad61610c-21d8-57dd-9641-37d7310f5550 | textbox | Calibration Expiry Date
db024b07-edc6-49ca-bee7-7aeaad1efdad | checkpoint-no-value | Installer Sign-off
4997561d-fb4f-4a8a-998f-ad8ecb55915c | signoff | Installed by:
7be88078-9aeb-46ce-91d8-a16e2f8f9102 | checklist | ITR-E-20 Cadwelds |  | ITR-E-20 Cadwelds
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
241a2515-5a2a-4e6b-9a09-d09b755df5e1 | checkpoint | Mold type, # and cable size identified
2f7320b4-2cff-5f71-8fe6-e7f3902dd6e1 | dropdown | Select mold type: | GT 50mm SQ to 16mm S/S vertical rod, XBQ - 50mm SQ to 50mm SQ crossover, TA 50mm SQ Horizontal Tee, XA 185mm N/C run to 185mm N/C4 120mm, T.A. 185mm N/C run to 50mm Horizontal Tee, X.A. 185mm N/C run to 185mm N/C Tap, X.A 185mm N/C # 50mm run to 185mm N/C # 50mm Tap, T.A 185mm N/C Run to 120mm N/C Horizontal Tee, T.A. 185mm N/C Horizontal Tee
abb76751-a881-52a1-8f7e-4fab54e87329 | dropdown | Select mold # | GTC-312C, XBQ-2C2C, TAC-2C2C, ZC-11159Z, TAC-3D2C, XAC-3D3D, ZC-11160Z, TAC-3D2V, TAC-3D3D
9126dd07-27cd-5c38-af56-01b35b0377d9 | dropdown | Select cable size | 50mm to 16mm Earth Rod, 50mm to 50mm Tee, 50mm to 50mm Cross, 185mm to 185mm Tee, 185mm to 120mm Tee, 185mm to 120mm Cross, 185mm to 185mm Cross, 185mm to 50mm to 50mm Cross, 50mm to 70mm, 50mm to 50mm flex Tee
d6cb8840-eb8b-4f4e-9456-f882faae229e | checkpoint | Cadweld Visual test
84038c1c-95a6-42cf-85b8-5e4cd21c417a | checkpoint | Cadweld Ductor test
c2a2a535-a905-5103-a824-0237c5ce931c | textbox | Result :
5654c549-fbd1-5ee9-82d1-23e4cfcf31ca | note | Pass if <50 micro ohms
4430fdf3-e236-438b-976b-0ff2ee98875e | checkpoint | Cadweld wrapped in 3M SCOTCH 23 RUBBER or 3M TEMFLEX 1500 GREEN TAPE
39c42f92-3ab2-47be-9a45-d4a7e350530a | checkpoint | GPS coordinates taken
ffe1514b-1ea7-557b-9a87-02c3973e71c8 | textbox | Coordinates:
a4ca5367-a6f3-4ed3-b094-27c73bbca1a7 | signoff | Installed by:
6d2d8201-3fe9-493d-90da-d2199883941f | checklist | ITR-E-23A Coaxial Cable |  | ITR-E-23A Coaxial Cable
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
069ba5b1-0491-4ab2-b284-8d947dba7012 | checkpoint | General
9d2657db-c036-530b-b905-785b1ff65656 | button | Cable passes visual inspection | Yes, N/A
fcef5917-93c0-5def-9aff-b3a303bccde4 | button | Verify cable type, size, colour code and tags are as per cable schedule | Yes, N/A
6470c79f-e95e-5fe1-b8d2-1d14953e3cbf | button | Check cable cores correctly identified and labelled. | Yes, N/A
27988787-0621-54b8-8e89-2e873b615368 | button | Confirm cable routing and segregation is correct. | Yes, N/A
f60b55de-b0db-51b5-9641-5c2bca20e01e | button | Check that cable core polarity is correct | Yes, N/A
d34715e9-cb68-51d4-9459-06b8b0947351 | button | Glanding / Locknuts correctly installed. | Yes, N/A
c1aaf9c7-9181-5a97-ae9b-b6eb2bf4401f | textbox | Gland type - from:
abcdba45-87c3-5449-8ed6-677975e720de | textbox | Haz. Area Cert Details.
802301b2-5caa-5b67-b60d-64bd13507cc7 | textbox | Gland type - to:
85457fe0-6983-5535-a92b-658418636c2b | textbox | Haz. Area Cert Details.
75d73dfd-de5c-5b57-be3c-b88734d4fb0b | button | All ‘spare’ cores have been made safe and are identified | Yes, N/A
e3b3e37f-9543-5373-af51-47303881b1ef | button | Bending radius satisfactory and as per manufacturer's recommendation. | Yes, N/A
55fee049-b8b0-4635-9988-e574e5602249 | checkpoint | Coaxial Cable
d13fb974-2014-5d4a-b1a1-b6cb0ed77f23 | button | Check cable terminated with correct crimps. | Yes, N/A
baa37f6b-b258-573c-99e2-f5a57e075595 | button | Check Continuity | Yes, N/A
c9c68288-7159-5f06-8d44-33b8de8ad146 | button | Check shield/screen correctly made off | Yes, N/A
c9bb02f6-8ac5-4f4f-9487-2a7b4d80e9d2 | checkpoint | Electrical Checks
ce9e2637-ed47-5bc6-9675-d6e7f2610e93 | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
7be5548a-6921-4e13-9778-63d77a986cc8 | signoff | Installed by:
1add05d4-0852-4823-8d5d-908f68bf7c78 | checklist | ITR-E-23B Data Circuit |  | ITR-E-23B Data Circuit
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
f1d87c70-5a0d-43a8-a5ea-f3de1781c58f | checkpoint | General
cefb7fa4-580b-5907-bd96-24bfe6261d71 | button | Cable passes visual inspection | Yes, N/A
f7692762-dd5d-552e-966b-b67504b02d6a | button | Verify cable type, size, colour code and tags are as per cable schedule | Yes, N/A
9f946950-9800-5089-a7d2-57e425e51626 | button | Check cable cores correctly identified and labelled. | Yes, N/A
8582991d-38d9-5d33-853e-cd59d18fe964 | button | Confirm cable routing and segregation is correct. | Yes, N/A
e6922dba-a113-58e8-bd5b-a88650f2207f | button | Check that cable core polarity is correct | Yes, N/A
2d7d335c-e7d2-5606-bbc0-461a51d2cf41 | button | Glanding / Locknuts correctly installed. | Yes, N/A
c4719cd9-c024-5f1c-bd15-1e6c403955eb | textbox | Gland type - from:
91885013-2da1-57ad-927f-723caf8ebdfd | textbox | Haz. Area Cert Details.
af5e0a1d-d591-5f7b-94e6-10e71e781db4 | textbox | Gland type - to:
5361fe1e-8d73-50c8-ab3e-c5b8c74f7997 | textbox | Haz. Area Cert Details.
32ba3d03-e26d-5a27-a803-ffbcfe251e02 | button | All ‘spare’ cores have been made safe and are identified | Yes, N/A
a95bd152-b724-5687-8136-78135f85c8ee | button | Bending radius satisfactory and as per manufacturer's recommendation. | Yes, N/A
8152e388-00c5-44bf-8900-7c3da99595ea | checkpoint | Data Cable
2a029111-dd2e-559d-a297-eb1011222815 | button | Check cable terminated with correct crimps. | Yes, N/A
317b6569-567a-57d3-acf5-465e6396a43d | button | Check Continuity | Yes, N/A
b29a0269-7637-5a2e-9974-20f7659a954e | button | Check shield/screen correctly made off | Yes, N/A
2bd1a639-9717-4227-a259-980d082a737d | checkpoint | Electrical Checks
14d77239-2f10-522c-8756-5595cd52bb13 | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
b756062d-afa9-4063-b2e0-977ea24035c2 | signoff | Installed by:
3cac879e-0ebd-418d-b453-b0f651405394 | checklist | ITR-E-25 Cable Lug Installation |  | ITR-E-25 Cable Lug Installation
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
494ee713-1f5c-4a42-b947-f113356e6374 | checkpoint | Cable lug
b4da03c1-8749-5f09-bfc2-374ac65a14e5 | button | Appropriate lug for cable size has been used. | Yes,N/A
9d4b1f51-de3d-576d-862f-a8d083765d4a | button | Lug has been correctly seated with no loose copper strands outside of lug. | Yes,N/A
363cce8b-dbbc-5348-be35-34c96d368a58 | button | Lug has been crimped with 60 tonne crimper. | Yes,N/A
262a3f8a-7f6d-5cea-93c4-a313b1519b40 | button | Joint sealing paste has been correctly applied to the contact surface of lug | Yes,N/A
a06ba470-150f-434b-b668-c51955fbac37 | checkpoint | Bolts
69ae2587-50e2-5271-82a7-c84e5555dfbb | button | Bolt has been torqued to manufacturers requirements | Yes,N/A
92f863e9-9769-5d14-b9b4-2801dd763abd | note | If no manufacturer torque spec, use torques below. M8-20NM, M10-40NM, M12-70NM.
d5c3518f-b52a-502f-844f-b34662539eed | textbox | Manufacturers torque requirement (if applicable)
d573f1d7-1b65-4041-9334-cbda550e7835 | checkpoint | Test Results
8514f77d-1ee6-52f7-97e5-204673608330 | textbox | Continuity test results
032e8a57-e21b-5eda-987a-780b7af7eba2 | textbox | Ductor test results if applicable
971fb58b-92a5-4681-8180-6eecb303a025 | checkpoint | Test Equipment Used
442655ff-c82f-5a54-8aee-346fe5834ed3 | textbox | Description
207feb44-b8f6-5f72-8b31-a539f70d4357 | textbox | Manufacturer
01e0704f-055c-5e3b-9f99-90d63018090f | textbox | Model No:
b5beb6da-e67e-5865-9e22-3182dcbd8b74 | textbox | Serial No:
5afeccf3-3aaa-4317-b4b5-347451828a7c | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
024a2cba-f57d-42cd-9986-26bc29123baa | checklist | ITR-E-29 Cat 6 Communication Cable |  | ITR-E-29 Cat 6 Communication Cable
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
81a7ef9b-5539-4bdd-bad8-1d749799842e | checkpoint | Common to all circuits
4ff6ab71-dce5-5077-86aa-864d2f1dab65 | button | Check cable for damage | Yes, N/A
99590348-80fb-5f6c-a801-6fd0620b3e4e | button | Check cable is correctly identified and labelled | Yes, N/A
166b40e9-3476-5c78-b3df-40dc4cb4f585 | button | Check glanding/locknuts correctly installed | Yes, N/A
90a29622-865f-5a8a-97b0-392abe2a99f3 | button | Confirm cable routing and segregation is correct | Yes, N/A
cb6adcca-2839-54dc-97e4-c056c3962e7c | button | Confirm to and from destination as per design. | Yes, N/A
19e08cdd-8192-42ba-a4b2-99206ee1fe76 | checkpoint | Data Circuits
3fb22e8b-c878-5047-8b00-61c058265792 | button | Check cable terminated with correct crimps | Yes, N/A
883378a9-1b30-5dac-ac31-3a51ef84c313 | button | Check shield/screen correctly made off | Yes, N/A
3b706ab5-639e-5c4f-a970-1aa8f1f6bd2c | button | Check Cat6 end-to-end certification (outlet and cable) | Yes, N/A
33a7ffd4-a62a-4fd3-b167-84ef33e7fd1e | checkpoint | Electrical Tests
8437f22e-b9b2-5507-9504-825e461f724d | button | Confirm LAN Link Tester is used to check continuity | Yes, N/A
66b1d4e2-78dd-5a61-8262-0cd62f4a2e57 | textbox | Insert Continuity results: |  |  | ohm
e94f230c-3390-4ff4-9f51-e5ebcc226562 | signoff | Installed by:
89690ab6-afc4-4063-bcab-0149059ba804 | checklist | ITR-E-30 Earthing Electrodes |  | ITR-E-30 Earthing Electrodes
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
a5bfa3a7-da27-4a04-935a-1396c4a22636 | checkpoint-no-value | Earthing Electrodes
ab301dbb-aa29-5568-8e65-39baf9c5313e | textbox | Location of electrodes:
3443ba6c-d4ca-5108-9120-9bfae58fa263 | textbox | Electrode length/size:
8d2f5a8e-70a4-5bd1-a15d-68ca16d2a5c6 | textbox | Electrode type:
6c595855-eb8a-57c5-92d8-a0ac1a421b2b | textbox | Method of installing electrode:
41b5d6eb-47a8-5eee-8fc0-b77c5a55c9d0 | textbox | Method of attaching to electrode (E.g. Clamp, cadweld, lug/bolt):
c4aa50fd-35f5-5644-a936-050abdab6727 | textbox | No. of electrodes:
031b001b-56b3-5941-bfae-1045ea1fda65 | button | Earth pits correct as per specifications, covers, no damage | Yes,N/A
23c2f581-c33c-546c-891d-627b093dacaa | button | Connections to electrodes are secure | Yes,N/A
b073d3d1-981a-514e-8584-5f0e2d1a70ac | button | Structural and equipment earth connections secure | Yes,N/A
945aa7ea-460b-5c3c-a9d5-df99aa45dc26 | button | Earth cable lugs secure, cable passes through concrete in PVC. | Yes,N/A
41aabb29-9afb-552c-9358-4014187fe36a | button | Equipment bonding, connection to main earth bar secure | Yes,N/A
793a1926-e194-535a-ae34-b1d67fe0de6b | button | Earth electrode identified, MEN linked, installed and labelled | Yes,N/A
8063742b-83d6-4226-a7a4-2500cea1f0e8 | checkpoint | Earth Electrode Test and Continuity Tests - Disconnected Electrode
8917ff85-066a-5e99-9db4-205629d84d61 | textbox | Electrode 1 |  |  | Ohm
d5e6b662-0e9d-59c3-ad87-2b3434424707 | textbox | Electrode 2 |  |  | Ohm
4aa60d1b-f626-5ab4-8900-3c8f9342cba7 | textbox | Electrode 3 |  |  | Ohm
371fa17e-0fad-5db3-b52b-ac10edacc4c0 | textbox | Electrode 4 |  |  | Ohm
ec6c3370-3613-5d85-974d-d5c1dc6895c2 | textbox | Electrode 5 |  |  | Ohm
9c2ed006-0cca-5dbc-8560-e7fb5b38f3ae | textbox | Electrode 6 |  |  | Ohm
47a8bcbb-2de8-5b97-a20a-eb44e071e5b8 | textbox | Electrode 7 |  |  | Ohm
9eadce2d-5c41-5123-8cd4-f1a3293a4022 | textbox | Electrode 8 |  |  | Ohm
b0979ca6-e684-4b3a-bf94-38c88acb2803 | checkpoint | Earth Electrode Test and Continuity Tests - Earth Grid Test Results
efe0bd15-6b4c-5c14-987f-12a8d398912c | textbox | HV earth grid |  |  | Ohm
7fac14b5-0cfa-51d6-acb9-275432c4c2a2 | textbox | LV earth grid |  |  | Ohm
fb8edbdb-c998-5443-a19e-42a95b8be934 | textbox | Combine HV and LV earth grid |  |  | Ohm
9afb7e81-aa4f-58df-9701-bff34ac056a6 | textbox | Instrument earth |  |  | Ohm
e2b2d84b-ecf1-47c6-a90c-abe61a47e324 | signoff | Installed by:
15fcd947-670f-4f5d-9be0-8306a1fd28e4 | checklist | ITR-E-32 Battery |  | ITR-E-32 Battery
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
82580a12-4ba7-472c-bfbb-9c954acf8ce2 | checkpoint | Batteries
ef1575d5-be8a-5950-b506-c7e6f7cd0e9b | button | Check equipment and nameplate details are correct in accordance with the data sheet and drawings | Yes,N/A
71b07843-1c7c-5601-9ee7-2c2478dc7bc9 | button | Transportation packing and plugs removed | Yes,N/A
2399f8b0-d1b1-57b4-80ce-4231f1ca3948 | button | Battery cells correctly rated and numbered accordingly | Yes,N/A
631ec1e2-f9ab-572a-a160-69a0050cf0e5 | button | All cells correctly mounted, links tight and shrouds fitted | Yes,N/A
d4b04a18-7231-55e7-84a8-7f9164cc8dfa | button | Internal cables correctly installed | Yes,N/A
8385b974-1a45-57f1-9ae5-fe977417b91d | button | Protection of live parts correct and adequate | Yes,N/A
813995dd-998f-5dca-bfca-c94165a3220a | button | Electrolyte level correct in each cell | Yes,N/A
ba5fe2d7-9b75-5bb5-9264-0131bf49629a | button | Check specific gravity in each battery cell | Yes,N/A
e182744e-f48d-51f6-99e3-d9160822fa1c | button | Check cleanliness of cells and battery racks | Yes,N/A
378615ec-75c2-5930-a061-ecab70d23fe9 | button | Verify approved grease applied to battery terminals | Yes,N/A
79226d91-7761-5e48-87ee-8c7578dd9569 | button | Earthing correct and tight | Yes,N/A
291b1a35-6d70-5fa6-bc22-09140ee622a7 | textbox | Verify polarity correct per drawings and record voltage
bcfd9582-6e05-58f8-9650-c81d622eed9e | textbox | Preservation as per supplier instructions
4f54d7ed-f368-5bf5-9cb2-fd213ce86628 | button | Leave equipment with any isolators and/or circuit breakers switched and locked in the off position | Yes,N/A
c0a0103f-01a9-4700-a8c7-0e3b5b1a7803 | signoff | Installed by:
2f5ed2d1-fba5-4b85-a950-ff5c2b5b5c24 | checklist | ITR-E-34 Low Voltage Switch Board |  | ITR-E-34 Low Voltage Switch Board
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
910d5a43-fef8-40a7-b2e1-26d6da8e2445 | checkpoint | Low Voltage Switch Board
cd235430-64d2-5e69-837b-7b306b6ed6b0 | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
5efdf7dd-5482-53b5-8e2b-4201a1fade6f | button | Check holding down/mounting arrangement is correct. | Yes,N/A
1c52c74b-67d5-5020-a850-472b4fcd9bcc | button | Check for mechanical damage. | Yes,N/A
141296eb-cb9c-57e0-8f35-2844ddc3e6e2 | button | Confirm that all temporary supports, jumpers and ties have been removed. | Yes,N/A
4f9896f6-45a1-5350-9c5b-8966ad659bc9 | button | Incoming cables correctly installed, terminated and supported. | Yes,N/A
572d7dc0-38c5-56a1-b48b-7fa756928cdc | button | Phase identification correct. | Yes,N/A
bd57fe01-0c2d-5fad-84ec-2bb7c13bf569 | button | Confirm that padlocking facilities are provided and operate correctly allowing all circuit breakers to be locked in the open position and safety shutters locked in the closed position. | Yes,N/A
c7bb178f-0922-5441-b9af-aa0fee8330c3 | button | Confirm all cubicle doors can be opened without obstruction and minimum required clearances are retained | Yes,N/A
3fb275b2-3c22-5954-b7fd-bfbc62f45fd5 | textbox | Bus bar alignment to manufacturer's specification and connecting links tight to specified torque.
76875fc5-210c-5e5d-a925-bdc79e4fdb64 | button | Confirm components, fuses etc. correctly sized and identified as per design drawings and Single Line Diagrams. | Yes,N/A
c1f9a3c2-fbde-5a3e-b362-c5c533e85977 | button | Instruments, indication lamps and interlocks correct. | Yes,N/A
52671435-bcc3-578c-994f-dfc5e5e9dd4f | button | Ammeter and current transformer correctly installed. | Yes,N/A
2bbf6ab3-d915-53e0-91b4-a668800b71d7 | button | Check internals for cleanliness. | Yes,N/A
4b88915f-0582-5941-923b-1861f6d23df1 | button | Check that Switchboard is correctly earthed. Check door, escutcheon, gland plate, gland and frame. | Yes,N/A
7ab3b1ee-5e2c-5587-9738-106c1274938e | textbox | Test and confirm the earth resistance between switchboard and local earth system is less than 0.5ohms
1613d7af-085d-5246-9107-60bb31d65ac7 | button | All internal cabling and wiring neat, correct, and undamaged. | Yes,N/A
7d708cfc-6394-5090-8ee6-3496d831fff8 | button | Unused cable entry sealed. | Yes,N/A
9b1076d3-6838-548a-b8e3-ab0a622759f0 | button | Heaters correctly installed. | Yes,N/A
4e4def6e-6ff9-5e08-bb27-150eb0627a78 | button | Confirm that all insulating bushings and barriers are satisfactory. | Yes,N/A
8661e92b-bb89-4509-907d-c561fdee93b2 | checkpoint | Check Busbar insulation resistance between earth and phases. For a duration of 60 seconds with the following voltages.
0d9750f0-65ef-515a-b46d-a076e60ab753 | note | System KV ¦¦ Test V (dc) ¦¦ Min IR Reading
044fe293-acab-5704-8aca-55c379535825 | note | <1.0 ¦¦ 500 ¦¦ 10 MΩ
155c7645-eabb-5f54-8a96-122cf3697180 | note | <2.5 ¦¦ 1000 ¦¦ 50 MΩ
c5a0227e-a0c0-52e5-8ca1-dcd11c4a653d | note | < 4.6 ¦¦ 2500 ¦¦ 100 MΩ
5b0a160a-f689-5523-9f35-a871b09dde33 | note | >4.6 ¦¦ 5000 ¦¦ 250 MΩ
47c66daa-50b1-55ab-92b7-e33343a96925 | textbox | L1 - Earth |  |  |  | mega ohms
c6be092f-0c6d-50af-85a3-c2674691b16c | textbox | L2 - Earth |  |  |  | mega ohms
6d4e070c-21a6-5fdc-afa6-c7889a4356b2 | textbox | L3 - Earth |  |  |  | mega ohms
6dc67cb9-40ff-572a-a417-d2c2b962ae79 | textbox | L1 - L2 |  |  |  | mega ohms
68259625-2eab-5b5a-aae5-fc107b04a1b8 | textbox | L1 - L3 |  |  |  | mega ohms
708e02ba-268d-55a5-a88b-64b2bb90082b | textbox | L2 - L3 |  |  |  | mega ohms
bbab0288-3756-5591-a178-53f344fe69e5 | textbox | N - Earth |  |  |  | mega ohms
2313dd27-72aa-4632-9715-f23737f8f507 | signoff | Installed by:
90c1f14b-635c-44d1-99f9-c6073d90ec6d | checklist | ITR-E-40 Bus Bar |  | ITR-E-40 Bus Bar
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
010083bf-8e3f-4bcf-a92f-68344f7f7ffc | checkpoint | Bus Bar
419586f1-81de-588e-ad92-22b8f7ceda33 | button | Check entire Bus Bar and confirm there is no damage | Yes,N/A
8d9fffd4-7f32-5bcf-a4cc-b5ac7c4972fa | note | Please attach photo of Bus Bar
48033efa-e8a9-54f8-b71d-43d5e146dfe4 | button | Bus Bar alignment is correct | Yes,N/A
6d83dd9a-ce84-52f7-8bc6-260de41d0dd2 | button | Confirm all jointing bolts are present and have been torque tested in accordance with the manufacturer and design requirements. | Yes,N/A
cd5a8c2f-1101-5cad-84fa-6aa51de73ad7 | note | Acceptable Bus Bar Torque Settings:
510b6263-66d7-5633-9831-f42b2173fb32 | note | Bolt: M6 ¦¦ M8 ¦¦ M10 ¦¦ M12 ¦¦ M16
d48e325a-dbb7-5ed5-bb82-e0da679374d2 | note | Torque: 10Nm ¦¦ 20Nm ¦¦ 30Nm ¦¦ 40Nm ¦¦ 60Nm
0b9f7360-eed0-5684-86bd-759036036131 | button | Confirm all transit packing and preservation materials have been removed. | Yes,N/A
a404a903-244d-59f7-9421-98b0fb8b582d | button | Confirm Bus Bar clearances conform to manufactures and design requirements. | Yes,N/A
695b8602-4984-5340-80e3-b556dbc206d1 | button | Confirm all Bus Bars are secure within the supports. | Yes,N/A
8949e3d6-37ba-5856-825f-a1295f980a6e | textbox | Insert applicable test results
5b26a5c0-2eec-4e4d-88e0-2490b8a13e0e | signoff | Installed by:
fc2523e6-51f7-4b90-86a4-401ac5f520cd | checklist | ITR-E-45 Local Control Station |  | ITR-E-45 Local Control Station
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
862532a2-b133-45c8-ab79-92ec02ab002b | checkpoint | Local Control Station
f601df52-7e6f-52d9-ac22-b6cf95871883 | button | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule. | Yes,N/A
e0c38cd3-9f08-5608-bcfd-87782cfa4ffe | button | No mechanical damage and paintwork in good condition. | Yes,N/A
a5129bcc-a64c-5e49-960a-059d04cd3ab9 | button | Glands correct size and type | Yes,N/A
a885f228-a93b-5662-8621-fe5dbdd95b82 | button | LCS properly supported and accessible | Yes,N/A
b8c82542-7662-55fc-9ea7-54fafa907c58 | button | Spare entries correctly plugged | Yes,N/A
4881f7ed-1c86-53d3-8ebf-32ee6a90cea9 | button | Check internal cleanliness | Yes,N/A
a6e866e4-fe81-5ce4-a14e-6ad7a11d073e | button | Check push button/control for mechanical function | Yes,N/A
d914740e-3620-5876-9d78-14e40a5dc2b7 | button | Check connections and terminations tight | Yes,N/A
7230ef78-bd63-558b-a310-16f7aa4d22cf | textbox | Check that LCS is correctly earthed. Test and confirm the earth resistance between LCS and local earth system is less than 1.0
e596f28c-da51-57e0-969a-39307d47690b | button | Check gasket and seals are installed and not damaged | Yes,N/A
248d51e1-e6b5-5201-b8a7-f6c7ecd894b0 | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
21a69e32-25df-5f0d-948d-4f4fe486c048 | button | As-Builts complete | Yes,N/A
f5e7f44c-ed2a-44ec-bd73-655074f21cf7 | checkpoint | Electrical Checks
403741ef-2f04-5ff0-b708-6d9c38d96d3a | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
ac7b91d6-d913-44f1-ad06-21f32f1e6338 | signoff | Installed by:
c96c36d5-b05a-47aa-9758-e28c288b2bff | checklist | ITR-E-48 General Lighting |  | ITR-E-48 General Lighting
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
72525231-4041-43d5-b2a0-1dcd8a4e1e7c | checkpoint | General Lighting
3c6824bf-6d79-558a-9b5f-c17baf105882 | button | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule. | Yes,N/A
6daf77b6-8b50-510a-a02c-3b2a67d62b35 | button | No mechanical damage and paintwork in good condition. | Yes,N/A
2c39e37f-9b79-5518-986c-3dac578cf42a | button | Operation of emergency lighting fixtures checked | Yes,N/A
bcf670dd-fc30-51a3-8df1-f619bed62c6a | button | Mounting arrangement and degree unit is installed is correct | Yes,N/A
42ae753b-ddd0-50fb-ae2c-edcb6b4b1109 | button | External cabling is correctly installed and labelled. | Yes,N/A
0f3360fe-e87c-5127-a2a1-4838638465d3 | button | Battery run-down test per manufacturers specification | Yes,N/A
b301fd42-45dd-5b8f-9f1c-89ae319e08d7 | button | Power / load balance on distribution board checked | Yes,N/A
da5ccec9-531e-568d-9b75-34df9dd4b687 | button | Operation of remote lighting control checked | Yes,N/A
3352d4f5-83b3-56e7-a103-c0df76cabdc7 | button | All spare entries blanked off with correct plugs. | Yes,N/A
7ae46989-20ae-5e12-9a19-9db265456240 | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
3c9772df-31b5-56f3-8aeb-46209b5ac02d | button | Conforms to Specifications and Drawings. | Yes,N/A
a0707218-4354-5a9d-b15d-8614ccd30615 | button | Insulation resistance of final sub-circuits checked | Yes,N/A
12a18436-08e1-58a7-a3e8-5007f7044f76 | button | Operation of photo-electric cell control checked | Yes,N/A
84e84693-1262-5d5c-8f8f-aa028bac1125 | button | Lighting pole is adequately earthed | Yes,N/A
87a14146-1e70-5089-850f-1aa44924e4d3 | button | Circuit ID fitted to all light switches | Yes,N/A
86e4401b-d1ef-5ec9-8969-8eef73f89a2c | button | All fittings correctly labelled | Yes,N/A
dbfb30e5-8902-5caf-9f8e-c6908b6a9e7c | button | All switching tested and confirmed as correct (two way, intermediate, on/off/auto etc | Yes,N/A
017e8688-26f3-5362-9047-3dabe7a020c8 | button | As-Built drawings completed | Yes,N/A
6deddb91-9235-417e-8828-ce15a175a384 | checkpoint | Lux Levels
f7e7c702-59c1-5ffc-866a-cee27ecdd80f | button | Lux levels meet minimum client specifications. (Closed door and measure lux level at darkest point of personnel accessible area) | Yes,N/A
9335e9ba-130c-59bd-80a4-2fbe40cb7d5a | textbox | Lux Results:
8577837f-56a0-4f29-be2d-f3fb5ecc71f0 | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
5b5e8251-1a6e-418e-9390-fc8c9ea73030 | checklist | ITR-E-55 HVAC System |  | ITR-E-55 HVAC System
3e49673e-985a-41d8-9365-3056a82f5681 | section | Details
1486ce81-7661-4eff-b38b-d6fce8dc6d05 | checkpoint | HVAC System
a5bf28c8-fbb8-5809-894a-f8a71c0922f4 | textbox | Model:
ca7f8cd2-6835-5a5c-8b28-90b2f1f9418f | textbox | Manufacturer:
1a58ee5d-9474-58d7-8085-b336469b770b | textbox | Serial and Tag Numbers:
ab22e19f-d43e-5265-ac57-b5ea914c4444 | button | No mechanical damage and paintwork is in good condition | Yes,N/A
f6f79a43-4897-58d7-a63a-f1a0c6fc37ba | button | Operation of units verified | Yes,N/A
896dace7-d220-5d2b-9a05-07e17d058eb5 | button | Mounting arrangement is correct | Yes,N/A
f09f4825-9ac4-5ba3-b7d9-8c606bf50f50 | button | External cabling is correctly installed and labelled | Yes,N/A
9f13605f-1982-55bb-a5e1-31876d066109 | button | HVAC unit isolator is installed and operational | Yes,N/A
d7567c56-df53-506b-9900-1644d92615f0 | button | Remote holders are installed with remotes inside them | Yes,N/A
3234461f-9a08-5d52-9ef2-caa4efc9d02e | button | Units are labelled with appropriate ID’s | Yes,N/A
bf28debf-1065-56c2-80d3-8798c11d5586 | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
a662a3a3-adce-51ed-ac4d-bcfa2e0a86ba | button | Conforms to Specifications and Drawings | Yes,N/A
08665d06-8ff8-5c47-b5d3-634e65407ca2 | button | Any applicable control system configuration has been checked and is functional as per design | Yes,N/A
2babfa14-13d6-57b8-875a-86a601a89c0d | textbox | Confirm ENTEC witness of installers testing
a599b134-79d8-44ba-b867-b3856366f31e | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
f41d0c8c-621b-4071-a5fb-a9fb09e520bd | checklist | ITR-E-56 Fire Detection System |  | ITR-E-56 Fire Detection System
6c0c8828-cdb5-4db9-ba0c-48f0f5e7c076 | section | Details
1ded4b2b-dd35-47e1-b443-b3e6faefb247 | checkpoint | Fire Detection System
0d4c2ab7-b52b-5663-b89d-b2b7a283a155 | button | Fire Panel ITR has been completed | Yes,N/A
7a90e0be-f1e0-5485-9e05-26b75955a09c | textbox | Tag Numbers:
3659e374-628c-59e2-a52f-2360835bcf61 | button | Smoke alarms have been installed as per specification | Yes,N/A
d66fe5d5-cfcd-52aa-82bc-d5cbee7202a5 | button | Smoke alarms are ALL operational | Yes,N/A
61d444ed-8431-555f-9147-601e722605bc | button | Alarm speaker has been installed per specifications | Yes,N/A
c08513b4-ed52-556a-9887-4de41cfc0278 | button | Alarm speaker is operational | Yes,N/A
5eb1e7e6-e8e3-56d5-80cc-9349b360a6ec | button | Fire alarm beacon has been installed per specification | Yes,N/A
1efac73d-3df1-5de3-97ca-2903485e65d2 | button | Fire alarm beacon is operational | Yes,N/A
a34194fb-7df8-5d8e-855c-92daf752881d | button | Manual call point has been installed per specification | Yes,N/A
1e4587e3-10ec-501d-a3c4-b934ad7a1bba | button | Manual call point is operational | Yes,N/A
590e6c0f-01f0-5db7-bfab-437378379cb3 | button | Installations are all unobstructed | Yes,N/A
2e99cb53-1b40-5a58-9e81-090ac4b1bf1c | button | No mechanical damage and paintwork in good condition. | Yes,N/A
8f332f09-ffaf-59d0-873d-1b8932915bfb | button | All installations have identification tags | Yes,N/A
c89e23f8-b7dd-54c6-b73c-911a9e5c4934 | button | All internal cabling and wiring correctly installed and labelled. | Yes,N/A
147e26b3-d50d-5dd8-a464-284fcdc66b47 | button | E.O.L has been installed as is operational | Yes,N/A
1044ebc7-4d39-5fbd-810f-c956d1eea6c8 | textbox | Other fire system installations have been installed correctly:
91a3fd82-805c-5ef7-b658-dc9c33b25f0f | button | As-builts complete. | Yes,N/A
efc185ca-ccda-461f-b1f1-fed2c28d6cc2 | checkpoint | Functional Check
ce974126-f31f-5387-ad0c-1c0318793639 | textbox | Selt test:
e531d03e-a203-5a6e-9921-e0642c421f64 | textbox | Alarm Operation:
1c8b2a96-ac92-5b5c-9526-1a9311b6370f | textbox | Fault relay operation:
c20d4858-f56a-5acd-8c0d-e24388a7d3ff | textbox | Measured output (clear path):
f55dfd84-e932-5fad-af19-1862832d2c8a | textbox | Measured output (blocked path):
4e92af51-e230-5182-89f8-bf67f6c1bc3d | textbox | Measured output (filter in place):
8603aabf-96f7-522c-96b9-ca769660e19d | textbox | Confirm ENTEC witness of installers testing
1b7f5906-4ed7-40be-834c-5c291c7a91e4 | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
697270ae-4e5a-415c-ab9c-a57082e96b63 | checklist | ITR-I-02 Instrument Tubing Installation |  | ITR-I-02 Instrument Tubing Installation
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
754a2d32-7738-4e27-95c6-ac2c3ef96e67 | checkpoint | Checks Pre-Installation
49159251-6dcf-5cfc-910a-abe92ecda659 | button | Tubing connection to and from equipment as per drawings. | Yes,N/A
40506286-5029-559e-8989-69a8e035b394 | button | Tube material type, size, gauge and standard confirmed and available | Yes,N/A
4eb3c4e0-23a1-5ea8-86f0-50ed7148722b | button | Tube fitting size and type confirmed and available | Yes,N/A
5d9c4872-4e9c-4794-bc7e-610b67c60dc7 | section | Checks During and Post-Installation
cc7d0830-c26f-4543-abe4-fb2d689a2156 | checkpoint | Checks During and Post-Installation
4ac924f1-4423-5dc4-8710-3c0438cba621 | button | Correct thread compatibility and engagement | Yes,N/A
cbbfed41-cbe9-522c-a048-88e0dc759d58 | button | Correct thread tape and sealant used on fittings | Yes,N/A
ea4dc0cc-6fc7-54c5-8a15-63572cc12509 | button | Check fitting ferrule orientation and confirm prior to connection | Yes,N/A
64202796-941a-5e4e-b5cf-42640ea5cd78 | button | Tube installation is in compliance with the client specification. (Supports, bracketry, slope, expansion, vibration, access, cables) | Yes,N/A
02fdd7b8-de9d-508b-8c62-666be25bc68e | button | Tube bent correctly, sufficient straight section into fitting | Yes,N/A
d8efd64a-8454-5fe8-a83e-24bdd64a665c | button | Tube cut clean and straight, de-burred, reamed, and blown through | Yes,N/A
9f80a8b5-837a-50f3-94a7-65b677fc8bb0 | button | Depth insertion tool used; witness mark visible at all stages of process | Yes,N/A
3be9045b-0a42-53df-b373-a0cfc7bca7e9 | button | Tube fitting hexes marked to ensure correct swage tightness | Yes,N/A
6319aca0-2069-53a9-8e62-d3e2549819b0 | button | Random check with No-Go gap gauge | Yes,N/A
3faf2134-eda7-586c-8f80-ff4efdbb25f4 | button | In service leak test performed and passed | Yes,N/A
26373ea2-aa60-53f3-b9af-cc9c96137cab | button | Fitting completion tag completed and applied to each fitting | Yes,N/A
8f041907-06ca-5ac6-8f42-14a1272505f0 | note | Refer to Swagelok book for tube/thread size pressure ratings
1efaef86-5739-490c-a7ac-ad98728ac7f9 | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
c92b7ac2-6a8d-4f7c-86ac-4a1b13cf3afe | checklist | ITR-I-03 Instrument Pressure/Leak Test |  | ITR-I-03 Instrument Pressure/Leak Test
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
f4d8d21e-a747-4db0-8e0e-68613190187e | checkpoint | Checklist items
29af9b06-db28-5cfc-9e37-3faa3b32b565 | button | Tube identification correct | Yes,N/A
ffa04ea0-0337-511b-8c53-be22c8eac155 | button | Mechanical damage visual check | Yes,N/A
8446b16b-6ec8-5867-a439-3311487b74ec | button | Flow direction and instrument orientation correct | Yes,N/A
77271c24-72dd-5fd4-8d95-c9f8d9450219 | button | Tubing size and installation correct | Yes,N/A
6d0f8c67-42be-42d1-a0f0-d1dbeef5b4f2 | checkpoint | Testing
9bcae28b-41a5-5f45-96bf-49230c06d0ec | note | Verify test pressure and medium is correct per project and manufacture specification prior to test
8e695ed6-5db1-5764-8a51-50820ae97b47 | textbox | Test fluid:
9f199dd9-592f-51ed-9ad0-d8fae0055c64 | textbox | Test pressure:
eb39dffc-c3ec-5758-934a-3a58ee75c599 | textbox | Max design pressure:
f65f4546-28e6-562c-80e7-5568d87e9473 | dropdown | Test pressure unit: | kgf/cm2, PSI, kPa, bar, Other
fe8bb36c-3155-5aa8-a219-19895507f1fe | textbox | Duration: |  |  |  | Minutes
9e6e7c33-8646-5255-a5cf-7d0107066ed8 | button | Confirm all impulse lines have been drained and cleaned | Yes,N/A
495802ce-2843-51f5-91db-461e87c892b7 | button | Confirm any temporary test connections, valve etc. are rated for the intended test. | Yes,N/A
b4e3a5a5-c160-5d3a-9e64-608c02d1e5fe | button | Confirm pneumatic, test gas and aspirator lines have been blown clear. | Yes,N/A
74c3dc63-6a39-512a-9a5a-4464730b5bd9 | button | Check hydraulic lines flushed to project specification. | Yes,N/A
3a1a66d6-e4fe-46bf-a921-6c29976a96e6 | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
6dff0826-0455-4bf8-8339-7811b52c752f | checklist | ITR-I-04 Valve & Ancillaries (Pre-Installation) |  | ITR-I-04 Valve & Ancillaries (Pre-Installation)
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
d918794a-8234-4c67-914e-097c71770e28 | checkpoint | Equipment
d783750f-9144-514e-a7d8-b5d9fca1120f | button | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No. | Yes,N/A
9132fc8a-82a3-58b3-8fb8-6bfc616b7c0a | button | Equipment checked for additional items as applicable | Yes,N/A
261050a0-62ff-4d6e-ac29-a0c44b4a295a | checkpoint | Valve
91e15710-c9d1-5d9e-9b17-0b1e8ce5f43e | textbox | Valve Size:
f0fd700f-decb-5742-99fb-821529abf655 | textbox | Flange type:
4b7b5d33-59e3-5456-adab-bcb5fe4dc350 | button | Material certification correct | Yes,N/A
4dcf904b-c604-59b4-b62d-a79bc5246767 | button | Trim material correct | Yes,N/A
ea2a0fb1-3cde-52cb-8f98-cb7d36da7fa7 | textbox | Rating:
b2c24ac3-7ca6-570e-b9d1-160025a7f677 | textbox | Service:
5003c73c-6561-51bb-bf09-0891f6b9bde4 | button | Body material correct | Yes,N/A
8896b5a6-f32a-5740-bac8-385038f3654e | textbox | Leakage class:
66d0aa4c-4ca9-4b02-b00d-6bc507f1f046 | checkpoint | Actuator
7f9973d6-6a20-57cd-bc4f-1e93cd878a4d | textbox | Input range: |  |  |  | kPa
0addbd9c-a08a-5194-bc88-91cc284ce2ea | button | Failure action | Yes,N/A
6926a1f1-f154-5926-b042-670177a2f27e | button | Hand wheel operation correct | Yes,N/A
8d758281-ffc9-4f06-8b44-c3ed5802aeb5 | checkpoint | Positioner
dd2a73c4-94cb-5bc4-a47f-e8bfc3b9ead8 | textbox | Signal range
6fcb5a75-7606-5048-80f6-9f3321406663 | textbox | Output range
1f7bca4b-86ab-4996-b716-273ef149d87d | checkpoint | I/P Converter
acea181e-3a9d-5baf-8035-a5c04afb1b17 | textbox | Signal range
c71cc4ca-dda9-5720-a00f-0310ea4287df | textbox | Output range
f213e6ba-724e-48e7-a09b-dc15887fa1bd | checkpoint | Filter/Regulator/On-Off Valve
f63038e9-1082-5c1a-a7e5-fcdc28c0bd44 | textbox | Range |  |  |  | kPa
4ba132a6-d2f2-5836-9f01-0073938a74f4 | textbox | Pressure setting |  |  |  | kPa
036170fc-af4b-5614-ba96-a78de5e4175f | button | Stroke Time correct | Yes,N/A
8062fc15-7255-58c1-8f61-46011af20170 | textbox | Open |  |  |  | sec
52e3928c-25cf-54a3-af7a-f14d827ea9b2 | textbox | Close |  |  |  | sec
a7864d54-b0f5-53a0-9f64-d4dea7d6b1ef | button | Open/Close times conform to commissioning specifications | Yes,N/A
6c0eab88-991e-4a28-9e25-46adfa4d52d5 | checkpoint | Fail Action
1ddd1587-b667-5c84-a215-85f3f1218519 | dropdown | Electrical Fail Action | FO, FC, FL
61d09ff1-4b94-5c84-b44b-3b81d6e3634e | dropdown | Motive Force | FO, FC, FL
a70c10ba-1ee6-4e93-b483-f1a70423e328 | checkpoint | Valve Field Calibration and Hysteresis Check
a31dd45f-740b-5332-b4ca-42c627cbaf24 | tickbox | Confirm test equipment is within calibration period prior to testing
51da174a-a39f-5fee-92da-d9361bae4caf | note | Valve to be calibrated according to manufacturer's data sheet and to be within quoted accuracy.
0cc82034-d2ae-5d50-bcc6-aaad15735387 | button | Check at the following range percentages; both rising and falling 0%, 25%, 50%, 75% and 100% | Yes,N/A
45788360-ed5b-4dfc-8fc1-e33e6bbaec2a | checkpoint | Proximity Detectors
3759ff33-4551-5efe-ac87-f50f32f977f6 | button | Open switch set, correct mode setting | Yes,N/A
f57cc0ad-a6d0-5beb-ad67-3e496dac94c2 | button | Closed switch set, correct mode setting | Yes,N/A
1925d13a-af36-53df-8916-38ec2fe043d2 | button | Electrical connections and certification correct | Yes,N/A
2cb7b721-5199-413b-8fb2-bf862c5e84c5 | checkpoint | Solenoid Valve
db34d79b-9209-5ee5-a44c-d3820e535c3e | button | Operation correct | Yes,N/A
9f0c2d4c-8d7a-5639-8c6c-734c82e9db15 | button | Electrical connections correct | Yes,N/A
43f101bc-3e44-580b-9b1c-3045bbaf33ad | button | Electrical certification correct | Yes,N/A
77043595-d414-5041-980a-963bde7030d5 | textbox | Voltage: |  |  |  | V
70fe5354-bb24-5ebd-806d-0e894227d4c0 | button | Pneumatic connections correct | Yes,N/A
1bfb1a06-5782-559b-bb7e-c811c6d60a18 | textbox | Pneumatic pressure |  |  |  | kPa
4c7a4297-9141-4d4d-962c-982d613fb3b4 | checkpoint | Pilot Valve
651f4ce9-34d7-5b14-8e01-047291eef784 | button | Pneumatic connections correct | Yes,N/A
d7024cca-170c-5d0a-8d86-b1b4dd9f916d | button | Operation correct | Yes,N/A
da8efef1-9017-54d7-966a-ba0fd27c6d3f | button | Action/Lockup | Yes,N/A
ea58187c-707e-4b32-a132-55c8bbabf6cf | checkpoint | Hydraulic Actuator
7c906b13-31da-53c3-bc93-1966b124ce24 | textbox | Working pressure
975b18ef-a3db-5b6a-b225-ac74d645dfa9 | textbox | Manifold pressure
9e504aad-a192-58f7-b6b9-1dc379071506 | textbox | Fluid type
6acc186c-b5ca-5e7d-94ca-f9b063aa9cf1 | button | Hydraulic connections correct | Yes,N/A
068794ba-bf5b-56fd-b042-f18e1c7bc939 | textbox | Regulator pressure setting
fe929150-361a-5156-86ef-a0ec2d47072f | button | Pilot operation correct | Yes,N/A
59c7f135-375f-4bdf-b196-f5cd9105f5eb | checkpoint | Accumulator
ea8ce1e5-3d92-5b1b-8918-ce6b3776b251 | button | N2 Charge required | Yes,N/A
a4313a92-c4d2-56ad-a485-3e153944003d | textbox | N2 Pre-charge pressure
3b32867c-fbe7-5dc5-97d1-23a668584b45 | textbox | Pressure switch setting
bf4e6352-97eb-518a-8032-351fb4d015a6 | textbox | Working pressure
85059d6f-bba4-5a9a-8d7b-e137243a46d7 | textbox | Output range
5c6bf8d6-980f-5bba-b389-068e33e15b06 | button | Volume tank & check valve installed correctly | Yes,N/A
2c2ea8c1-614e-48ac-bf6a-c90d5e521047 | checkpoint | Electric Actuator
e58ee991-02fd-5079-86b9-a6420505c888 | textbox | Voltage:
0364a3f0-ada9-574c-8370-0d149defbb01 | button | Electrical certification correct | Yes,N/A
881aa6ad-f0cb-5e59-a9c0-8726e39bc6f6 | button | Electrical connections correct | Yes,N/A
ec9b2798-4085-55b6-88c1-ed19fab85b14 | button | Remote operation correct | Yes,N/A
6810ad7a-f665-5a66-ab51-049b8b839b0a | button | Local hand operation correct | Yes,N/A
815aba2e-0c80-5533-a061-fd958a9bbd80 | button | Torque switches and travel stops set | Yes,N/A
facfa88b-58f4-49fd-8f63-b6f076aa8a28 | checkpoint | Miscellaneous Equipment
de0c820c-cd0b-5a2e-8356-23b7617fb595 | textbox | Description
4dff5fab-4822-5d72-8594-51d2b625a058 | textbox | Manufacturer
21d60b02-b32d-544c-9d8c-161b841ffac8 | textbox | Model No:
6065b1ce-8baa-5248-800e-c09763814df6 | textbox | Serial No:
bb9a0b65-7a66-570f-b775-2a536584923a | textbox | Range:
91146ce2-7872-450b-ac49-64cd814c1d67 | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
f4c6212a-8912-475c-9276-25a5c3053bb8 | checklist | ITR-I-06 Instrument Installation |  | ITR-I-06 Instrument Installation
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
d6a32dbe-2f5a-41a6-8353-bcfed88d8687 | checkpoint | Instrument Installation
70bfe3f0-9c75-5eaa-8640-42b8477319c8 | button | Check Instrument is labelled, nameplate details are correct in accordance with the instrument index/datasheet. | Yes,N/A
c10d2180-eb34-51a5-b35d-e17ca96387bd | button | Instrument is suitably rated for area. (Ex Rating, IP Rating) | Yes,N/A
24a3bed4-cf49-50a4-bcee-d1376d8048db | button | Instrument is undamaged, correctly mounted, orientation correct, elevation correct and free from vibration. | Yes,N/A
20d79831-6c2c-50aa-98e9-232f7d48bedf | button | Instrument is accessible for maintenance and clear of obstruction and debris. | Yes,N/A
956a3be0-3981-5c57-8a0d-798237c801c2 | button | Vent lines are directed into a safe area. | Yes,N/A
b0634453-debf-5772-8892-ad94488189bc | button | Cable/s glanded and installed correctly, IP washers fitted, cable label installed. | Yes,N/A
ac2cc897-ce53-5de0-adb6-4e1e79761ab8 | button | Impulse, hydraulic, pneumatics, lines, air headers, correctly installed and supported. | Yes,N/A
d69cea9c-2d78-58f7-b078-3ec086b59cbd | button | Spare entries plugged correctly, using certified plug. | Yes,N/A
27ad0057-270b-5803-a1e9-2be2b198bec3 | button | Instrument earthed in accordance with project specification. | Yes,N/A
a46da691-3395-42ba-a098-0fa4c3171525 | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
5cfa4415-f79f-4ab3-b33e-2a58bc6c2c61 | checklist | ITR-I-07 Instrument Calibration |  | ITR-I-07 Instrument Calibration
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
01c37575-6d48-4100-93e9-6f442bb68f85 | checkpoint-no-value | Required Data
075d59a8-a405-51ec-b678-532537e459f7 | textbox | Type and Size:
49e45df9-e286-5443-bf3a-ffd44443acd5 | textbox | Make and Model:
e753bef5-c50e-5e16-ad82-cea8456e26a8 | textbox | Serial No:
351549b5-ed76-5f94-888e-0174969499d6 | textbox | Instrument Type:
e425d1f8-9dc5-52f8-9a9c-4d6fc2d9bbf1 | textbox | Instrument designation/equipment no
826ba9dd-12d8-5e3c-bedd-6ada592bff41 | textbox | Calibration interval
410f1caf-8b65-5671-86a6-e5970e473c15 | textbox | Calibration method
5a2240c3-d9f0-532a-b944-dab99706253a | textbox | Calibrated at
04fbe0f0-18d7-49b7-82d0-ac581199bb2b | checkpoint | Instrument Power Supply
5b2173ae-ef15-5380-b56f-bd7844e43ca3 | dropdown | Supply type | VAC, 2 Wire DC, Other, None
3f4b253c-158b-56f8-b3f7-14bece4d793a | textbox | Supply value:
924dceb1-5202-4f45-b57d-f3a06ce1ed76 | checkpoint-no-value | Calibration
338e227b-c699-5d7c-b9cf-d4cd7fdca993 | textbox | Sensor Type:
76688e55-aeca-5a34-ae98-57835564ffd1 | dropdown | Output: | Pneumatic,Electronic
54a1434e-28a5-5d28-94ee-edc1e535860f | textbox | Input Simulated by:
e56c4797-257d-52a3-912d-499102af3106 | textbox | Output Simulated by:
5e2632ad-58d3-57e5-806f-7b2f555e8af6 | button | Calibration sheet completed and attached below | Yes,N/A
44413f86-1d27-4fb3-8804-fe34ad13d056 | checkpoint | Details
4c258bb5-fa39-5fd6-8723-43dbdeeb0bfa | dropdown | % | 0%,25%,50%,75%,100%
7939b978-3fa9-57ad-bc1e-07961b4b9688 | textbox | Range
f7fe2316-13b1-506f-8794-589de853ecf0 | textbox | Expected mA
3453bbe7-fff0-5752-b3f8-9625bb5d6802 | textbox | Local Indication
ec9a01d9-edae-5aff-8020-0f5a7e2ca3a6 | textbox | As-found TX Output mA
9f7b2cbd-934e-557b-bb38-4c286407814b | textbox | As-found TX Output
372ac5dc-7226-571c-9ce0-ad98c0fd11a4 | textbox | As-found TX: Error
b5723b5a-124d-5d01-b2b3-e471cc8252f4 | textbox | As-left TX Output mA
dce68b62-2b5e-5121-9298-8cfb48f965de | textbox | As-left TX Output
1574f0a6-0d2e-56b4-848d-8b11352bd00e | textbox | As-left TX: Error
bda766b1-6d9a-42e2-9d3b-041c66ea27a1 | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
1629ea98-bdcc-489f-9481-435fe12e32c7 | checklist | ITR-I-08 Instrument Pre-Commissioning |  | ITR-I-08 Instrument Pre-Commissioning
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
9b2abd80-5840-4242-93db-d41c71599f50 | checkpoint | Checklist items
1de93dc0-5a4a-5ecf-96e5-3e3ada82f5b4 | button | Verify transmitter loop connection - Remove wire on transmitter and confirm at Control System interface | Yes,N/A
4f4a87b2-acf0-51b9-9c1a-3fe190a006e1 | button | Relevant individual control system/ESD loops have been checked and test sheets completed | Yes,N/A
9f759255-2361-4b4d-b2ce-a430f0522603 | checkpoint | Analogue Input:
e59c8de5-9a21-4311-b51b-6be7ce40a56a | checkpoint-no-value | Analogue Input:
4164e952-b628-55cd-b75f-aa2c4676d742 | textbox | Input range & units:
d8d5bad2-542c-5cb5-accd-54a1f4bac12b | textbox | Indication range & units:
e9fb9b16-c86f-4d64-9d3d-a4f900805ff2 | checkpoint-no-value | 0% Rising
75970b5d-8105-5da9-a40d-b2cfdbe844af | textbox | Input Signal:
cbc3cab2-d7c4-5b1e-8794-dcc21f38642a | textbox | Control Interface Indication:
02209309-951c-42d9-a2b0-2279ce704abf | checkpoint-no-value | 25% Rising
d6556c18-049e-5403-acfd-c86487991a8e | textbox | Input Signal:
ac08c071-bdf1-54dd-a1d1-54adf56993aa | textbox | Control Interface Indication:
843de891-b802-4680-8866-e0ef077819f6 | checkpoint-no-value | 50% Rising
c55a71c6-d3ab-5fc1-b8ee-239c61b6b325 | textbox | Input Signal:
2a763173-8a1a-5f04-9597-18f03635935e | textbox | Control Interface Indication:
76c1c3a1-3f27-4db0-aa59-2f060e84c71f | checkpoint-no-value | 75% Rising
7f52aa7a-a662-5861-b325-06d09def837b | textbox | Input Signal:
5a8a81cc-e72c-594e-a7da-641a85292857 | textbox | Control Interface Indication:
9f0aaf51-a6fe-4c71-8b8e-8bd798ff1b35 | checkpoint-no-value | 100% Peak
20195e35-4e9f-55cd-9dfb-7fdb03b3c5d8 | textbox | Input Signal:
933476b1-ea08-53e7-b59d-c5ee3a79e55a | textbox | Control Interface Indication:
65034cca-0ce4-4eb2-9022-f5e8c79243a6 | checkpoint-no-value | 75% Falling
51a1e175-3060-5ba0-a565-b94b4881f630 | textbox | Input Signal:
1c2aa0bf-c697-58c0-80ca-1a31378be7d5 | textbox | Control Interface Indication:
b0eb862a-f80c-4faa-8fc5-e501ad51189a | checkpoint-no-value | 50% Falling
4f673392-ba14-5802-a029-58303833b0c8 | textbox | Input Signal:
4b279618-f4a7-5d10-bef6-b17ca2e8871e | textbox | Control Interface Indication:
f9cc3ee4-a274-4580-bb01-c421f9ec9fa3 | checkpoint-no-value | 25% Falling
fa643578-db55-54db-9d57-a34c3f5bafb6 | textbox | Input Signal:
39080333-48fc-5885-876b-674f091042dd | textbox | Control Interface Indication:
69e47036-b6a4-47f7-afc1-7caef5c09693 | checkpoint-no-value | 0% Falling
be470454-ce94-5cfb-b1f5-e0dc8761f535 | textbox | Input Signal:
366eb58a-af13-582d-9736-e1eba26055dc | textbox | Control Interface Indication:
e097e85d-7cfd-4330-903a-bd10d2b03bd1 | checkpoint | Digital Input/Analogue Alarm Trip Points
7ad5e831-7807-4c9d-b8ec-49726264cb6d | checkpoint-no-value | Alarm Lo:
f77b7ecc-54fc-561e-8147-79fac2d96f5a | textbox | Alarm setting
6c11278a-377b-5e8a-bc5a-3789a04a09b2 | textbox | Measured Alarm Point
6eee2af9-b436-54c9-955c-8c767643c523 | textbox | Filter/Time Delay
7b3e022d-effb-578c-8a1d-0b01a7df9ed8 | textbox | Result
2d735702-fabc-442d-adb6-cbda0b8d3399 | checkpoint-no-value | Alarm Lo-Lo:
e6f66d50-c165-5b2a-a41a-fc4f1fbb24bc | textbox | Alarm setting
8733da33-55f1-54f2-8cff-184687bd858c | textbox | Measured Alarm Point
ece75955-1cff-53e5-aad7-2bd5c61bc3a3 | textbox | Filter/Time Delay
b99553e6-c8bc-5561-b491-d8b411051617 | textbox | Result
6be6c957-d6c7-4b45-99b9-51a32d58e050 | checkpoint-no-value | Alarm Hi:
80d99dc1-ebcd-544f-9523-c5d687622b60 | textbox | Alarm setting
430edd6e-5de7-581a-973b-79afc1696762 | textbox | Measured Alarm Point
04e19ddf-202e-5ae6-99be-210f8eb50557 | textbox | Filter/Time Delay
36429f64-5c3b-5e5f-a7a0-372ab744836a | textbox | Result
83cf3fb9-5492-4b7c-aad4-629a12c10bfe | checkpoint-no-value | Alarm Hi-Hi:
c7108dc8-91c5-5449-8727-ad4dcf969f72 | textbox | Alarm setting
e027ebbd-3723-5197-8def-5dbb93a24516 | textbox | Measured Alarm Point
75fd7c8d-c406-5112-a15a-7e82964118fc | textbox | Filter/Time Delay
dadf751e-9b7c-550c-8d56-1a36be82926f | textbox | Result
edd80f6b-38bc-4ec4-86e3-756e0712dc57 | checkpoint-no-value | Control loop set points correct:
eb2594be-ba35-5f00-ba05-219cfba1dfb3 | textbox | Set Point 1:
433fcf49-8f29-5b4d-9b51-e6c9ab5f0b44 | textbox | Set Point 2:
a3d804f6-3084-5c54-845c-afec09f4edbf | textbox | Set Point 3:
78182109-21e4-59fb-aee1-34c8d21c500e | textbox | Set Point 4:
25e6479b-2e80-48d5-be65-2c88a2c20744 | checkpoint | Startup, Shutdown and Override functions
62623f92-3e27-5bbf-b7ca-64cca4738ef3 | button | Control system graphic display | Yes,N/A
92776563-2e22-5318-9875-a9cc5779aa87 | button | Control system point display | Yes,N/A
fb970c56-ebd7-5c63-b50c-c95acc303b18 | button | ESD graphic display | Yes,N/A
33049592-28cf-5745-828b-00a67e1ef762 | button | Alarm Recording and Text | Yes,N/A
0e577e02-0956-41ce-b607-726e8a650bf3 | checkpoint | Additional checks
67617b44-316c-55e1-b491-3673356b4a58 | button | Control system display and alarms are correct as per control functions | Yes,N/A
d81d0e1a-ce16-5165-9f45-b8e2a7974388 | button | Transmitter fail direction and burnout are to spec (Upscale/Downscale) | Yes,N/A
7feed3f2-1e2e-5e30-ad19-43c57e95f617 | button | Switch action verified, including power loss | Yes,N/A
a27b22b9-f951-5c69-91ca-7dce55839236 | button | Drawings, documents and As-Builts scanned and attached | Yes,N/A
5aee35b9-ecc6-4bad-ba10-138cd0a960de | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
1d78fddf-fd2b-46c1-bf3a-25fd9a0f4251 | checklist | ITR-I-09 Commissioning Instruments |  | ITR-I-09 Commissioning Instruments
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
f5e1b227-d30a-4423-a96e-0a10bf869c07 | checkpoint | Required Data
11569a38-46f1-5f78-a29c-5e681b1809cd | textbox | Instrument range:
208cebbb-a864-5db0-b2ae-ce78f5a8ade6 | button | Installation complete | Yes,N/A
475db32d-6c63-563d-aeaa-d74f8681cca9 | button | Point-to-point | Yes,N/A
96c1e3f6-510b-5dde-9f21-6b3f8321014f | button | Haz. Inspected | Yes,N/A
64be49d3-e7a2-53e4-95fd-b247131a9e90 | button | Tag correct | Yes,N/A
07721343-ccc9-5a52-be10-854e8933ab92 | button | Hook-up correct | Yes,N/A
088c749c-660b-470c-921b-7d9d668e2c44 | checkpoint | Alarms & Set points
a9c5e9cc-6bb4-4e59-aba4-2a67bc1fcdf4 | checkpoint-no-value | Alarm Lo
0acf13c2-41e3-533b-9a13-edb016568046 | textbox | Activated:
f6525ac1-6c13-4e6c-8fb2-535028d2a5c2 | checkpoint-no-value | Alarm Lo-Lo
477fc033-a107-54bf-acc5-27c13e880a74 | textbox | Activated:
4a4131f9-c2d1-48bd-885b-ce97f2866b6d | checkpoint-no-value | Alarm Hi
70391dba-f211-50c9-87d0-833df64590ce | textbox | Activated:
9c85d819-6989-4cd9-9ebf-41324e1c835f | checkpoint-no-value | Alarm Hi-Hi
4e3eb6bc-65ad-5870-b2e9-3e7af224c4e4 | textbox | Activated:
dcbc942e-afcb-44a5-82c5-8cefe1fe8136 | checkpoint-no-value | Set Point 1
f0964f5a-801b-5d72-8d1f-cb93e67f8b5c | textbox | Activated:
e1de1ced-efc5-452d-92f4-a0c37f4c5c4f | checkpoint-no-value | Set Point 2
49911ba9-a8d0-54ea-83f2-497bde88431f | textbox | Activated:
f1835b4e-170b-4fd5-bc72-1b33deba1cdd | checkpoint-no-value | Set Point 3
19e304bb-ff98-5e03-b707-8c2469cf781c | textbox | Activated:
e1bfe6ea-3a09-428b-ac6e-d3afe3d3fc83 | checkpoint-no-value | Set Point 4
89ba7c8d-5df9-532c-a4d1-bb7963a303a3 | textbox | Activated:
1fba16f3-4c6b-4b13-9e8c-29b4cc81cc69 | checkpoint | Calibration settings
31eab0d5-40e7-5aad-9c03-021da99a368b | textbox | Zero
7bbcd1a0-9dfc-5fdb-a7aa-e274b86f2b10 | textbox | Range
260038f7-30d8-5e56-b497-8b7cec945021 | textbox | Other (Specify)
001091c4-a5d3-4824-950c-46cac9f2a0fb | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
dfa832f3-b88b-4da6-b1c0-ee102444eb8b | checklist | ITR-I-10 Cone and Thread Tubing Installation |  | ITR-I-10 Cone and Thread Tubing Installation
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
089ff366-8db8-4a2f-a0de-3c836a65deba | checkpoint-no-value | General Data
836862e4-2ee5-5480-be92-2e390beb2c3d | textbox | Location:
f3987e3c-e071-53fe-adef-d6961dc1dd05 | textbox | Duty:
52227d67-48d3-5477-93d4-be69bceb615e | textbox | Reference Drawings/Hook-up drawing:
817b5bcb-636c-5873-8584-d3da6a0f478e | textbox | Related instrument tag no:
67c3a7fa-1af0-5757-a6db-9cf3cdb6bc93 | textbox | Tube diameter and wall thickness:
641085bb-117e-464f-aef6-c16cb3c51a75 | checkpoint | Cone and Thread installation - Stainless fittings
b198dca1-5fe8-5c0e-bde8-ca01afc7022c | button | Correct thread compatibility and engagement | Yes,N/A
5040f0d8-5bbd-56b0-9659-9070f2103d00 | button | Check fitting collar prior to connection - 1 to 2 threads visible at cone | Yes,N/A
5d2f36de-beda-569d-ad2d-87bbc5713d15 | button | Tube installation follows the client specification. (Supports, Bracketry, Slope, Expansion, Vibration, Access, Cables) | Yes,N/A
25a037c6-87a9-56f4-a344-905158bbc784 | button | Tube bent correctly, sufficient straight section into fitting | Yes,N/A
3825cff5-9492-5b90-b0fc-62d6e4a2fcba | button | Tube cut clean and straight, de-burred, reamed, and blown through | Yes,N/A
272724d7-16a8-4bd9-9ce8-17e72511950a | checkpoint | Cone machined face. No defects, lines, bumps etc.
e156b36f-5462-50d1-a4e8-8a4a308cba8a | note | Attach photo of cone and thread.
4c00f4e8-8964-43a7-8ad7-ec59407be98f | checkpoint | Thread cleanly cut, de-burred and cleaned.
7147c5fd-c45f-5907-b92a-324fcfc8f2ca | note | Attach photo of collar.
2ae41ab5-260e-5980-b4ed-81892b0b990d | button | Lubricate collar, cone and gland thread at assembly to prevent galling as required | Yes,N/A
79ed5d6a-5032-5aac-aa19-0019a8086902 | button | Correct Tube nut used for the right sized tube | Yes,N/A
2effeb49-3819-538d-b71c-963916d664a9 | note | Ensure No thread tape or sealant are used on tube nuts
ce29034e-276d-5cae-b28f-fcb5f94165e2 | button | Tube fitting hex torqued to ensure correct tightness, marked with pen | Yes,N/A
3bfd23b0-e15f-5e78-9152-eaa2d2c5611b | button | Ensure Weep hole is unobstructed and clean | Yes,N/A
7495e682-eb45-53d2-a53b-950e4f3b9c38 | button | In service leak test performed and passed | Yes,N/A
5e3c8b4b-74ca-5a06-b759-70347c9eca44 | button | Fitting completion tag completed and applied to each fitting | Yes,N/A
4b98cd58-41d3-4cb9-9489-3945c4e4c18a | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
be1da43d-d508-4495-a76e-2eea57b37bb3 | checklist | ITR-I-12 Telecommunications Equipment Panel |  | ITR-I-12 Telecommunications Equipment Panel
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
48345094-72bb-4b1b-8a46-ab4ebbaa79bd | checkpoint | Telecommunications Equipment Panel
37c3f6fa-c7e3-54b7-851b-9f8084288ee8 | button | Ensure equipment panel is securely mounted within the Telecommunications Cabinet in the correct location as shown on general layout drawings: | Yes,N/A
6f7b694b-5c62-5036-97a8-52843c4d1f9a | button | Check tag number is in accordance with Telecommunications Equipment List. | Yes,N/A
278fcbde-ff47-5571-a008-fc889d0597e4 | button | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order. | Yes,N/A
e20ada87-7a7b-55e8-a8d2-d3e9a9948a3d | button | Confirm equipment panel has adequate air ventilation, as appropriate to its internal heat generation. | Yes,N/A
8645b65c-00f3-5997-b36b-8183745a6826 | button | Confirm any slide-in cards are firmly fitted to the equipment panel and properly identified. | Yes,N/A
636fd1fd-6e63-55d5-8793-2749a7f71c6d | button | Check panel air vents are clean and free of dust and dirt. | Yes,N/A
fabb5c44-d645-5715-9481-4d85d352d262 | button | Check equipment panel external earthing connections are securely fitted and properly terminated on the cabinet protective earth bar. | Yes,N/A
8b506adf-59ea-5070-b47f-7f8a9601d9e6 | button | Where fitted, check instrument earth connections are securely fitted and properly terminated on the cabinet instrument earth bar. | Yes,N/A
b7b7e247-73fd-53cb-b0f7-d7cdb6bfaeb5 | button | Ensure any AC power connection(s) is securely fitted and cabled to the appropriate Power Distribution Panel circuit breaker(s). | Yes,N/A
413c18d4-968e-5abd-af56-b9749f2abac0 | button | Check sealing of all cable penetration (where applicable). | Yes,N/A
7525bf9d-3a4a-53c7-b22e-a73d8ba6d585 | button | Ensure all signal cables, including any RF co-axial cables, are correctly identified and securely fitted to the equipment panel. | Yes,N/A
b68c1b6b-f6e0-52ea-8303-b61bf60e10f4 | button | Where fitted ensure panel sliding rails are operating smoothly and without risk of damage to external cables and connectors. Check alignment of false floor after panel installation (where applicable). | Yes,N/A
d1b9edc9-2800-5b42-aefb-047bf71f0b3f | button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
8a2633dc-1acc-4067-8c0e-f875e3f950dc | checklist | ITR-I-13 Temperature Instrument Installation |  | ITR-I-13 Temperature Instrument Installation
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
269d7c43-e589-47b2-ab83-07f96e319221 | checkpoint | Temperature Instrument Installation
6a6bdcdb-494f-599b-9b9f-d89869425c3c | button | Check Instrument is labelled, nameplate details are correct in accordance with the instrument index/datasheet. | Yes,N/A
715a5f0c-48f7-5f7b-acdd-b254c67ea1c5 | textbox | Type and Size:
60baa098-0025-5341-a219-ea8879e47a50 | textbox | Make and Model:
c74cc3c1-ee96-5f1e-bf78-5bb0d69f379d | textbox | Serial No:
23740f8e-a299-5c2f-92be-2f463fae54ef | textbox | Instrument designation/equipment no
79709bc0-83d2-5a7d-8c45-9b2fe9849f4f | button | Instrument is suitably rated for area. (Ex Rating, IP Rating) | Yes,N/A
8559adf1-a411-52c4-9901-05376f205e1a | button | Instrument is undamaged, correctly mounted, orientation correct, elevation correct and free from vibration. | Yes,N/A
72f06700-4dcc-5d3c-8eb9-c18f242564e0 | button | Instrument is accessible for maintenance and clear of obstruction and debris. | Yes,N/A
571bdeb5-9ddb-5a10-b0c8-7eb0c5c9267f | button | Vent lines are directed into a safe area. | Yes,N/A
f95db7ca-f369-534e-9ab6-bb92a91e228a | button | Cable/s glanded and installed correctly, IP washers fitted, cable label installed. | Yes,N/A
9815721e-ce0c-5258-8f1c-a10b0509a5e3 | button | Impulse, hydraulic, pneumatics, lines, air headers, correctly installed and supported. | Yes,N/A
6f680931-beb1-5da6-8c22-36432028e0cb | button | Spare entries plugged correctly, using certified plug. | Yes,N/A
e03a90c9-d148-5816-8969-8c7f0f6a6795 | button | Instrument earthed in accordance with project specification. | Yes,N/A
2c01a3bd-2cfe-55bf-b4a5-ae6723fdca15 | textbox | Calibration interval
592a2cfd-d829-5964-951a-b00b81b19245 | textbox | Calibration method
804e6ffb-28cb-583f-bc71-adf74899b223 | textbox | Calibrated at
16710066-7743-4181-8802-a7c56d71bb99 | checkpoint | Instrument Power Supply
04d6adec-eb9f-5e98-9d9b-cf37f67d071c | dropdown | Supply type | VAC, 2 Wire DC, Other, None
c7ec3276-dfdf-51b9-b093-6965b353429e | textbox | Supply value:
2255c745-7d00-5c63-b9d7-4ca1b119a296 | button | Calibration sheet completed and attached below | Yes,N/A
0d8a0f2d-dae1-59b9-a94b-19f3a33ee9a6 | dropdown | Type of thermowell installed | Flanged, Welded, Screwed, Other
f07afaa7-7e0b-5479-b609-335cc96c37af | button | Thermowell details including flange size are correct in accordance with the specifications | Yes,N/A
912625b7-0780-5443-9c6c-8773ce46873f | button | Internal depth of thermowell checked and recorded | Yes,N/A
0d8f6f95-5ee7-51b7-b6a5-ad96e34891df | textbox | Depth:
072d0694-1563-5414-9da7-6e7d2daf6e39 | button | Bar material and tag number stamped on thermowell flange/exposed surface | Yes,N/A
8aaf6f40-21b3-5882-a43e-28fb33a115ab | button | Thermowell CE marked | YES,NO
11270d38-ed63-56b2-b9d6-581d8ce4e39e | button | EOL resistor fitted and correctly rated where applicable | Yes,N/A
c406aeea-d4d1-46db-bbc5-4917115f1e7d | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
8f5b5c42-4253-41b4-b3c7-dbe0c719135e | checklist | ITR-I-14 Flow Meter Installation |  | ITR-I-14 Flow Meter Installation
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
620241e3-1c47-471b-936f-6df13f1b2994 | checkpoint | Flow Meter Installation
d2d13fc9-3803-54b2-93d6-df97ab3c33ba | button | Check Instrument is labelled, nameplate details are correct in accordance with the instrument index/datasheet. | Yes,N/A
548badd8-87a3-5dad-a5cd-03f39566d434 | textbox | Type and Size:
11472ea6-2df3-5976-aa68-c498228bf7cc | textbox | Make and Model:
908e16dd-0d2c-51af-8ec5-df2a8cf656d8 | textbox | Serial No:
c555d079-ae50-53a3-9e82-bfab50e58967 | textbox | Instrument designation/equipment no
aa73866e-8a29-54f3-ab21-51edca127972 | button | Instrument is suitably rated for area. (Ex Rating, IP Rating) | Yes,N/A
4564e293-8fa5-5531-8b3b-5cce8db5f0c3 | button | Instrument is undamaged, correctly mounted, orientation correct, elevation correct and free from vibration. | Yes,N/A
353b9521-779c-571d-841d-9c8fb16418f4 | button | Instrument is accessible for maintenance and clear of obstruction and debris. | Yes,N/A
2facc962-fd2b-5f9a-b69e-737f9122d2ab | button | Vent lines are directed into a safe area. | Yes,N/A
c70e45c7-a001-5699-8f83-b647d33cc78d | button | Cable/s glanded and installed correctly, IP washers fitted, cable label installed. | Yes,N/A
b4fabc78-d67d-580a-af72-0e4c2a2496bb | button | Impulse, hydraulic, pneumatics, lines, air headers, correctly installed and supported. | Yes,N/A
959b7e64-d96e-5a73-8173-6f8fa23c60cf | button | Spare entries plugged correctly, using certified plug. | Yes,N/A
8b3056bc-d0d8-511e-9adb-9d40645d78f5 | button | Instrument earthed in accordance with project specification. | Yes,N/A
c3b4f328-5e82-5731-bc7f-8b9f592b1112 | textbox | Calibration interval
64ec83b1-d563-5cab-9f79-1ce6c6d8fc4c | textbox | Calibration method
7098b1f4-f943-53fd-99f6-2eb107aa76d2 | textbox | Calibrated at
f07d7cf5-c643-4b49-8d8c-2556a00343ea | checkpoint | Instrument Power Supply
7bd52285-fc00-5e8d-a5de-61e9106151d2 | dropdown | Supply type | VAC, 2 Wire DC, Other, None
3cfe182c-1ef5-57f4-bdc5-51ff69f8c2f1 | textbox | Supply value:
b4186f24-204d-5272-a2d8-9ea829ceea10 | button | Calibration sheet completed and attached below | Yes,N/A
b9b664e9-58ec-5977-b12c-1d41885046db | button | Ensure location and tapping point is verified as per P&ID & location drawings | Yes,N/A
7759037b-7794-5cee-9615-bde34091a57a | button | Ensure direction of flow is correct with respect to flow meter | Yes,N/A
e55aec1f-c8f3-5784-b8c3-e225154cbfae | button | Check mechanical clearance is adequate for installation of flow meter | Yes,N/A
a50f7f8c-d881-5ce7-8c86-368a2f2e9090 | button | Verify type and size of gasket is correct between process line and measuring unit flange | Yes,N/A
1df40803-fe08-59e5-8bbe-b1cb7bd44874 | button | Ensure correct nut and bolt grade and material for connecting unit to process line | Yes,N/A
6d972da0-e3dd-5ca8-8a25-e68b3843f381 | button | Verify display/cover is oriented for ease of use for operators and access for technicians | Yes,N/A
910c7ab2-36df-4399-b514-1587545cd33d | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
a777718c-a3c9-4b0a-b8c4-58c4649f0861 | checklist | ITR-I-15 Pressure Instrument Installation |  | ITR-I-15 Pressure Instrument Installation
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
ddb2fcd0-e046-4404-afe8-4ce03c558f7f | checkpoint | Pressure Instrument Installation
2b746ea0-3d6d-5798-956f-1deddcb166f9 | button | Check Instrument is labelled, nameplate details are correct in accordance with the instrument index/datasheet. | Yes,N/A
ae1eaf31-2cb5-5c75-9f47-ddebda2d2c1d | textbox | Type and Size:
d5394e3c-ab3a-5a07-bfaf-f12403a171c1 | textbox | Make and Model:
d5afc151-2500-5874-9935-92361d79f951 | textbox | Serial No:
6cccb1a4-4c1e-5e20-8687-c517f0bfeab1 | textbox | Instrument designation/equipment no
2a8bff10-0d02-5be4-9545-89a16b264dc0 | button | Instrument is suitably rated for area. (Ex Rating, IP Rating) | Yes,N/A
14883db8-72ae-5a2a-b137-dded47c36d17 | button | Instrument is undamaged, correctly mounted, orientation correct, elevation correct and free from vibration. | Yes,N/A
925a9563-5924-5340-b5ac-fb4f4fa03ba7 | button | Instrument is accessible for maintenance and clear of obstruction and debris. | Yes,N/A
f6310c26-ab94-5547-86c6-f694b9e7ca9d | button | Vent lines are directed into a safe area. | Yes,N/A
7e573cc6-68e4-5684-bca3-2dad3f02cbe5 | button | Cable/s glanded and installed correctly, IP washers fitted, cable label installed. | Yes,N/A
6fec3d3c-2dc6-5fe7-8c06-2c4a96a28924 | button | Impulse, hydraulic, pneumatics, lines, air headers, correctly installed and supported. | Yes,N/A
da552dff-d2d7-5f68-8d26-b753bcbd0c94 | button | Spare entries plugged correctly, using certified plug. | Yes,N/A
94657789-e4fe-5c57-b3f6-cc2ccb55f052 | button | Instrument earthed in accordance with project specification. | Yes,N/A
5293e854-1f81-5b3c-8f6c-305a5bfc03fa | textbox | Calibration interval
c0866615-fe84-5730-9710-5681f7ab0935 | textbox | Calibration method
98afce03-a0b1-5664-888c-5718de546875 | textbox | Calibrated at
77ad5b55-6741-4db8-8335-50d2d7dba2c2 | checkpoint | Instrument Power Supply
99ded8a4-8bce-5140-9d21-78c3730e315e | dropdown | Supply type | VAC, 2 Wire DC, Other, None
e1b04bb0-0a75-53de-a7e4-729b40c7f409 | textbox | Supply value:
ed7b055a-0567-5147-a68a-e8fd8a3625b4 | button | Calibration sheet completed and attached below | Yes,N/A
a9270fab-8e53-55e8-99f1-c8ea2fc0fe37 | button | Instrument mounted as per hook-up drawings | Yes,N/A
ebc5b7d7-7ed5-5a3a-a36b-20e9f6e4ddfa | button | Air line/Impulse line are correct material to site specifications | Yes,N/A
e2507f02-836f-5457-b30f-8d35db4fedea | button | Air line/Impulse line are routed tidily and as per hook-up drawings | Yes,N/A
30955280-5bd6-5ae6-8a04-17d70e1df30b | button | Correct bolt size and material/grade used | Yes,N/A
f15d2a76-8895-5c86-9aa4-176c290d53cb | button | Local indicator is mounted and easy to read, easy access for technicians | Yes,N/A
b4969649-ff14-5eb7-b1b0-4ad222e8c47d | button | Instrument and tubing are adequately supported as per drawings | Yes,N/A
01d03224-9ebc-54ed-b088-f0f8e9f73c81 | button | Isolation valve installed | Yes,N/A
6d41ae6f-5122-40e3-8238-029f5eb3ded7 | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
a0cf32cd-9bb2-4af9-bf20-037c874f18df | checklist | ITR-I-16 Level Instrument Installation |  | ITR-I-16 Level Instrument Installation
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
e369d01c-ba1d-4be8-9bbd-f97f055b1e98 | checkpoint | Level Instrument Installation
4f5632f8-8a40-5293-ac07-ecfdb8b72c83 | button | Check Instrument is labelled, nameplate details are correct in accordance with the instrument index/datasheet. | Yes,N/A
10ba450c-1816-573a-9794-d4718d9cfbe6 | textbox | Type and Size:
c6330cec-42ee-5957-8dce-e9e3e971dd9b | textbox | Make and Model:
cc02d3b6-59a9-5eba-85bf-a7ba8bc9d9fa | textbox | Serial No:
e16f8068-e810-587c-9e80-660ca711a5e2 | textbox | Instrument designation/equipment no
a94a7761-d7cc-5fc1-b553-1885444a2ea7 | button | Instrument is suitably rated for area. (Ex Rating, IP Rating) | Yes,N/A
5bbdd757-9161-5919-84a2-c33dbbfd9f98 | button | Instrument is undamaged, correctly mounted, orientation correct, elevation correct and free from vibration. | Yes,N/A
7b38804c-b656-52fb-ae93-79a50b06b6cf | button | Instrument is accessible for maintenance and clear of obstruction and debris. | Yes,N/A
f7ab8c31-e516-5c20-9393-201945b128cb | button | Vent lines are directed into a safe area. | Yes,N/A
61f504a5-8b36-5b41-a758-6cf2217685b2 | button | Cable/s glanded and installed correctly, IP washers fitted, cable label installed. | Yes,N/A
d143451f-bb26-532a-9337-b3f0a0dfa302 | button | Impulse, hydraulic, pneumatics, lines, air headers, correctly installed and supported. | Yes,N/A
65a6137a-b1ff-5ef9-bca8-157f9677a499 | button | Spare entries plugged correctly, using certified plug. | Yes,N/A
34f0b00d-8f3b-54ed-9d8d-d4b7c2b70198 | button | Instrument earthed in accordance with project specification. | Yes,N/A
956bbb10-2219-50b5-851e-89dbcbbcdeea | textbox | Calibration interval
18dc4966-6e9e-5c92-89ca-423accc7b458 | textbox | Calibration method
8de81f63-2e3c-5b56-975d-69f143b114e2 | textbox | Calibrated at
dcec1d94-3129-4c71-be45-1b0dea62c37a | checkpoint | Instrument Power Supply
97581e84-7ac4-5664-a87c-981a244bef35 | dropdown | Supply type | VAC, 2 Wire DC, Other, None
b084c983-b7fc-5bad-930f-2649dabc647b | textbox | Supply value:
10c88007-9913-513a-b5cf-b8551addcffe | button | Calibration sheet completed and attached below | Yes,N/A
b31225a3-9c7f-5bd7-a15b-533f9657e654 | button | Level Instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
87ae1bc3-a239-516a-860e-54422c677f8d | button | Level instrument mounting equipment is adequately sturdy and correct materials used | Yes,N/A
84eee38c-3c22-5190-a8eb-74a58f1e37fc | button | Bolts and studs are to site specification | Yes,N/A
1cf16dfe-10e6-557c-aa2f-61eddf1aa74f | button | Ensure location and tapping point is verified per relevant drawings | Yes,N/A
fefb07fc-db0c-5775-bfca-b6f57fe46003 | button | Ensure gasket and studs are used as per specifications | Yes,N/A
430623ad-817e-5f4b-aaa0-1e2cacc7085a | button | Verify contact type sensor probes are installed without any resistance | Yes,N/A
2455155e-73a6-59be-8667-b0673d38ce03 | button | Verify antenna/source are installed correctly | Yes,N/A
0764ce1a-b3c7-5859-9b4c-69ad9d2e5b35 | button | Ensure display is easily readable by operations and access is easy for technicians | Yes,N/A
13a49aab-a168-43e6-a5ec-1c58c5aec42e | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
d208d0ed-b66e-4d94-8360-ce5c2e2c8a76 | checklist | ITR-I-21 - Instrument Cables |  | ITR-I-21 - Instrument Cables
7bd502a5-f36e-4866-bcfa-88f07380c345 | section | Details
29c7fc72-e64a-462d-8878-ba307de02dc4 | checkpoint | Instrument Cable
c26afd48-238f-5685-bd6c-178e6154a278 | button | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Yes,N/A
78bb052b-2088-5dee-8e8d-e538a157c06a | button | Check dressing / cleating, cable undamaged | Yes,N/A
61c0b238-80b8-54cd-bec6-4cc71b7871fa | button | Cable mechanically protected | Yes,N/A
0e0927c7-8bb3-546e-aab5-436d30320f45 | button | Cable terminated with correct lugs and crimped with the correct die. | Yes,N/A
d1cc7599-8d0c-5e62-a95e-6265679ada07 | button | Screen correctly made off | Yes,N/A
f8b8c00c-2cc5-50b7-9d10-0cb618ed3106 | button | Glanding / Locknuts correctly installed. | Yes,N/A
bc934d9a-4391-5336-8691-25807358b0d7 | textbox | Gland type - from: |  |  |  | Haz. Area Rating
43c9f0f2-7f72-5971-9660-2bdc0c51ce08 | textbox | Haz. Area Cert Details.
bf0efd63-a849-5a72-8282-2b50315a234d | textbox | Gland type - to: |  |  |  | Haz. Area Rating
823fa259-9913-56da-b9ad-6577e75b2d53 | textbox | Haz. Area Cert Details.
5695d0b0-2dad-5bfe-bbeb-9514c52446c8 | textbox | Confirm spare cores and shields are terminated and conform to drawings and client spec.
e93a3567-5932-4171-99f8-8d737f720f73 | checkpoint | Electrical Checks
699eb36b-f249-5644-a3c9-4a97efb0403f | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
eca2dbcc-a6b2-4b89-885f-9734cb90ca78 | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
d7249779-f2dc-4b1f-a3f2-e9fd4bddccff | checklist | JHA - Job Hazard Analysis |  | JHA - Job Hazard Analysis
367b959a-31c0-486b-9798-c8074ef29bd6 | section | Job details
844716ee-598d-4e93-8098-c5a1b98194db | checkpoint-no-value | Job details
d73afacd-fc5f-53b9-a07d-f675a0b9e31a | date | Date:
cc7d5829-8af6-582a-a833-dc29e4955ba7 | textbox | Permit No.
0209e583-f13d-565d-a8c7-3ea6a1ca436e | textbox | Job No.
ad0ecca4-9f7b-593d-8c73-84473675dd96 | textbox | Site
0421a179-094c-515b-b75c-9029c84465bb | textbox | Activity Location
cbfad55b-10fd-5191-b98b-8378abfa80d4 | textbox | Asset:
e0cc8654-ee08-5185-8a03-a27d395343ec | textbox | Work Details:
4912e8dc-cfe0-4e53-aa01-c3309f10f9a4 | section | Prompts for Hazards - Mark all that apply.
7c8b2a7d-4947-4fd4-84ca-21e2505358ca | checkpoint-no-value | Prompts for Hazards - Mark all that apply.
d861a012-41d8-5336-a006-0601b1e9336d | tickbox | Sparks/Open flame
0006f2e0-1147-56ac-b869-13783cb35735 | tickbox | Disabled safety device(s)
b23664ec-1bf7-5714-af07-a84376bd9740 | tickbox | Uneven surfaces
c8183bb8-9b3f-558c-9cec-17ed696cc6a4 | tickbox | Fatigue, over-exertion
6b6e7932-20a0-5cbd-bfe4-4c2b9a45256a | tickbox | Crane movements
c6734840-900b-52ff-9a98-cfcc11ada84a | tickbox | Moving/Rotating parts
5a745015-b2ae-5e18-a5df-ddcd2350057f | tickbox | Remote area, working alone
e0e71479-32cf-57e1-990a-c8e186abde14 | tickbox | Conflicting work/SIMOPS
61e26cd4-97e2-5d6f-8270-6a10a2a9c8f3 | tickbox | Electrical arc flash
3c4b13e7-3980-5666-8659-e6fccb457644 | tickbox | Sharp objects/materials
1bb7aac1-f5cf-5881-adad-6cca616fef38 | tickbox | Restricted/Difficult Entry/Exit
13909cae-9c7e-5583-93d2-bcdcced8576f | tickbox | Overhead obstacles
64e032c9-2892-54a5-84f9-93cd0676e25b | tickbox | Ignition sources (other)
7d26ef84-f130-5e0f-8b56-aef1502cde24 | tickbox | Access/Egress
b8704016-9150-5d92-830d-ddc551b2ac95 | tickbox | Water body
020ce0f4-b45b-5a7d-acb3-39b14bf06aa4 | tickbox | Live equipment
d1a4dfcb-da0c-5158-94e7-86784ec6a6c7 | tickbox | Slippery surfaces
e9c25dd6-02a3-5cc2-8499-8a6f2b7e7225 | tickbox | Suspended loads
67a205f6-6314-5112-9625-e5585067dccf | tickbox | Hazardous substances (chemicals)
450ef1b1-30c4-5bae-a134-14f6d6b4faa4 | tickbox | Use of non-intrinsically safe equipment
a147d81a-bcdf-570e-b635-4d465d95d593 | tickbox | Weather extremes
b99477f9-fa30-5fcf-b9e1-ddff56a9531f | tickbox | Moving vehicles
a6d727f6-75b6-5b4d-b88e-e4d539f077ab | tickbox | Task related noise
678d2a9c-c647-54f0-b0ba-35c3ee8d9bd8 | tickbox | Engulfment
78b5300f-03cb-5907-a348-92f27654767d | tickbox | General waste
0de12bb5-1ab4-51e0-bcfc-7608c96a062d | tickbox | Hazardous waste
84c782e0-72a5-5ea3-adf5-811e06bece92 | tickbox | Hazardous/toxic substance, fumes, gas
417942ec-1ebe-590e-b693-347aa4adb403 | tickbox | Flammable materials - Gas, liquids, solids
aace0207-0b95-5309-b235-af35918e9575 | tickbox | Reduced visibility, lighting
fac86e44-c910-5401-99ba-c8ab87a551da | tickbox | Electricity
87fa19db-3704-5f97-bc5a-a4e515ad453b | tickbox | Static electricity
6208f132-8822-5832-800e-63afc0b3f656 | tickbox | Work at height
3fe2f8fb-db5d-5973-8cfa-061f978f8989 | tickbox | Underground services
4fb6d000-067e-5077-b2d6-4834b8469f12 | tickbox | O2 Deficiency/Excess
1641a091-59f5-5186-b466-09e3e83133e4 | tickbox | Temperature extremes
25571961-00d0-52bf-b936-8c4edc984165 | tickbox | Heavy objects
b1f4da6b-56bd-587f-ac6b-3a12dfee2876 | tickbox | Radiation
e9ee4ab2-df02-5053-844c-21e2e0c1e9ab | tickbox | Potential energy - Tension/Compression
d8b2bb0a-e364-55f3-a787-6f37aaa00fd7 | tickbox | Flying particles/Dust/Objects
e90f856f-6dc7-5c8a-a930-f2ec427b06fd | tickbox | Vehicle entry
001c08fb-252a-5692-857c-c9895a909900 | tickbox | Exposure to process temperatures.
f2e920b0-d4e4-4c56-aa65-a494ec5e98c7 | section | Prompts for Initial Consequences - Mark all that apply
c8a97056-9986-44da-9318-1dacb4b6bacb | checkpoint-no-value | Prompts for Initial Consequences - Mark all that apply
ada79b0a-b326-5fa2-8f70-9d6092f64061 | tickbox | Falling/Dropped objects
2e66b34d-bd2d-5335-8071-20ea4f2865ac | tickbox | Fall from height
2de6ffd5-32bf-56ca-a019-849d9aa52f1a | tickbox | Trip/Slip/Fall
33372931-1e12-5e55-a4ef-36b5513d7c43 | tickbox | Gas release
23aa8ea6-e0e4-57e5-b0f0-073db18251ca | tickbox | Pressure release
6e32f2c1-06aa-5217-9728-ba384c4f230a | tickbox | Struck by object
05aad929-efd2-54e7-b4ec-634cefd1b623 | tickbox | Exceeding tool limits
3fda1d54-299a-5da7-a1e1-087cb4ce92b8 | tickbox | Overloading people
6bd42cdf-f11d-5537-a962-c13858b9f465 | tickbox | Unplanned shutdown
ca1946df-e546-5caf-8c95-eee042a5ae8d | tickbox | Exposure to O2 deficiency/excess
18e4d98c-62cb-5bdc-9517-10a7231c72c9 | tickbox | Exposure to hazardous substance
114171ae-9b37-596b-981f-1e816cd4c989 | tickbox | Entanglement
c334b135-b764-53f7-8593-404a1305cdb6 | tickbox | Flying objects
86ce07e5-2bdd-5d9f-b17e-f91fc6d6b5f0 | tickbox | Loss of control
71803041-0bb8-50f0-a837-a46e144900d0 | tickbox | Loss of containment
ecc82886-d3d9-59eb-8f7c-9c9dc40b7d1a | tickbox | Excess exposure to Emissions, dust, fumes, noise, fibres, heat
86fef76a-ae81-5cf6-92c3-454bb21598a3 | tickbox | Loss of structural integrity
f1a33d27-f430-56e6-8c06-e65cbd74f5b6 | tickbox | Equipment failure
87ae9c7e-c018-55f3-ab02-7ad812185dd5 | tickbox | Uncontrolled ignition source
6730112c-e576-552f-a986-7cad538b1e4d | tickbox | Collision
b5932100-0408-50a7-8b45-fa670d7654eb | tickbox | Ignition/Fire
38d134ed-2ba9-5359-81a3-89f47c08e285 | tickbox | Back strain/Injury
83c22e6c-aa5b-50e7-bb47-73c688ef78a4 | tickbox | Burns
a4c40c53-c415-53ed-8adf-aeb817b2b1d4 | tickbox | Heat exhaustion
52248038-2d25-41e5-b09d-8075ead64394 | section | Initial controls - Mark all that apply.
b56aa456-fb85-4e8a-aef4-d4706d56a553 | checkpoint-no-value | Initial controls - Mark all that apply.
b5f8375f-f7a4-52ae-9e44-82e266da57b4 | note | People controls
40ec1de9-37c0-5c52-8083-100630cc2f63 | tickbox | Safety/Fire watch person
0bb56a3a-4f2f-5989-92e4-86931a0bd06a | tickbox | Barriers/Flagging
6c652daf-043d-53da-9aca-a89985c4d2fb | tickbox | Warning signs
cb795045-8821-5d91-964b-6ac7cefc6f05 | note | Equipment controls
ba172de8-1723-5ca1-bebf-3dfd24efa46c | tickbox | Master tags and locks
8cf662b1-85d7-53ac-b364-13d2aa6d7706 | tickbox | Scaffolding for access
b486d1b5-6711-5a68-b9fc-67df08b45e11 | tickbox | Radio communication
c754a3b2-2aff-50dc-84da-5ba23831ffcf | note | Environmental controls
e7a89826-bfce-5f83-ac38-3eabbf0e8a5a | tickbox | Ventilation
fce464d1-b598-5b66-ae11-263db4aebc6f | tickbox | Lighting
b933bbf9-8111-5e52-9aca-eb7e6832d865 | tickbox | Gas Testing
64d8dfb8-8a88-5ad3-98f7-4232822553b5 | note | High risk controls
03b5a920-941c-5b28-8f65-e46882f34340 | tickbox | WSCS Work permit
f5825dea-75ea-5bfb-a09d-5fd26f9f9f60 | tickbox | WSCS Certificates
ea53838a-de12-5e6c-8b84-c0e3f69a039e | tickbox | Critical lift/Fall protection plan
4c29b0e2-4762-5073-b791-17bf36a16d4e | tickbox | Specialised PPE
6f057333-7556-51c9-904e-4dec9439a180 | tickbox | Spill kit
f631a6b0-cc4a-5ae5-b73f-2ec9abbba9c2 | tickbox | Fire extinguisher
0b42f5c6-b5ac-4e18-9128-b2c2c1796e55 | section | Signatures
28d675b5-d597-454c-b6ff-7feed5edfd07 | checkpoint-no-value | Signatures
58f539bd-a904-4587-90b9-e5df637863bd | signoff | Applicant signature
ec5cd9b2-f61b-47e0-8d72-83777ba90ddf | checklist | JHA - Job Step |  | JHA - Job Step
5811ffb5-94b6-455b-9ecb-d504990e1de3 | section | Task Step - add task step for each individual task
01d3089f-c034-408d-9767-2e5d9e3d0b09 | checkpoint-no-value | Task Step - add task step for each individual task
9386b4d6-9569-5447-a7ed-183a2fed9e54 | date | Date:
dbc4f1e5-f9da-5ddc-bb62-3186ba53fc9d | textbox | Task step number (eg. Step 1, Step 2 etc):
54bd3e80-8181-546a-acad-09aa938e4012 | textbox | Task details:
d4efd8ce-ff70-5741-a854-07a3ac049c3b | textbox | Hazards:
ba7e3b31-f0b1-5728-bf3a-a54b8bdc520f | dropdown | Initial score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
e2113dac-a748-5fb5-ba8d-1f0d5943835a | textbox | Potential consequence:
7c491d01-adec-5adc-8091-d4bfcc3b63f0 | textbox | Controls:
88e33cc3-5e88-5cbf-85a7-c6b3fa158aa0 | textbox | Recovery steps:
cbb5bde6-8396-539e-a371-8f0bc93b8566 | dropdown | Residual score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
1d814334-7cfd-4391-8677-2212d7cffe1c | checklist | Low Voltage Cable - Drum Test |  | Low Voltage Cable - Drum Test
d4b54c40-4bcb-43ea-9f8a-a16d0f2f423b | checkpoint | Low Voltage Cable - Drum Test
5bf962ef-b716-58c4-a95c-45a92ff14122 | date
1c4c8345-fd23-4400-b443-7cc3c5c1a5fd | checkpoint | Cable type as cable schedule.
ae30a6dd-078f-4efc-bf80-bd1440414778 | checkpoint-no-value | Cable legth:
5eb09cc0-80ea-5035-8169-8f062fdac67b | button | Cable undamaged - Visual inspection | Yes,N/A
f2cc14a8-6ed2-49de-80e2-ea3874452b42 | checkpoint-no-value | Electrical Checks
d1216562-401e-55c1-a312-38031db15b6c | textbox | Record test results: Insulation Resistance, Continuity, Other.
1b795185-3e3c-46a4-9e64-f74ad3f01e5e | signoff | Installed by:
14b36b3e-da59-4ea5-bb45-f099152c6acf | checklist | MSDS |  | MSDS
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
6be55d6f-996e-4484-a2be-155f9601b6e8 | checkpoint | Please Upload MSDS Sheets
eae56ce8-f60c-48b3-a1f3-94a5e76eb8f6 | checklist | Record of Inspection (ROI) |  | Record of Inspection (ROI)
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
d20643be-2e4b-4e04-8679-f2860bb4aa45 | checkpoint | Please upload Record of Inspection here when complete (ROI)
bfaa09ee-76ae-4093-bc22-0de62d023e78 | checklist | Test Equipment Details |  | Test Equipment Details
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
7049c5ab-7e9a-4fe6-8e93-3b8888099745 | checkpoint-no-value | Details
c72be79d-3a6d-54d6-b55a-32929cba9523 | textbox | Make
500a2cb1-f22d-5a13-839a-cdf6f614f9d5 | textbox | Model
f0805bdb-05aa-53ca-adde-c0465669dbb4 | textbox | Serial No
559d358d-ff53-552f-ae29-05742d970f31 | textbox | Calibration Expiry Date
103934cf-9252-4c42-8881-ff6d2e1d212e | checklist | Toolbox Meeting |  | Toolbox Meeting
8e06c923-cd64-417e-a061-6cadda90b587 | section | Toolbox meeting
03b7ee45-9925-4ee4-86c5-e6dc6f27ae99 | checkpoint-no-value | Toolbox meeting
6d0e949e-139b-54bc-ba83-a89b17136bb8 | date | Date:
137e8e51-5225-55dc-a330-2c2862083aa7 | textbox | Meeting location:
495f191a-011f-5006-980d-f33f3d063ae4 | textbox | Meeting conducted by:
500c9feb-5a7a-5823-b477-bd5c14a64efb | textbox | Meeting attendees:
cb21558e-ef12-55dd-8859-cc0660420e3d | textbox | Today's work scope/Hazards
7faa4d02-7838-5234-866d-ec555493f7ea | textbox | Hazard controls:
3aba7a16-51d8-4b21-aa89-5931ec544c31 | signoff | PICWS Signoff