## Master List Templates
Id | Type | Name | Values | Prompting Name
477fe336-12c7-4ed9-ad17-ca897c5474a9 | checklist | Access Control |  | Equipment -
0e0f0a3a-a59f-4708-9490-da4071c64b1a | section | Pre-Commissioning
56b4d59c-2afa-4c4b-8d8f-01153e936909 | checkpoint | Precommissioning report
3883d431-e012-4301-89e6-3b9e4cf05c5f | section | Commissioning
4dae96e7-d1ff-4f0b-9398-58e7755a4fee | checkpoint | Commissioning report
23547c4e-effd-45cf-b0b0-f4f1168c3847 | checkpoint-no-value | Mcconnell Dowell
4e993070-3cb6-4257-b201-28e4b088411c | signoff | Request McConnell Dowell Signoff
68c61f93-0c1e-4ef6-91ec-e931fb0bea00 | checkpoint-no-value | Beca
bbb7e61a-eaf3-4c85-9c5f-c37393260396 | signoff | Request Beca Signoff
3caab129-1204-4346-b9e8-2377ac98f1bb | checkpoint-no-value | FIRP Signoff
d8155074-a1a9-49ea-891e-6ad4959ebae9 | signoff | Record of Witnessing
65782946-f789-449d-8ea0-70701db801e9 | checklist | AHU |  | Equipment -
592082d8-f018-4342-8994-5fae5aabe85b | section | Pre-Commissioning
36b93de9-a6ce-4829-be87-b6746755aabd | checkpoint | Pre-Commissioning Test Report
502e82e9-0de5-4bf5-a6ae-9f454c7da077 | section | Commissioning
352d973f-af5f-4897-9f3a-3a396c026402 | checkpoint | AHU Commissioning report
2cf02a48-eb03-4439-97bf-1fddedf6ccf6 | checkpoint-no-value | Mcconnell Dowell
b11a8319-8325-46d4-a22d-e71ac658e786 | signoff | Request McConnell Dowell Signoff
55e5e85b-7eab-4350-a095-5878354f392b | checkpoint-no-value | Beca
cf344d85-838e-4cdf-ae98-220f0c9f3f3d | signoff | Request Beca Signoff
38311721-d6ea-446c-91db-c13021ea70f1 | checkpoint-no-value | FIRP Signoff
ca50a6e5-5fbc-4dbd-be1a-d9b50606d21a | signoff | Record of Witnessing
600bac5d-dc2e-4714-9376-6cf24c02822c | checklist | Air Quality Monitoring |  | Equipment -
d9a7ec7a-2091-4d94-9c97-f0c995793da7 | section | Commissioning
8f41dab9-f83d-4c7f-81f1-21d302c266ad | checkpoint | Air Quality Monitoring Report
b2016130-9b3d-410c-83dd-4aa0c048c332 | checkpoint-no-value | Mcconnell Dowell
627e54cd-4bea-4c56-bde0-69562838e493 | signoff | Request McConnell Dowell Signoff
d11d59da-ff07-4f9f-ab6b-6e4fa8322507 | checkpoint-no-value | Beca
b3aa781f-9053-420e-97f0-4b642929e472 | signoff | Request Beca Signoff
27cfafa0-a831-4337-9211-68caa1ddd003 | checkpoint-no-value | FIRP Signoff
db684876-ee50-476a-a68b-1f7d0bbe927e | signoff | Record of Witnessing
0954b564-8c82-4e91-8639-79ca780fc985 | checklist | BMS Functional Test |  | Equipment -
a690c1fa-2b39-4ec6-9bcc-da139074e6b9 | section | Factory Acceptance Testing
4cf9c48d-f40c-49dd-b0c5-0a4d12635b94 | checkpoint | Factory Acceptance Test Report
65bac459-e06a-4c28-8f16-0cc0b94d1dd2 | section | Pre-Commissioning
e4d48bbd-ed74-4aba-93ee-ced84aa7467b | checkpoint | BMS Point to Point Testing Report
ecb48c42-a05d-473b-84e2-b90721ac8c06 | section | Commissioning
e5c64bc7-333d-417d-9f00-ebe109823286 | checkpoint | BMS Device Commissioning report
82c0d72d-66a2-469a-94ed-97bcd1d76a47 | checkpoint-no-value | Mcconnell Dowell
578d1148-deac-4cfa-a45c-cebcfa7a0123 | signoff | Request McConnell Dowell Signoff
a028d332-b92b-46bf-9814-b48f4570866c | checkpoint-no-value | Beca
8d031cca-de98-4ca8-95f3-7e15cfb16999 | signoff | Request Beca Signoff
ac5b83d8-2a40-4279-8913-d03ba2243ce5 | checkpoint-no-value | FIRP Signoff
c6a664c6-462a-457c-948a-66e01666f067 | signoff | Record of Witnessing
575ebff8-b834-4391-a736-9c08c87d1dc8 | checklist | BMS-MCC |  | Equipment -
a1b98d38-590f-48f5-b517-e1f6923fdc68 | section | Pre-Commissioning
8b38987c-63c5-4942-92d6-da04a48a048d | checkpoint | BMS Point to Point Testing Report
826c852c-6b89-4d97-b5cd-12b1707f1993 | section | Commissioning
224cbb14-c75f-4953-aac7-19df38917325 | checkpoint | BMS Functional Testing
4235226e-da83-4415-92d2-38d88671b862 | checkpoint-no-value | Mcconnell Dowell
84038f91-1415-449a-8b69-85e0dc1ec39b | signoff | Request McConnell Dowell Signoff
70e61c35-ccd9-4e21-8685-12f0fc80f139 | checklist | Building Distributor |  | Equipment -
2c0a934c-0b71-4226-b87a-802c9d3ff789 | section | Pre-Commissioning
6dda2b8c-706c-46cd-a177-87f487310cf6 | checkpoint | Precommissioning report
9328ed52-c450-4f93-8366-39c738df3f06 | section | Commissioning
ffef2923-89a4-4f9e-93f8-dc0350c3f4cc | checkpoint | Commissioning report
de0703f4-5881-4396-8057-7a5b70a59e3d | checkpoint-no-value | Mcconnell Dowell
e67a8db6-dcd0-4423-b978-fcee688e8286 | signoff | Request McConnell Dowell Signoff
c5d56100-a5e6-4366-b3c2-2fac54394975 | checkpoint-no-value | Beca
034a9abe-70c8-4fea-af67-52eece0b5f89 | signoff | Request Beca Signoff
aa0cf5c7-b153-4ff8-a6b8-52f137cf4e88 | checkpoint-no-value | FIRP Signoff
697f0a34-0e05-4595-a3df-926346ccdfbc | signoff | Record of Witnessing
9c19a6c6-10eb-4533-8d3f-60e378a80d94 | checklist | CCTV |  | Equipment -
2cdf8ba4-c91f-4514-a92b-1a4178788ec5 | section | Pre-Commissioning
b1253691-3105-4c80-a232-95bd4d4426a4 | checkpoint | Precommissioning report
5c7117e2-a7d1-41a6-bab2-aeca1f0d18cb | section | Commissioning
8887a3f6-7ed1-46ba-9b27-99867336c0bb | checkpoint | Commissioning report
e88c68c4-d8bc-4faa-8e96-4bae42afbe4e | checkpoint-no-value | Mcconnell Dowell
3444818a-2d73-4ae2-80c0-966232c79481 | signoff | Request McConnell Dowell Signoff
6557cdb7-04b4-44e7-a5f2-b145e03ae103 | checkpoint-no-value | Beca
eee954a8-848e-47e9-b713-3af5eab95364 | signoff | Request Beca Signoff
b8f30ef7-77ad-4c5b-bd87-6b36433c7e57 | checkpoint-no-value | FIRP Signoff
3d5aa90b-7149-4ba0-829e-9a2937e60e9b | signoff | Record of Witnessing
49b4fddc-cd7e-45b5-a01a-76c0bfaf4b2b | checklist | CDW Pipework |  | Equipment -
2e85c341-c4a1-4d49-a730-3505df9ca4bb | section | Pre-Commissioning
32d30343-2da7-4c29-b457-decc70e7fa1e | checkpoint | Pressure Test and QA Record
c8f0d31b-766a-402f-bfd3-73b08febfdc0 | checkpoint-no-value | Mcconnell Dowell
737a6656-f529-4552-abd7-97b24e606d5f | signoff | Request McConnell Dowell Signoff
61d6ac46-3f9b-4ad6-b38f-c349bbd70b63 | checklist | Chiller |  | Equipment -
414b02de-e2d2-4d17-8183-693112f133df | section | Factory Acceptance Testing
c71f8123-cf95-4f3a-a3f4-f26e087b3988 | checkpoint | Factory Acceptance Test Report
4bd6cc4a-5055-4665-908a-43263fee3bd1 | section | Pre-Commissioning
936a7359-8f6f-48c1-bec7-9e82bd1ce758 | checkpoint | Pre-Confirmation Check sheet - Trane
58be8063-5054-4d04-b968-9fd934723e64 | checkpoint-no-value | Mcconnell Dowell
dff79650-501f-408f-beb3-64d007346585 | signoff | Request McConnell Dowell Signoff
33a63581-ceb5-4ff5-8e18-0ccba4790653 | section | Commissioning
190cbe60-54ea-4a1c-bbb7-f230cc9dab84 | checkpoint | Commissioning Check sheet - Trane
7552b0b8-af07-461d-9dd0-7e4e9ad247c4 | checkpoint-no-value | Mcconnell Dowell
dd0f8e1a-833e-4cc2-83fc-ceeca1457800 | signoff | Request McConnell Dowell Signoff
a4bd43d2-45ab-40bd-98e7-30897b0539e8 | checkpoint-no-value | Beca
64f3fc2a-eaa4-401a-bf42-fc7507fd2d10 | signoff | Request Beca Signoff
768aed40-3bb3-4cb3-9efe-2c4d5916c60a | checkpoint | Completion and Certification documents
83a567c1-0c88-4efa-bdb9-a221e03a3809 | checkpoint-no-value | FIRP Signoff
cc9c3c55-4037-4a84-948d-57c4acca0352 | signoff | Record of Witnessing
377f9656-4790-436a-960e-09462057db8f | checklist | CHW Pipework |  | Equipment -
08327a5b-f363-4c7c-8c23-7621b6b01f45 | section | Pre-Commissioning
03d738c3-410a-4c02-b55b-7118eddeb002 | checkpoint | Pressure Test and QA Record
6cbfbe07-9888-4a5d-9950-9cb5312ca9f9 | checkpoint-no-value | Mcconnell Dowell
55570009-4aa6-4b5c-b512-066921068a84 | signoff | Request McConnell Dowell Signoff
4f640f62-1fa4-44d5-a329-4c47478e61f9 | checklist | Cooling Tower |  | Equipment -
c77726de-be2c-4625-a188-06e222d0fc92 | section | Factory Acceptance Testing
f7064fa8-b67e-4557-a49e-b86b09a24fcd | checkpoint | Factory Acceptance Test Report
2d7e17ea-d307-4872-b3e3-39fca8939dfe | section | Pre-Commissioning
10ab3080-da5e-4128-b818-1f4f2780faca | checkpoint | Model Number
bda6fd49-5629-57f2-8ab6-1443a61f7346 | textbox | Model Number
b6df1fc9-a651-488e-93ba-7c4d7a4dc84a | checkpoint | Visual inspection, no apparent damage
5461df65-db46-4ae5-8aaf-36952a8d947e | checkpoint | Vibration isolators installed and shipping restraints removed
c05e06f9-9ef8-4fe0-9565-e2d0090c11bc | checkpoint | Cooling tower levelled and seismic restraints installed
8a678acc-6c18-42af-a765-7aa5be8693a3 | checkpoint | Tower basin strainers cleaned and sump filled
158eb0d6-c33c-44b7-ae77-91f8add8996f | checkpoint | Cooling tower over flow installed and piped to sewer
42b3a917-59d4-4c4c-8309-81f8461b8aca | checkpoint | Fan rotates freely, belts and blade pitch adjusted (where applicable)
0249ca37-8692-4b8c-84ea-c2ad6587c9c5 | checkpoint | Spray nozzle cleaned and adjusted
10dec9e7-bb17-47dd-aef2-1d2efe62a86a | checkpoint | Fan inlet screens free of debris
e2061f95-cab2-4544-b9d6-253eae625104 | checkpoint | Pipework, associated valves and test points installed
4e6543a0-775b-4117-934d-231f3f248acb | checkpoint | Pipework adequately supported
f84c2fbc-4dde-424e-8e96-47e02fc1fbe7 | checkpoint | All N/O valves are open, all N/C valves are closed
87679845-3545-48b9-aa13-7f8590252074 | checkpoint | Pipework flushing and chemical treatment complete
3ec3fdae-c5a7-4168-a591-8da81a7f6eb3 | checkpoint | Chemical dosing regime in place
fbf55863-9505-4916-a3a0-04f318be3609 | checkpoint | Distribution header balanced
364e5362-da96-4709-81fe-0fa4287a57f4 | checkpoint | Pressure gauges, thermometers, sensors and test points installed
46fd928e-0d12-4726-88c3-a72d986b8069 | checkpoint | Basin quick fill and makeup float valve installed and set correctly
23895e0b-8c62-4e3e-8a3f-8e6fb0572105 | checkpoint | Local isolator installed in accessible position
f63caa47-bd8f-4a90-8866-a90eff3156df | checkpoint | All power and control wiring correctly installed as per schematic
857d6c51-bce9-4852-982a-18c564c11c15 | checkpoint | All connections tight
9b5b6374-090f-48be-b078-0757023e6d52 | checkpoint | Cooling tower fans energised, rotation and vibration checked
0c024cf1-acea-4026-99a4-fc8ec44f9664 | checkpoint | VSD programmed and integrated with BMS
52a9d94d-8007-4aa8-a166-bfcb5d58d9bd | checkpoint | Controls point to point checks completed
2b2fe2c7-2dcd-4af5-8df2-08ba5e6f6e1e | checkpoint | Adequate space around towers to prevent short circuiting
aa533c5e-cb9b-491a-aafc-50236e0a9f0e | checkpoint | Condenser water pumps operational and tested
2ce231cc-c0a8-4b2b-8762-528a80a35273 | checkpoint | Condenser water system complete including pipework, valves, pumps, chiller connections etc.
89f4612c-f2f0-4b7e-8383-01751dae5c44 | checkpoint-no-value | Mcconnell Dowell
da4c3fdf-6c41-4668-bdd8-9c120c5b351d | signoff | Request McConnell Dowell Signoff
c3d1eaf1-f903-403e-8386-921f20f7c1c4 | section | Commissioning
3ce1b261-07c6-456b-92e0-0596f87d0e9c | checkpoint | Cooling Tower Commissioning report
78a418ad-5832-49fe-923c-f1bee79fe812 | checkpoint-no-value | Mcconnell Dowell
43f3d870-5cc5-4f45-ba85-a33edd37db95 | signoff | Request McConnell Dowell Signoff
95944b21-3f4a-4a94-8db5-d1511ba62579 | checkpoint-no-value | Beca
bbef3df9-0904-47bb-ad62-fe691593bcf2 | signoff | Request Beca Signoff
84b69755-edc9-42f6-a743-a908907c5352 | checkpoint | Completion and Certification documents
545d2990-deba-4545-b1eb-398d0349b01e | checkpoint-no-value | FIRP Signoff
be158370-f8dd-4f5d-a830-c94fb58bf8c6 | signoff | Record of Witnessing
81346ee0-3ce6-4802-97e9-af68dff65871 | checklist | DC Power supply |  | Equipment -
416c4381-5ecb-47bb-89c9-48195a12d3ba | section | Factory Acceptance Testing
4b5d54e0-5927-40b0-9c50-cc30665c09b4 | checkpoint | Factory Acceptance Test Report
27943260-5edd-46b6-8bcf-aad83a5c4690 | section | Pre-Commissioning
cdf1d9b0-7460-4429-ba28-1ca6618560d1 | checkpoint | Site Acceptance Test Report
c63749dc-7117-48c6-b34e-84bbe13ead51 | section | Commissioning
81ecfa6d-442b-4cae-9dee-66b5a246dc00 | checkpoint | Site Acceptance Test Report
b97af176-6b3f-4609-a281-472fdf2001f5 | checkpoint-no-value | Mcconnell Dowell
9a5c9682-f71c-4350-aaf4-31bd9dd1a8b1 | signoff | Request McConnell Dowell Signoff
4024ab94-b0ae-4ca9-a6ee-6231eb38b75c | checkpoint-no-value | Beca
6ce2bdc2-c761-42e5-88fe-9742a63506d0 | signoff | Request Beca Signoff
83b1d21e-3792-49c3-bd15-6e39c7f3c692 | checkpoint-no-value | FIRP Signoff
43c00469-8aae-4609-aca8-e2cd67cd7a95 | signoff | Record of Witnessing
b6cda124-574c-4034-bde0-0494bc264303 | checklist | Diesel Fire Pump |  | Equipment -
af00400d-bc7b-4277-8fbc-a93c4bc010bd | section | Factory Acceptance Testing
906f02c8-e8b2-42a0-b055-fb033c51c42b | checkpoint | Factory Acceptance Test Report
5d788b96-a452-4e5b-8edc-d0a17f0ce33b | section | Pre-Commissioning
4471786d-0c38-44f5-b28c-943cb3e7e77f | checkpoint | Pre-Commissioning Test Report
6379481e-b1ae-4b31-a054-4f909d282e95 | checkpoint-no-value | Mcconnell Dowell
1de68be1-1875-465f-991f-a69eeb1df277 | signoff | Request McConnell Dowell Signoff
316ea9e5-bd86-4dea-8b7f-52ef6a0be063 | section | Commissioning
49c18af5-2e07-480e-adb7-0661f03eec65 | checkpoint | Diesel Fire Pump Commissioning report
8e5dca3d-929e-4103-a7a4-b0148434280d | checkpoint-no-value | Mcconnell Dowell
2c56bb57-cace-4559-b0f3-f875ce0e0eb0 | signoff | Request McConnell Dowell Signoff
77c5fa7f-6725-44f8-8c9a-9ae04fe9c7ea | checkpoint-no-value | Beca
dfc26a8f-5d8f-4078-b6c0-b2c7d2f47d93 | signoff | Request Beca Signoff
f4b3b2a7-a137-411f-a553-7cfde434aa02 | checkpoint | Completion and Certification documents
01cabb25-0be9-4d74-bc26-6bc44e7ea3bf | checkpoint-no-value | FIRP Signoff
9403d2d6-0a47-4ab6-8f79-2d2f6eb9532a | signoff | Record of Witnessing
da664f44-bb4a-4b41-b3ae-91bd45a91c42 | checklist | Distribution Board & ATS Panel |  | Equipment -
edd81d8d-e97c-4b77-b4b3-d971c50b42f5 | section | Factory Acceptance Testing
497adc86-f514-4e57-a0bb-99a18a68fdf0 | checkpoint | Factory Acceptance Test Report
2ec23ff2-ff61-414d-9e7a-0adbbf12d453 | section | Pre-Commissioning
e2c75da2-1b23-4cde-b688-49b8d0fc7244 | checkpoint | Sub-Mains Cabling - Visual Check
b660b549-0c80-46be-9db9-1c053585a7d2 | checkpoint | Sub-Mains Cabling - Continuity
4cc19669-5364-52c3-9fef-bb1d9105b0aa | textbox | Continuity:
1abf5f0d-2a61-418e-9e4a-adaa829b9656 | checkpoint | Sub-Mains Cabling - Insulation Resistance
9d957c80-3648-5694-ab11-bd0ad7bd7b6c | textbox | Insulation Resistance:
54cf7725-2e65-4324-a588-79208ef8a5e2 | checkpoint | Sub-Mains Cabling - Check Terminations
b2f87359-5ebb-4251-b46c-165187d3a342 | checkpoint | Sub-Mains Cabling - Power On
ec016a6e-e526-491b-a5e7-674d9254789e | checkpoint | Sub-Mains Cabling - Test Voltage
76b6963e-c2ad-520e-8492-2a200ca589c1 | textbox | Voltage:
d6fce570-7305-4538-b046-5fa42ceac6e2 | checkpoint | Sub-Mains Cabling - Confirm Polarity
c6072db8-b71c-4872-a0bf-1ff96ee86147 | checkpoint | Sub-Mains Cabling - Confirm Phase Rotation
cda000a7-1ada-4740-a0c5-b0edfe404eff | checkpoint | Sub-Mains Cabling - Earth Loop Impedence
29f0fccb-6482-53b5-82ab-0c30277575e2 | textbox | Earth Loop Impedence:
40fcd297-e7a0-4f5b-bd9a-fe779c70e3bf | checkpoint | Sub-Mains Cabling - RCD Test Button
7a4ac23f-9a56-486a-9990-32b35501f450 | checkpoint | Sub-Mains Cabling - RCD Trip Time (MS)
32eaf3c3-ecb0-5e45-98bf-5799ae0e347f | textbox | RCD Trip Time (MS):
99f07a91-7550-4a28-8b46-b0bc5bed9bae | checkpoint | Sub- Mains Cabling - Confirm Circuit Ready to be put into service
2447cc60-41d7-4420-876c-8876e6dced00 | checkpoint | Distribution board- Confirm MSB room / position meets regulations and is finished ready to house a live switchboard including weather tightness.
b5325f4a-c568-447d-9d5c-4614e75d3365 | checkpoint | Distribution board-Confirm MSB is securely fastened
3ef80c7a-598d-468f-8e12-cd122549fd0b | checkpoint | Distribution board-Confirm supplier has completed all Site Testing once shipping breaks connected, attach results if available.
fd875436-8eab-4577-8cde-3a939153c134 | checkpoint | Distribution board-Confirm there is no link between the earth & neutral bars
dc15ec75-0764-47a5-a9fe-dd58d5a2d65f | checkpoint | Distribution board-Check that the SB has an identification label matching the single line diagram
9428e682-affc-4f31-b075-bbbd850fac15 | checkpoint | Distribution board-Confirm Main earth is labelled
591a37b5-5f96-4276-9424-bb06c945b197 | checkpoint | Distribution board-Check that there is an earth bond to the case of the switchboard
9383dc71-e4f0-42af-ad9c-fb017eb0142e | checkpoint | Distribution board-Check that metal work is undamaged and free of corrosion
7e0e5721-d7c8-484e-b73e-0d7cda684a4e | checkpoint | Distribution board-Check that MCB/isolator ratings match the switchboard schedules / SLD
9e5a74b9-c7c3-4866-93b0-1c7eb8710a8f | checkpoint | Distribution board-Check that all circuit terminations have phase identification
818df4e9-b4c4-4193-b890-885681c385ad | checkpoint | Distribution hboard-Check that circuit schedules have been fitted
356e4445-8c4c-400f-b6b4-dd33055388e1 | checkpoint | Distribution board-Check that all out going Circuit Breakers are "locked off" or tagged prior to energising submains.
98d490c5-3f1b-40bb-9103-a14459ccb059 | checkpoint | Distribution board-Connections (all tight including MCBs to chassis) - Mains
edf47f93-1a4b-48d8-a248-b5e9246b6ab0 | checkpoint | Distribution board-Connections (all tight including MCBs to chassis) - Mais Earth
268bd249-b40f-4941-9e79-3438346202cb | checkpoint | Distribution board-Connections (all tight including MCBs to chassis) - Main Neutral
0c854b3f-5cfb-4e7d-9bf5-e9fdba1ee75c | checkpoint | Distribution board-Connections (all tight including MCBs to chassis) - Sub Circuit CBs
fcf5202e-6075-4c06-88b0-c959e4168053 | checkpoint | Distribution board-Connections (all tight including MCBs to chassis) - Sub Circuit Earths
7e2a2611-30be-4acf-967c-14045bad573c | checkpoint | Distribution board-Connections (all tight including MCBs to chassis) - Sub Circuit Neutrals
7ad289e0-8fde-4bb1-a915-e26d83ad84cf | checkpoint | Test Insulation resistance between bus and earth is greater than 50 MΩ and record results.
fcffadf5-b4da-5268-a7f3-25de68918c25 | textbox | Insulation Resistance:
a5717823-a756-4614-a998-0db57dd7c33f | checkpoint | Confirm Distribution board ready for inspection by Independent Inspector
f202e88c-f4c3-4ca5-b576-00ad13860f33 | checkpoint | Once Inspection Complete Confirm Switchboard is ready to be livened
ef36f1cf-d0ba-4d75-ab7b-1495446f316b | checkpoint-no-value | Mcconnell Dowell
ab3058a6-fcc3-468a-bac5-0dc27153ca2a | signoff | Request McConnell Dowell Signoff
d3fdce46-53d4-497a-aa80-61e4f3169c1a | section | Commissioning
d2c7caa5-544a-4861-9591-5c300f4f09e1 | checkpoint | Confirm Pre-livening check sheet is complete
62ff6c25-8df7-4591-bb92-e15c86b3666e | checkpoint | Distribution board Post-Livening - Confirm Correct Voltage present - R-W
5ac6e425-7926-41d9-9936-aacb03a93719 | checkpoint | Distribution board Post-Livening - Confirm Correct Voltage present - R-B
6d20a4e0-3725-4b93-998b-06eded9ddb48 | checkpoint | Distribution board Post-Livening - Confirm Correct Voltage present - W-B
35752a61-5200-4eaa-8d8b-4fa3eed9e46f | checkpoint | Distribution board Post-Livening - Confirm Correct Voltage present - R-E
7442f732-116d-4739-a11a-cb1a9c93d6e1 | checkpoint | Distribution board Post-Livening - Confirm Correct Voltage present - W-E
c9f3ee92-83ef-44f3-a5fe-a7ec8cca0a3e | checkpoint | Distribution board Post-Livening - Confirm Correct Voltage present - R-N
59367825-417c-47be-b927-09d5a209dd05 | checkpoint | Distribution board Post-Livening - Confirm Correct Voltage present - W-N
9e93646f-dc14-4458-94de-1ac82b4e7584 | checkpoint | Distribution board Post-Livening - Confirm Correct Voltage present - B-N
d9791d1d-c8d4-4ace-be63-ae7e14b1e5a5 | checkpoint | Distribution board Post-Livening - Confirm Correct Voltage present - B-E
b8098837-92fc-45c7-9cb5-deff979507f6 | checkpoint | Distribution board Post-Livening - Confirm Correct Voltage present - N-E
ae23b6a2-46cc-407f-b538-8b3558aba19e | checkpoint | Distribution board Post-Livening - Confirm Polarity and Phase Rotation - R
b7717f1b-a02a-4194-ad82-bac5b4a05910 | checkpoint | Distribution board Post-Livening - Confirm Polarity and Phase Rotation - W
541e5a83-d734-4db9-9ff2-cd0be6e3c1b6 | checkpoint | Distribution board Post-Livening - Confirm Polarity and Phase Rotation - B
4d4a14de-abe2-435b-a9d2-f87a3ee361bd | checkpoint | Distribution board Post-Livening - Confirm Polarity and Phase Rotation - N
10dc9e70-0861-4d45-9698-add4c8bee6fc | checkpoint | Confirm correct control voltage is present
17d24caf-1410-584c-a681-3478e326c20d | textbox | Voltage:
cf99be05-2ad0-4678-95cc-0b33bf659640 | checkpoint | Confirm all meters / monitoring devices are set up with correct parameters
c98d4664-f1c3-48f7-a0bb-36594668abfe | checkpoint | Confirm all switching devices (ACB's, MCCB's, MCB's etc) are switching correctly
9acf69f7-afd4-4649-aa0c-6236749eaa8d | checkpoint | Confirm all Auxillaries Switching correctly including A/O/M
722d46dc-77a7-4af5-a9c9-16a1c9c109d3 | checkpoint | Confirm all point to point tests on controls cabling to external sources complete
8c9ad76f-00e8-4474-95ba-d92e7e7e0156 | checkpoint | Confirm all adjustable circuit breaker settings are recorded on Distribution board
4fed1ac1-50e6-4231-9ff7-4e51388e9bad | checkpoint | Confirm Distribution board is ready to be put into service.
a46247cd-a77c-4423-859c-0e93b54fe782 | checkpoint | Circuit Test Schedule
f82750f8-287d-4d08-8e65-507172aa3327 | checkpoint-no-value | Mcconnell Dowell
2ce19e48-05de-4dc4-a2c4-6816b1487ce3 | signoff | Request McConnell Dowell Signoff
a107bad4-c10e-4f42-9af7-faaf9165fb8e | checkpoint-no-value | Beca
320a19c7-cc26-4cb6-ac24-4cf86829b9d1 | signoff | Request Beca Signoff
33c72485-3aa2-4a63-b402-ddebcbffe4bb | checkpoint | Completion and Certification documents
c688e2f8-41e1-401f-854e-f18cde8ff148 | checkpoint-no-value | FIRP Signoff
8183355f-36c8-444a-adc2-351681c51789 | signoff | Record of Witnessing
9c6aba3b-4748-4084-822a-5c977ecf7229 | checklist | DS01 - Diesel systsem idle |  | DS01 - Diesel systsem idle
1778d3e3-51d7-4f25-9e30-b484f126aece | section | IST Test
cb8d1324-ecbe-4818-9aa2-7197876a4e4c | checkpoint | IST Details
9d79e3a1-7502-5858-ad96-6beea592fab1 | textbox | Test Method - Normal scenerio
a36c2058-350c-5414-93e1-213bf976bed5 | textbox | Area - A40
7bcac3ad-50ae-4464-a6c6-a3a433f21ec2 | section | First Test
cd42b11b-d808-453c-9655-5995fe57f385 | checkpoint | Mains power healthy (green light)
c6cb6b60-b3b2-44e2-9fd3-19de317af4ac | checkpoint | Controls UPS healthy (green light)
0a313464-9ca3-453d-af0f-c3a97829ac69 | checkpoint | Controller power healthy (green light)
bf6f8b0e-8870-408f-bf5e-4985455f4ea4 | checkpoint | Leak monitoring healthy (green light)
b76195c1-0ea6-411b-bc05-8dd62e8b3d50 | checkpoint | SP-1 pump ready (green light)
8b4db295-7ee4-423b-885d-195aeef75377 | checkpoint | SP-2 pump ready (green light)
82591cab-aa22-4dc1-8667-ec489cd76be1 | checkpoint | SP-3 pump ready (green light)
697a4c32-0563-45c5-baab-ff361af98e4a | section | Second Test
108e7e42-2050-4cab-b282-c22312277586 | checkpoint | Mains power healthy (green light)
28998650-206d-41a5-afc7-1d0d32f698f9 | checkpoint | Controls UPS healthy (green light)
a9e64133-e355-4b33-856f-9e482486e6b2 | checkpoint | Controller power healthy (green light)
7251157d-0194-4cd3-9db5-63bc6895bbf6 | checkpoint | Leak monitoring healthy (green light)
fe2f6e22-c741-4a9e-8e4d-a82ebf05115f | checkpoint | SP-1 pump ready (green light)
c02c75f8-a317-44a5-b2ab-de64b9c17107 | checkpoint | SP-2 pump ready (green light)
b11d6838-137c-4d40-ad8c-f0e5b97dd6c3 | checkpoint | SP-3 pump ready (green light)
72d8997d-8408-4227-aab7-3f586854ab82 | checklist | DS02 - Duty diesel pump failure |  | DS02 - Duty diesel pump failure
a1e12648-0dae-42e1-992c-ed7f2be32b97 | section | IST Test
e89f8882-382b-41ab-a667-86ec52b91a3d | checkpoint | IST Details
c5c5dcfc-8a71-5525-807b-2733f03b35fe | textbox | Test Method - Simulate diesel pump Failure- How can we simulate this?
e0dbc198-eb48-53aa-ba93-e1e1e4bfaeea | textbox | Area - A40
bf27d879-7919-4bc0-a8b7-5e942eade820 | section | First Test
44cfd987-8dc4-46e2-ab0b-a402b41f919b | checkpoint | BMS - BMS Alarm
5d5fad28-4945-41fa-9c4c-6df2173dc3a2 | checkpoint | BMS - Generator run signal from BMS
35d561ba-b837-4e0a-9031-5b18c842044d | checkpoint | SP-1 pump fault (red light)ON
f0775ba8-cb74-4a6a-9303-2814511abf02 | checkpoint | SP-1 pump ready (green light) OFF
04f7577b-236d-4026-a4dc-0a5f286c7e74 | checkpoint | SP-2 pump run (green light)ON
777d95b6-0bff-4d64-98ff-3071a8356fca | checkpoint | SP-2 pump ready (green light) OFF
00f0b3eb-74b3-490a-a3dd-010e96fa2604 | section | Second Test
8e1e4c4b-b688-4589-b3d0-ea38bb7cd1f9 | checkpoint | BMS - BMS Alarm
6495979c-0918-4e09-aa2b-aab91d94530e | checkpoint | BMS - Generator run signal from BMS
a5594cc2-2dbf-4715-a41a-0fd680cbc54e | checkpoint | SP-1 pump fault (red light)ON
8ff1b906-615c-49f7-81a5-2de64c813217 | checkpoint | SP-1 pump ready (green light) OFF
1a238bf4-adbc-4a13-8101-fb46e69a343a | checkpoint | SP-2 pump run (green light)ON
8f15b8a9-b1b0-4142-8b1e-7680db1dd11f | checkpoint | SP-2 pump ready (green light) OFF
b0b756af-7050-46f1-82de-805876267bbb | checklist | DS03 - Standby diesel pump failure |  | DS03 - Standby diesel pump failure
fc4ba3dd-307b-44ac-9020-fa6b2c447acb | section | IST Test
9fe6d077-18eb-4ba5-b05c-fa328ce2eb17 | checkpoint | IST Details
5975fb20-50fe-573c-82f3-a8a56eb9a91c | textbox | Test Method - Simulate diesel pump FailureHow can we simulate this?
b246d348-cfe2-5216-b6d4-dc3666b1f3e1 | textbox | Area - A40
de38c0e9-b837-4efe-81ef-c13c8e2f103c | section | First Test
64227d93-e51a-446f-86ba-ed69533f1067 | checkpoint | BMS - BMS Alarm
170b6da4-eced-4079-9fa7-87d59f5cf3bf | checkpoint | BMS - Generator run signal from BMS
c07c7a30-107d-4b8b-9594-cbd6b702631a | checkpoint | SP-1 pump fault (red light) ON
ff61dcfc-d269-4364-8bba-1b199eff2e21 | checkpoint | SP-1 pump ready (green light) OFF
75d0f258-a673-4512-8947-008868110cf8 | checkpoint | SP-2 pump ready (green light) OFF
188f6140-3872-4334-91db-45d2fe26bd9b | checkpoint | SP-2 pump fault (red light)ON
6fd73ffb-6a3a-4137-aa73-421166e61d8c | section | Second Test
a1dc6266-453a-4a70-9d1e-4345720f9dfe | checkpoint | BMS - BMS Alarm
74b6fac8-76b1-4030-b43f-d1ada280c894 | checkpoint | BMS - Generator run signal from BMS
19c9de48-9119-48d7-aad2-4f15876659a0 | checkpoint | SP-1 pump fault (red light) ON
9eaf6359-69f2-43b6-b3da-69917af44013 | checkpoint | SP-1 pump ready (green light) OFF
d291fbb7-b725-4929-9f2f-38eeff29fb70 | checkpoint | SP-2 pump ready (green light) OFF
9d89d326-5b4b-4476-98d2-5201b6dc73cc | checkpoint | SP-2 pump fault (red light)ON
d51b04b4-c5d5-49d3-b74b-129883739fd8 | checklist | DS04 - Diesel supply pipe leak test fail from duty pump SP-1 (loss of line pressure). Duty pump locked out, standby pump SP-2 enabled. SP-1 pipe line isolated. All three U/G tanks siphoned together |  | DS04 - Diesel supply pipe leak test fail from duty pump SP-1 (loss of line pressure). Duty pump locked out, standby pump SP-2 enabled. SP-1 pipe line isolated. All three U/G tanks siphoned together
d4f168bd-0013-4579-b1c1-1e1ebbd116b7 | section | IST Test
4c134647-c942-4c3f-a8f7-707a1c104715 | checkpoint | IST Details
41fab036-52a6-5c19-ba97-448d23fef41f | textbox | Test Method - Simulate loss of line pressure, How can we simulate this?
ed572152-d386-5458-b51d-74e362768296 | textbox | Area - A40
a10781f2-14b2-4a6c-874b-36c225075798 | section | First Test
ffdeae42-cf24-4106-a8cb-edc0e727823f | checkpoint | BMS - BMS Alarm
682d98ec-a34f-4b9d-8cff-760ca844b0f2 | checkpoint | Leak detector panel alarm
b917968d-2ba8-401c-88d1-3fa1a42f2b1c | checkpoint | Leak monitoring healthy (green light) OFF
ee0775e1-7f5e-4d02-8dee-fe8de5c8506d | checkpoint | Leak monitoring fault (red light) ON
cfc06f34-c6b8-44ed-b1f0-a05e18a42b66 | checkpoint | SP-1 pump fault (red light) ON
a5443a2a-0733-4776-8328-d00aa5cc1abe | checkpoint | SP-1 pump ready (green light) OFF
794654c1-bdcf-4c16-8a0a-622563565f7d | checkpoint | SP-2 pump ready (green light) OFF
e737a811-c4a3-4772-8af9-67d008024f77 | checkpoint | SP-2 pump fault (red light)ON
61ff48e7-bc65-4d77-8303-607ab02fd07a | checkpoint | BMS - Duty diesel pump electronic line leak detector alarm
ffd57c06-44cb-4dfe-b210-0c852b88cfbb | checkpoint | Pump SP1 supply pipe iso valve IV-M3 NO - Closed
76604005-a4e5-464c-80ec-f859a8a512b8 | section | Second Test
91afcacd-e8b2-41d9-b62e-d1d12c6a6c75 | checkpoint | BMS - BMS Alarm
5a4f0e52-25b0-4c76-bd5f-289ab889ea32 | checkpoint | Leak detector panel alarm
103c2ea6-f7ee-4236-a754-17383f759488 | checkpoint | Leak monitoring healthy (green light) OFF
006d6129-23cf-407f-a5b1-96a0042d23be | checkpoint | Leak monitoring fault (red light) ON
38c1ade2-41d9-4b10-b6a5-36cca303a2b4 | checkpoint | SP-1 pump fault (red light) ON
6d0f11d7-a077-4d2d-a368-fee514027b60 | checkpoint | SP-1 pump ready (green light) OFF
b16d3341-8420-4172-8585-b655d4887dbf | checkpoint | SP-2 pump ready (green light) OFF
34f51386-ab25-4184-ab6c-730fa3091f04 | checkpoint | SP-2 pump fault (red light)ON
b47600c1-fff1-404b-9569-a1930287c4ff | checkpoint | BMS - Duty diesel pump electronic line leak detector alarm
3fe100ab-df0a-4126-a57d-7359efe1e0a6 | checkpoint | Pump SP1 supply pipe iso valve IV-M3 NO - Closed
650ededd-7867-47be-9291-4f7de82d4c81 | checklist | DS05 - Diesel or water leak detected via a discriminating leak detector |  | DS05 - Diesel or water leak detected via a discriminating leak detector
39e67414-f9c3-4038-9ccf-35438c1a4961 | section | IST Test
a87b7ed0-8718-4ae8-a685-7d22c02a6148 | checkpoint | IST Details
aecffb68-9e6c-5d69-a315-cbc66fac0075 | textbox | Test Method - Trigger leak sensor
9ca897b1-6a67-58da-8cd0-5a42b2325697 | textbox | Area - A40
9e8252af-ecba-40db-8e2c-83cc6e17560a | section | First Test
81141db2-036c-4ef2-bfc3-8743130279fb | checkpoint | BMS - BMS Alarm
9c6cec02-e49f-43fb-9f9e-b6a32cd35ec0 | checkpoint | Leak detector panel alarm
162d3480-0947-4295-a9d3-9d5cb2cf1fb4 | checkpoint | Leak monitoring healthy (green light) OFF
a0cd5f89-8418-46af-a2f7-e4144bde3cf2 | checkpoint | Leak monitoring fault (red light) ON
1582829c-87f7-4abb-b18d-012f7d21d8d5 | section | Second Test
ba8b6d12-463e-499c-b03e-78852b0af1c1 | checkpoint | BMS - BMS Alarm
bf380173-4a84-47a0-bab5-42899c962a9c | checkpoint | Leak detector panel alarm
e1dfc789-be24-4cdb-aa3d-27ffa4d46e83 | checkpoint | Leak monitoring healthy (green light) OFF
c403de7a-963f-459b-82e1-f14311ea5399 | checkpoint | Leak monitoring fault (red light) ON
c6284834-b4ad-47fe-a661-d99bacdceee1 | checklist | DS06 - Leak in underground diesel storage tanks |  | DS06 - Leak in underground diesel storage tanks
e8c55f18-6180-49c3-9b27-ec1c4ce5e466 | section | IST Test
8f7c9b2f-68b8-4701-b3b6-24eb80fc08e4 | checkpoint | IST Details
fbd70c4c-e52f-5d3c-8efb-b909a5d98ed1 | textbox | Test Method - Trigger leak sensor
3ca6fecc-f5b8-5210-af63-96cd355d9a5f | textbox | Area - A40
790c2d53-9b57-4d89-a4dd-728a4987b3ec | section | First Test
792416f3-9eb1-4fda-bac6-859f777c92f8 | checkpoint | Fire - Fire Alarm
5b5d0793-d435-46df-b500-1ad7bcfecc97 | checkpoint | U/G tank Hydro Guard leak sensor
bb918ac1-2dc3-41b6-b4e5-3276df9ece7a | section | Second Test
3dfb1578-fa83-479f-a465-0950b34234af | checkpoint | Fire - Fire Alarm
607dc4ce-1850-437d-8125-5f71c7d7f5a3 | checkpoint | U/G tank Hydro Guard leak sensor
a33029da-e681-44c5-a594-c540e519cf3e | checklist | DS07 - Diesel theft from any tank |  | DS07 - Diesel theft from any tank
1aa1df91-b31e-42e7-975b-660f679ecc35 | section | IST Test
63d116a7-d233-494f-aee1-58bfb29593cb | checkpoint | IST Details
2df02ac6-3cc7-5d69-b6fc-c59faeee7931 | textbox | Test Method - How can this be simulated?
f109fe4a-e881-5f76-b52e-77887705c3d7 | textbox | Area - A40
99406196-b6d5-4e60-8524-ca168df5291c | section | First Test
fd12fa5d-bf85-4e01-9117-f23b88b510c7 | checkpoint | BMS - BMS Alarm
7bf7ea19-c7ec-4d3a-9210-9dc1e899de8c | checkpoint | Leak detector panel alarm
d1f23be4-f48e-455d-aaad-3af1a8156236 | section | Second Test
198038ca-af35-4e60-9007-e15bea35ad37 | checkpoint | BMS - BMS Alarm
dbaa66cb-2b1a-4145-aee6-c0a6c1be7e2f | checkpoint | Leak detector panel alarm
e1269c8c-0601-4e9c-81f8-86739dd19f66 | checklist | DS08 - Either underground tank is over filled with diesel |  | DS08 - Either underground tank is over filled with diesel
8cf9861d-8763-460f-b39e-90664c229c13 | section | IST Test
6df3c466-b519-4ee0-bb50-bf1027dee32a | checkpoint | IST Details
e76a2764-b5ef-5a25-ac1b-ff4aaf36e7a5 | textbox | Test Method - Manipulate Level sensor?
41221c30-6d85-5186-91f3-c50850173a0c | textbox | Area - A40
618779a8-b21e-4c28-bf31-e1c3a79ed714 | section | First Test
abf80817-ec61-4071-893e-c3afe622b9f8 | section | Second Test
ee87eca0-ea30-4f18-a00e-6efe0f5c7173 | checklist | DS09 - Generator day tank diesel fuel level reaches 80% and calls for diesel filling, duty pump (SP-1) enabled |  | DS09 - Generator day tank diesel fuel level reaches 80% and calls for diesel filling, duty pump (SP-1) enabled
e397be71-2c00-4a77-b7d0-c01ffca39fa6 | section | IST Test
361cadd3-4ad3-47fe-9a66-130c6b887096 | checkpoint | IST Details
4a34cc63-929c-5abc-81b4-cbd1c26acb6f | textbox | Test Method - How can this be simulated? Manipulate Level sensor?
44903038-40e1-59d1-aaa3-7c2b8ec86b5a | textbox | Area - A40
85f8d80f-7557-4a44-a891-652e5136829d | section | First Test
11dc8a44-1c57-4ffc-99fa-81fa26cc1603 | section | Second Test
8446a30b-fe36-4ab6-a038-8f4081d85c65 | checklist | DS10 - Generator day tank diesel fuel level reached 95% full |  | DS10 - Generator day tank diesel fuel level reached 95% full
d258bc1c-be01-4ffb-9226-d5bfa8d583a3 | section | IST Test
aaa14e86-190f-4f23-a0a5-ec321c20d1e4 | checkpoint | IST Details
2e97ef17-08c5-55bb-8751-1fe33dcf15a1 | textbox | Test Method - How can this be simulated? Manipulate Level sensor?
bb047582-09a6-5937-a006-b615f4012491 | textbox | Area - A40
a425bbee-4bcf-4d31-b179-d7d06e33963d | section | First Test
e3d377e5-9dd5-49dc-9cb9-fe3ea49a1102 | section | Second Test
ba502b9b-116f-420e-8a73-1a2156f28522 | checklist | DS11 - Generator day tank diesel fuel level reaches 60% duty pump (SP1) still enabled from 80% day tabnk level fuel fill enable |  | DS11 - Generator day tank diesel fuel level reaches 60% duty pump (SP1) still enabled from 80% day tabnk level fuel fill enable
29d28f10-f8cf-41e1-bad3-a824d6ef416e | section | IST Test
28928b88-4926-469d-bbeb-3d9d24cd33fd | checkpoint | IST Details
ce3fcf48-5e4c-5d46-b41f-a4edb0a5c8cd | textbox | Test Method - How can this be simulated? Manipulate Level sensor?
8f7aa0c6-fefd-5250-80e5-c4fec684ac05 | textbox | Area - A40
89aefb6b-95f0-4b0d-a58a-8776c249794d | section | First Test
0189c0dc-0734-41e7-9ed9-b30df6c822e8 | section | Second Test
419613b3-0b68-47c2-a0ef-5029839f8155 | checklist | DS12 - Generator day tank diesel fuel level reaches 40% duty pump (SP1) enabled |  | DS12 - Generator day tank diesel fuel level reaches 40% duty pump (SP1) enabled
a8fca7b5-604c-4583-bef1-86bb1f7c280a | section | IST Test
7bdc109d-4f99-4658-9730-a577358e4b6d | checkpoint | IST Details
570986eb-164b-51c3-82ff-4308400a3bff | textbox | Test Method - How can this be simulated? Manipulate Level sensor?
abbdef40-541d-5c7d-b23a-e10d5d646a60 | textbox | Area - A40
6fc64474-9544-4424-9f0e-1b3bd70c23e7 | section | First Test
0fdc7256-9228-4287-97e8-69b8f3501d61 | section | Second Test
3f141f71-6126-4292-a5a5-99aaa6cf21d4 | checklist | DS13 - Any day tank is over filled with diesel |  | DS13 - Any day tank is over filled with diesel
9639dfc4-afd6-438a-9a44-47aedbff5c94 | section | IST Test
b431f440-6b42-4133-a231-3962f8214da7 | checkpoint | IST Details
e6755f2b-5151-59c5-90e4-483074e3f364 | textbox | Test Method - How can this be simulated? Manipulate Level sensor?
3ac52c20-c986-5040-8c4e-2369a0f373ba | textbox | Area - A40
3346c332-a41b-4886-9446-c9727ddc02f7 | section | First Test
9f379ef8-cf85-40c2-9ced-b92126ff6a10 | section | Second Test
e8ed574f-6f89-43cb-96a8-74382f674293 | checklist | DS14 - Generator day tank diesel fuel level continues to drop despite diesel fill request activated |  | DS14 - Generator day tank diesel fuel level continues to drop despite diesel fill request activated
c31fe3c4-602e-4fa5-ae3d-2d9a71f5e883 | section | IST Test
7c5e2038-af85-4418-a1da-8c8572475583 | checkpoint | IST Details
a9cab0e6-f9ae-554c-8b9f-9deb9be740fd | textbox | Test Method - How can this be simulated?
9c622ceb-69a2-586f-b86e-3fb26c3176a9 | textbox | Area - A40
08211340-db68-42f4-997f-b7abf81eee49 | section | First Test
b1acd86c-9e18-48ff-a588-2ef0bcdffda0 | section | Second Test
b77fbb2c-82df-41eb-bb74-1b9359c28852 | checklist | DS15 - Any emergency stop button activated |  | DS15 - Any emergency stop button activated
a9e764dc-de89-4870-a8f1-46de26eeb05e | section | IST Test
5b8dfcfe-3087-437d-8de3-2f47c98dc73d | checkpoint | IST Details
cbac3304-a8f4-5bbc-a057-64e1de8e56a8 | textbox | Test Method - Press Emergency stop button
6b4b6c76-55ca-5479-90ac-1db8596fd352 | textbox | Area - A40
82c0617e-2064-427a-bb4d-b1c0601006dd | section | First Test
a5bdc006-c83b-4a16-a645-48d76358ddfe | section | Second Test
6f6d0730-ff5b-4f34-b6be-ad82220f9cc2 | checklist | DS16 - Generator running, fire occurs at generator engine and fuseable link releases, no request for day tank filling |  | DS16 - Generator running, fire occurs at generator engine and fuseable link releases, no request for day tank filling
a48eec76-c0e8-4d25-9eca-ce971d589ade | section | IST Test
50ed5d41-9305-4c81-a91a-4fdb8a1ca352 | checkpoint | IST Details
5ea2df93-92f5-54ae-a817-2f61a13d65ba | textbox | Test Method - How can this be simulated?
19fc3daf-4138-58dd-bda5-8444a1171702 | textbox | Area - A40
d64f14e6-1629-4be3-8813-dacfca3fed69 | section | First Test
7aa61e6b-8972-476d-a5c8-784864321d07 | section | Second Test
732ad6eb-5a89-4dfb-962f-3a88f44b8fe1 | checklist | DS17 - Mains power fail when system is idle |  | DS17 - Mains power fail when system is idle
1b2cc536-0a7d-4c57-b2d7-fa2bcd5bc659 | section | IST Test
50904672-f09a-42d2-a599-64a70bb48440 | checkpoint | IST Details
81cd40bf-8b7a-5037-bd45-4b514f52d53b | textbox | Test Method - Isolate mains supply
b106093b-9942-5b7a-bcd1-8ed32f7eb804 | textbox | Area - A40
253dc7fd-3003-4c78-95af-d09bf9c6f73c | section | First Test
639244d9-2022-4a8e-87e0-738e7e0566f0 | section | Second Test
f76d4c6e-bd08-4a34-aee8-ce01e4bf5af5 | checklist | DS18 - Controls UPS power fail, mains healthy, system idle |  | DS18 - Controls UPS power fail, mains healthy, system idle
7f4b4d1e-c879-4c91-9852-ce60cbc0879e | section | IST Test
87cd3064-a315-4dbe-97d3-5acf57aadbc9 | checkpoint | IST Details
afbcba93-b04f-51c2-b0f1-4f2aa1796606 | textbox | Test Method - Isolate UPS supply
19e0e737-f9be-5951-b16c-b0a2daa7f865 | textbox | Area - A40
c4d46089-059b-439e-a01b-0d3c04e1c3f0 | section | First Test
b8ffbe05-ed09-4d76-a8c3-5c713bae4a77 | section | Second Test
e81ff759-43ee-4b31-ad95-8944fd6e928b | checklist | DS19 - Diesel controller fail, generators running diesel will be called for fuel shortly, duty pump (SP-1) switched to manual at MOA selector switch at MCC |  | DS19 - Diesel controller fail, generators running diesel will be called for fuel shortly, duty pump (SP-1) switched to manual at MOA selector switch at MCC
3d98cf7d-bdb9-4d8e-b27b-330043014f8e | section | IST Test
2cda414d-47ac-4a77-bdb6-4260e640f594 | checkpoint | IST Details
b11feba0-80a7-55de-a4f6-df98bb5a8095 | textbox | Test Method - How can this be simulated?
cf146e66-afdc-5217-bada-f0f4f457568c | textbox | Area - A40
4a22f641-d7de-4394-a803-67af6109e795 | section | First Test
4cd79c2e-8941-47e6-b1fc-eb258341cf7f | section | Second Test
bf705dd2-6b64-43ea-b39a-d318aa693025 | checklist | DS20 - Fire in Tunnel, generators not running |  | DS20 - Fire in Tunnel, generators not running
830273ee-7823-48a1-9d81-e25010dbb2e7 | section | IST Test
53e94c67-ef8d-439d-a6bb-15c204b246f9 | checkpoint | IST Details
b1079956-672b-5794-b243-04a6d354fefa | textbox | Test Method - Trigger MCP in tunnel
576f5fc0-6855-54b0-bf07-acda0a4fda0e | textbox | Area - A40
f1b9b1e0-a47f-4871-a791-e908e14300d9 | section | First Test
ae0a56fc-8f15-470c-8862-46bd6c8505fc | section | Second Test
ab56a092-b567-4c60-bffe-92c6bb96bf1b | checklist | DS21 - Fuel polishing enabled with generator not running (Tank 2 example) |  | DS21 - Fuel polishing enabled with generator not running (Tank 2 example)
0d4406da-85f2-45ee-b98f-3e8d8723e9fb | section | IST Test
c3665676-1266-4825-9ef6-04a5f0e4d136 | checkpoint | IST Details
2d99a1e0-dbae-57fc-acfe-2cd4f138b204 | textbox | Test Method - How can this be simulated?
12504dc7-e00d-561a-8da2-ca3ca6e276df | textbox | Area - A40
2a0a885c-7637-4082-9ccb-7245579880eb | section | First Test
8b69c425-3c80-4a77-96b2-abc9e1af8859 | section | Second Test
389e98ae-05cd-4cac-8b6f-2cf385587207 | checklist | DS22 - Fill command from future A06 diesel systems for day tank filling (SP-2 duty) |  | DS22 - Fill command from future A06 diesel systems for day tank filling (SP-2 duty)
f60155ab-7175-4ded-b31b-440d341f4d4b | section | IST Test
13f0cc9a-56a2-46e7-b003-b14e3ce65ceb | checkpoint | IST Details
1fb2ff45-abfb-55ef-bdad-4c642545163b | textbox | Test Method - How can this be simulated?
253e8d29-fbc9-5d74-8350-921192173af5 | textbox | Area - A40
959ae6b5-cb18-4d92-b430-fbf653e40c5a | section | First Test
b2bda79c-02c5-4b72-a6b5-041d642509a7 | checkpoint | SP-2 pump run (green light) On
cac5c344-976f-416b-962d-019058547466 | checkpoint | SP-2 pump ready (green light) Off
5e74a303-7079-4012-b8f6-714202c91072 | checkpoint | Tunnel motorised isolating valve (MV4) NC
11947912-27da-489a-a934-038c1265096f | checkpoint | Tunnel fire cell motorised isolating valves (MV- 5 though 10) NO
2f010321-3bb8-4fcc-8ac3-90fbbb9d5eaa | section | Second Test
c8d84c07-980d-4e96-b4c9-e33918020a8e | checkpoint | SP-2 pump run (green light) On
9d71a545-74ba-45b9-9d96-8605ad00ad1c | checkpoint | SP-2 pump ready (green light) Off
3742b9e6-c88b-4e19-adba-e24c1ea6cb0d | checkpoint | Tunnel motorised isolating valve (MV4) NC
7c16f6fa-3656-4734-b969-ac335c15cbcd | checkpoint | Tunnel fire cell motorised isolating valves (MV- 5 though 10) NO
77e42fa6-672b-4dc1-9bc5-6fa5bfca8b29 | checklist | DS23 - Diesel controller fail, P1 pump switched to manual, day tank fill valve by-passed and day tanks are flooded and diesel overflows and drains back to tanks 1 and 2. Generator running. All three U/G tank siponed together |  | DS23 - Diesel controller fail, P1 pump switched to manual, day tank fill valve by-passed and day tanks are flooded and diesel overflows and drains back to tanks 1 and 2. Generator running. All three U/G tank siponed together
41022b78-4c7a-479a-a40b-6f517201c14c | section | IST Test
5d074cea-f563-4af9-b070-6635c684dcbf | checkpoint | IST Details
f46186e5-9904-5ed8-ae62-c732377541a9 | textbox | Test Method - How can this be simulated?
94926612-9be4-5f52-befd-1453575d6e05 | textbox | Area - A40
9ab5728e-b9e8-4da3-a6f0-33996f7cdaa1 | section | First Test
daa615b4-0461-478a-8530-c561d1d0d276 | checkpoint | BMS - BMS Alarm
f394bfef-f9b1-4249-965b-9ff789068f84 | checkpoint | Day tank High high tank level switch
96f9a37b-f477-483f-9fb3-e4037810a4c9 | checkpoint | Day tank motorised overfill protector valve (MV11, 12, 13 or 14) NC - Manual Open
0371e1c1-3e06-4e25-b602-c765af11b16c | section | Second Test
efd6bf57-87bc-428c-a52a-5f57a2673c3a | checkpoint | BMS - BMS Alarm
7dba0444-19b8-4719-b080-ab18d38631ff | checkpoint | Day tank High high tank level switch
9bd10e2e-0ae9-4fa9-bca7-d629192f3033 | checkpoint | Day tank motorised overfill protector valve (MV11, 12, 13 or 14) NC - Manual Open
ea3d427d-364b-46d6-b079-0c523ed967c4 | checklist | DS24 - Automatic tank gauge fail, P1 pump switched to manual, day tank fill valve by-passed and day tanks are flooded and diesel overflows and drains back to tanks 1 and 2. Generator running. All three U/G tank siponed together |  | DS24 - Automatic tank gauge fail, P1 pump switched to manual, day tank fill valve by-passed and day tanks are flooded and diesel overflows and drains back to tanks 1 and 2. Generator running. All three U/G tank siponed together
cf03d68c-cbb4-4e5e-885c-c70904e37c60 | section | IST Test
60d34231-8dc2-46d7-94fc-41dfee48c9c1 | checkpoint | IST Details
057281be-5c5d-55f1-9081-b09ab9ec7306 | textbox | Test Method - How can this be simulated?
d87f86a6-44db-5e99-9ae6-8bf786f08f4e | textbox | Area - A40
5c94d047-2ce8-432c-a3bd-7bc4ffad977f | section | First Test
ac7daf5c-c034-4c46-98e6-ade1d89636dd | checkpoint | BMS - BMS Alarm
310f0be2-e002-465f-b86d-ac543ede5d6e | checkpoint | Leak monitoring fault (red light) On
738781a8-1c8e-45b7-ba0e-f5e9ed94cc81 | checkpoint | Day tank High high tank level switch
0cd02361-296c-40c2-b9dc-85e4b10fdaed | checkpoint | Day tank motorised overfill protector valve (MV11, 12, 13 or 14) NC - Manual Open
e767197c-823a-4d93-99e9-d48a146e55a1 | checkpoint | Normal Condition
2f240b95-e262-4e94-a787-7cafdd7037cb | checkpoint | BMS - BMS Alarm
81fd30cc-e1c1-49d8-b874-72727ac7cf12 | checkpoint | U/G Tank 3 siphon isolating valve IV-M7
f182ba50-df7a-4198-a7a1-31111c3a6433 | section | Second Test
2bc25f96-aa8d-4764-bfaa-16d99c61c656 | checkpoint | BMS - BMS Alarm
1bbf2d84-efe6-49dc-b3e1-5d8ad508a074 | checkpoint | Leak monitoring fault (red light) On
4687085b-dfac-4941-a83b-e6f3e03b01a1 | checkpoint | Day tank High high tank level switch
1af2a2cd-9b78-4b63-9ad0-03d3c8cc27fd | checkpoint | Day tank motorised overfill protector valve (MV11, 12, 13 or 14) NC - Manual Open
371451bb-53d1-4635-88dc-2acb0ce1b3ef | checkpoint | Normal Condition
e28ca73a-8c5d-4ced-8d70-836c580ab58b | checkpoint | BMS - BMS Alarm
d29ac6b6-1608-4a5b-bd91-a6152dd5ba71 | checkpoint | U/G Tank 3 siphon isolating valve IV-M7
2d51f8bd-a254-4435-b25f-8627284cf54f | checklist | DS25 - U/G tanks 1, 2 and 3 siphoned together, system idle |  | DS25 - U/G tanks 1, 2 and 3 siphoned together, system idle
363d53f9-1be8-4569-9f06-d07018ced491 | section | IST Test
57bc0391-ee22-4a81-907b-bf6eeb6ac458 | checkpoint | IST Details
52812449-6d18-5f6a-86b3-aa342ac1024c | textbox | Test Method - Normal Condition
393de0d5-fecf-58a0-a6ba-a12e2f20253b | textbox | Area - A40 - Bulk UG Tank Isolation
5b24d6d8-8dec-4f30-a012-ba779bdee0b1 | section | First Test
ebb861ef-b186-46a8-9fd5-e5f9a523fb39 | checkpoint | Normal Condition
1f4aea1a-a156-49b6-a6d9-db779d7ebc35 | section | Second Test
0a5a7813-bcac-47b6-b0c4-0084a302cebd | checkpoint | Normal Condition
27d63feb-84bf-4a52-93a7-1ae226fef45d | checklist | DS26 - U/G tanks 1 and 2 siphoned together, tank 3 isolated from diesel fuel system. System idle |  | DS26 - U/G tanks 1 and 2 siphoned together, tank 3 isolated from diesel fuel system. System idle
def323ad-3f50-443e-807d-211bb6344ccb | section | IST Test
d9429bac-14cf-4027-b71b-7605a110af9a | checkpoint | IST Details
c29e1a4a-921b-58c3-9fbe-8549d0ef4396 | textbox | Test Method - Isolate Tank 3
eae3f9cd-13f7-5ce4-b4f0-0ea5ddf10074 | textbox | Area - A40 - Bulk UG Tank Isolation
f0b7508a-ba04-4110-8229-93aa748a2977 | section | First Test
41b02bf3-c747-49e5-97a7-fbb203e34f47 | checkpoint | BMS - BMS Alarm
6b14c0d5-e1d9-468e-8679-c9dcac9db934 | checkpoint | U/G Tank 3 siphon isolating valve IV-M7
bba39462-83d7-4370-a0ec-8eb2a6b3a512 | section | Second Test
92f7eb7a-c0ae-4e89-869b-7ffd75842fee | checkpoint | BMS - BMS Alarm
87783e64-8721-4fef-ae62-3ce8bf3f1ed5 | checkpoint | U/G Tank 3 siphon isolating valve IV-M7
5f533e4b-cac6-4e63-b290-e370abdb48f3 | checklist | DS27 - U/G tanks 2 and 3 siphoned together, system idle, tank 1 and SP1 isolated from diesel fuel system |  | DS27 - U/G tanks 2 and 3 siphoned together, system idle, tank 1 and SP1 isolated from diesel fuel system
4863f816-270f-4d58-93c0-5a0c82bf7db8 | section | IST Test
82e06255-75b1-4207-998c-3cdbc2aa47a9 | checkpoint | IST Details
6b55462b-e385-5c02-af73-a3ab594d0bf3 | textbox | Test Method - Isolate Tank 1 and SP1 from system
e5b81a77-7be7-5c05-9dee-949b3da408cf | textbox | Area - A40 - Bulk UG Tank Isolation
1c78cba1-4b37-4c8a-8ac7-4ed96933b9f0 | section | First Test
07738f36-0a65-40ed-b7af-873b0adeebd8 | checkpoint | BMS - BMS Alarm
d008c1b8-f299-4014-b57c-ffe2fb17fd86 | checkpoint | SP-1 pump fault (red light) On
9f7f1ff3-4fb4-4d3f-9953-60d806b2f979 | checkpoint | SP-1 pump ready (green light) Off
60aaa374-75e4-46f5-9247-041b3348e352 | checkpoint | Day tank overflow drain to U/G tank 1 iso valve IV-M1 NO - Closed
a23981c2-73d0-4d06-bf98-8e8e65f24f39 | checkpoint | Pump SP2 supply pipe iso valve IV-M4 NO - Closed
c2b7343b-f17c-4087-a502-6fa0b15648b3 | checkpoint | U/G Tank 1 siphon isolating valve IV-M5 - Closed
6ffbf999-2dd2-43a6-ac93-c3e41f873135 | section | Second Test
bb83eff9-7281-4cc7-bd01-ad132a91e0e7 | checkpoint | BMS - BMS Alarm
a0a57ce2-5b14-40fc-8756-9f9ada03c6f0 | checkpoint | SP-1 pump fault (red light) On
2ade1fa0-688d-48c2-b2d5-918f97926a96 | checkpoint | SP-1 pump ready (green light) Off
cfe8919f-6f27-4166-b7c0-fb96a7a5da52 | checkpoint | Day tank overflow drain to U/G tank 1 iso valve IV-M1 NO - Closed
5f1129aa-00f2-4b70-bff7-108344484f54 | checkpoint | Pump SP2 supply pipe iso valve IV-M4 NO - Closed
62c851da-9494-4f80-9774-0ff08596d48e | checkpoint | U/G Tank 1 siphon isolating valve IV-M5 - Closed
e1ac37aa-df9e-48b6-964f-9766fd0a972c | checklist | DS28 - U/G tanks 1 and 3 siphoned together, system idle, tank 2 and SP2 isolated from diesel fuel system |  | DS28 - U/G tanks 1 and 3 siphoned together, system idle, tank 2 and SP2 isolated from diesel fuel system
e05cf0ec-25ef-4eae-9efc-323d3a99bd2b | section | IST Test
8bd4207c-c518-4045-be2c-4de2022d3230 | checkpoint | IST Details
c6a55d80-611f-587d-9540-d09b8b6b79cb | textbox | Test Method - Isolate tank 2 and SP2
279f7110-86da-570e-8c8f-c0bb7a6e2d41 | textbox | Area - A40 - Bulk UG Tank Isolation
bb3dd4ad-6a88-4ed3-a8ed-07f8ff67e110 | section | First Test
87f4ae91-afb8-45d7-94e5-8c2312f5e286 | checkpoint | BMS - BMS Alarm
c85adbb8-127b-4c0e-8a30-88986771e7ff | checkpoint | SP-2 pump fault (red light) On
88a34906-d1f3-4d1a-a5b2-706c58460bf1 | checkpoint | SP-2 pump ready (green light) Off
4f6a0e55-1601-47f2-bc28-f88712e153b6 | checkpoint | Day tank overflow drain to U/G tank 2 iso valve IV-M2 NO - Closed
dbb95b49-1e3e-4d99-b2f6-803eb73fee25 | checkpoint | Pump SP1 supply pipe iso valve IV-M3 NO - Closed
f3e2074c-0069-40e1-b3fd-685abae8c340 | checkpoint | BMS - BMS Alarm
b1815c9b-1201-40f9-8ea9-cfa0dff9e3a9 | checkpoint | Manual Isolation valves position TBC
69c7284c-a988-46eb-8885-92486849a6f3 | section | Second Test
31114c48-fba8-422e-8585-46364b15667b | checkpoint | BMS - BMS Alarm
69ab650a-6911-4405-acd7-fc3936f0b1c7 | checkpoint | SP-2 pump fault (red light) On
6af83c1b-0f0b-41bc-a1d1-ca2bc60eeda2 | checkpoint | SP-2 pump ready (green light) Off
ab530f4a-fc50-45db-b7ef-c4b2922193dd | checkpoint | Day tank overflow drain to U/G tank 2 iso valve IV-M2 NO - Closed
3db1d8b5-c2b2-46e6-8df4-770d04b73247 | checkpoint | Pump SP1 supply pipe iso valve IV-M3 NO - Closed
92ce11a8-9e74-4647-8636-47e89ed72c3b | checkpoint | BMS - BMS Alarm
e5ebb282-48e1-4c1e-a6ae-bcf1dcdd5478 | checkpoint | Manual Isolation valves position TBC
b6d92eaa-3f61-49f7-b29e-271a4f18176a | checklist | DS29 - Monitored isolating valveValve position mis-match |  | DS29 - Monitored isolating valveValve position mis-match
709f290d-4e1d-447a-8c15-d54fc3b98a9f | section | IST Test
89544b07-990e-448a-905a-73cf6b0c8590 | checkpoint | IST Details
e17c0f5f-ac4a-5aa1-967c-df812e1f678e | textbox | Test Method - How can this be simulated?
e6b31657-b116-5cad-b3c6-0e4984fb7a41 | textbox | Area - A40 - Bulk UG Tank Isolation
0d3567a1-f577-4f1d-b478-3afa3611c5d2 | section | First Test
2ede6780-c37c-4f45-9f62-f2e94b5f7252 | checkpoint | BMS - BMS Alarm
39def8fa-782d-4d04-8cc2-d7d06f5f75fc | checkpoint | Manual Isolation valves position TBC
9affd15d-3cf4-4f3a-a75e-09ba74eda716 | section | Second Test
8f54e96b-208f-4843-ac6b-10a2e23b9be4 | checkpoint | BMS - BMS Alarm
8e9194c0-cacf-4f5b-b835-2e889882d69d | checkpoint | Manual Isolation valves position TBC
0bf7ab79-cacd-4748-8cf5-0972391ee2c7 | checklist | EL01 - Tunnel Fire Cell #1 - Fire Activation |  | EL01 - Tunnel Fire Cell #1 - Fire Activation
7eb0b64e-a316-4991-94df-85030f7f69bf | section | IST Test
2cda56c6-7850-4130-b3cf-0e671755e1c6 | checkpoint | IST Details
768cc282-cbe7-5ac7-bb6a-a34f75d214f3 | textbox | Test Method - Activate Smoke Detector in Tunnel Fire Cell 1
b6ce72d1-61de-59dd-8fec-863458185f13 | textbox | Area - A40
2148cb9d-b197-4b74-93df-880fe970460a | section | First Test
bdb778aa-845d-4e89-a21f-59c94965af01 | checkpoint | Fire - Exit signs direct Fire Cell #1 to evacuate to A40 building and Fire Cell 2. Fire Cell #2 and Fire Cell#3 evacuate via A01 Building
e760de1b-24dc-486f-8053-f4ccdfa41528 | checkpoint | Group 1 - Exit
d16cc13a-5564-4a84-990c-a87bd0acd571 | checkpoint | Group 2- Exit
aa96ca38-0e49-4140-b747-991790589749 | checkpoint | Group 3- Exit
5940a2a7-50ff-4c92-b291-b2eee11a299e | checkpoint | Group 4- Exit
95c39a90-1e9d-4e05-9c09-18c41c08ae68 | checkpoint | Group 5 - No Exit
7b326ade-baaa-4968-b620-d2bfd6195362 | checkpoint | Group 6- Exit
69ef555b-a808-4766-98a5-e035463564a8 | checkpoint | Group 7 - No Exit
49e67279-ffcb-44f7-bfbf-bbe936f5aac6 | checkpoint | Group 8- Exit
5a109a71-097a-4d16-82a3-70921b4cf4fd | checkpoint | Group 9 - No Exit
a1c91168-fbd3-4789-87fe-728599ac1c40 | checkpoint | Group 10- Exit
6017851d-7c22-488b-a56b-48992320e5a8 | checkpoint | Group 11 - No Exit
45cdc0b1-e02c-4876-ad39-ec81c5fefc8e | checkpoint | Group 12- Exit
68b5882a-34c9-464c-8770-6f04ba6aa609 | checkpoint | Group 13 - No Exit
43747f99-ec68-4d12-95c6-925a324442ae | checkpoint | Group 14 - No Exit
090b1a93-a7c2-4351-a606-6094a8ae6dda | checkpoint | Group 15 - No Exit
69cd932b-bdcf-4598-9129-f5228979516b | section | Second Test
79c8e75b-4b66-4351-ac6f-95d971ec0718 | checkpoint | Fire - Exit signs direct Fire Cell #1 to evacuate to A40 building and Fire Cell 2. Fire Cell #2 and Fire Cell#3 evacuate via A01 Building
2026627b-b480-45cb-b1f2-270b43019e9b | checkpoint | Group 1 - Exit
dd6d590b-409b-4b61-a8ad-9af1795a212b | checkpoint | Group 2- Exit
67fe5567-d77d-4d53-9daa-7213da86537f | checkpoint | Group 3- Exit
3ae353dc-c855-4ec8-83fe-8a13307bc550 | checkpoint | Group 4- Exit
d3d115b3-982c-4bac-9758-327501a606bd | checkpoint | Group 5 - No Exit
3c2c55b8-9a53-4740-8830-7d3c3abe8782 | checkpoint | Group 6- Exit
f21374bd-e3d9-4d31-90bf-46c0ecb3ab24 | checkpoint | Group 7 - No Exit
3f42dd46-65e6-4f96-ad5a-bbfbc3df6571 | checkpoint | Group 8- Exit
7fc6739e-9891-4a5f-a578-a7e8ece8ce5c | checkpoint | Group 9 - No Exit
6eae70e5-a4ea-4005-a1ab-ecfbf0317572 | checkpoint | Group 10- Exit
50b55b1c-13f1-4af2-8f24-d030bc094cd1 | checkpoint | Group 11 - No Exit
b9daf407-345b-407b-b0c3-597b94c97280 | checkpoint | Group 12- Exit
0278f736-1129-45fb-aac4-fc613cf326b3 | checkpoint | Group 13 - No Exit
6875a1fd-e130-411d-8288-edf9a73cdf5d | checkpoint | Group 14 - No Exit
71b8a95d-b586-413e-a2d1-5aa309a81efd | checkpoint | Group 15 - No Exit
7994bedf-86fb-420f-835a-93550365599f | checklist | EL02 - Tunnel Fire Cell #2 - Fire Activation |  | EL02 - Tunnel Fire Cell #2 - Fire Activation
841fe302-40d6-48d4-a52d-3f6515c03be8 | section | IST Test
8e72994b-da68-4944-92ea-004c8a7e3fb4 | checkpoint | IST Details
4f055451-49e8-5139-a9e9-e3df6cb7d350 | textbox | Test Method - Activate x2 Smoke Detector in Tunnel Fire Cell #2
c26da74e-d613-5d3b-abe5-daf515888c9f | textbox | Area - A40
8addbd6b-4d8d-45e9-bc47-6ed6012e12b6 | section | First Test
b77b007b-9447-404a-88fb-3d1775afc185 | checkpoint | Fire - Exit signs direct Fire Cell #2 to evacuate Fire Cell #1 and Fire Cell #3. Fire Cell#1 evacuates to A40. Fire Cell#3 evacuates to A01 Building
66c0bf28-79f5-4aa6-a5c2-9fdff7804b14 | checkpoint | Group 1 - Exit
5f3fc9e0-8ad5-4d75-a6fd-0f26802dfc03 | checkpoint | Group 2 - No Exit
de908a2c-5e8a-4e94-85a2-c51f152a9c0f | checkpoint | Group 3 - Exit
a1964260-234f-4ff6-8135-13cf0f36c0dc | checkpoint | Group 4 - No Exit
07054154-d0c7-4fc5-9131-c73639249154 | checkpoint | Group 5 - Exit
a8373f52-4811-4bd8-9b71-fa3e721ef863 | checkpoint | Group 6 - Exit
2f7c4de0-7a96-4417-839a-9213beec6a4c | checkpoint | Group 7 - Exit
b10d909d-52a4-4d2f-b236-f8c60025c586 | checkpoint | Group 8 - Exit
d11eddbc-815e-4f8a-8d5b-f84f5bd43179 | checkpoint | Group 9 - Exit
6e7ad1fe-f3f6-4225-9db2-6b3939f19f2b | checkpoint | Group 10 - Exit
703df681-ed65-40d7-904c-b9d5ca40967f | checkpoint | Group 11 - No Exit
9f4dbe46-845e-44ac-b053-f213a4a11c9e | checkpoint | Group 12 - Exit
c6b01e5c-d384-44f9-896f-9fc040e98eb3 | checkpoint | Group 13 - No Exit
30cd0261-30b0-43b3-b245-5cdc5b897b2c | checkpoint | Group 14 - No Exit
4d84d115-6c0d-4087-af49-2075364226d6 | checkpoint | Group 15 - No Exit
09bfac58-cdab-4be5-bdb4-0a6ccd2a3f2a | section | Second Test
75241a74-4c91-472c-a201-5cba72a82434 | checkpoint | Fire - Exit signs direct Fire Cell #2 to evacuate Fire Cell #1 and Fire Cell #3. Fire Cell#1 evacuates to A40. Fire Cell#3 evacuates to A01 Building
01887e69-d03c-4042-b2b5-9644ac3e16f2 | checkpoint | Group 1 - Exit
620f0af9-41c7-40e3-b98e-9ac917089c20 | checkpoint | Group 2 - No Exit
9d8553df-63a2-448e-aeb1-726f72e9fdd9 | checkpoint | Group 3 - Exit
90cb9d83-e21d-4585-a0dd-955325d9c75e | checkpoint | Group 4 - No Exit
601554d9-26c7-4a25-8486-7799f79b15ca | checkpoint | Group 5 - Exit
deeb41c9-09f3-440d-835e-5453edfd165b | checkpoint | Group 6 - Exit
7ac63a78-3922-4469-ad20-1a53bfca2332 | checkpoint | Group 7 - Exit
08b01d54-2fd0-4b59-9e2b-0998ebf007dd | checkpoint | Group 8 - Exit
f52f84eb-c0aa-4f3d-9cdf-9c9220e53636 | checkpoint | Group 9 - Exit
254b8569-d278-43d7-ae8f-a039ef61b219 | checkpoint | Group 10 - Exit
41b18e1f-ffd6-4ea1-a41f-eb6038b50eda | checkpoint | Group 11 - No Exit
45d4e8a3-8b84-4d66-b144-21e33fef0153 | checkpoint | Group 12 - Exit
46faacad-75f2-4c2b-b7fc-4078bfe0b5e7 | checkpoint | Group 13 - No Exit
b42ba7c7-edde-415a-af44-1317e529665c | checkpoint | Group 14 - No Exit
70f3bbfb-4dfd-49f9-9577-b48dc69fb279 | checkpoint | Group 15 - No Exit
b2bea3b3-5fa7-4c98-9e5e-9b09118d7255 | checklist | EL03 - Tunnel Fire Cell #3 - Fire Activation |  | EL03 - Tunnel Fire Cell #3 - Fire Activation
475a2adf-2d2c-49de-83a5-1886e4f050c4 | section | IST Test
401dc5ee-2d30-4e53-835b-248de0c6deaf | checkpoint | IST Details
707ed75f-d3f2-571b-8011-2769e79fbc1d | textbox | Test Method - Activate x2 Smoke Detector in Tunnel Fire Cell #3
6b140215-08f9-59ee-8f16-6f86388754b5 | textbox | Area - A40
dc66ecea-4ba9-4953-988b-0ac3785903d7 | section | First Test
fbcf2af3-6ad1-40e3-8aea-fd6a162a9adb | checkpoint | Fire - Exit signs direct Fire Cell #3 to evacuate via Fire Cell #2 and A01 Building. Fire Cell#2 and #1 evacuate to A40.
afc84b32-06c1-4562-8bf4-d137a49abd35 | checkpoint | Group 1 - Exit
374f3011-21b2-4745-8232-1fc4c003d4d6 | checkpoint | Group 2 - No Exit
11ba1863-5daf-4e42-be0a-3ec67aabc275 | checkpoint | Group 3 - Exit
678cf09c-c8f7-4ed0-a233-06d5597db2d9 | checkpoint | Group 4 - No Exit
f720673f-c232-4fe3-a6ff-56a3aabaa7a2 | checkpoint | Group 5 - Exit
901bf001-c577-4aa0-b8eb-2de72a265ff4 | checkpoint | Group 6 - Exit
c688e08b-4af5-404c-9edf-cb627640277b | checkpoint | Group 7 - Exit
e5f1202d-df8d-47a4-ad6c-44bc522f6de2 | checkpoint | Group 8 - Exit
499e2e0c-37d5-4827-a83b-e60d9aeb1ee9 | checkpoint | Group 9 - Exit
ed241bdd-b420-4650-b9a9-d0b7c045e706 | checkpoint | Group 10 - Exit
fa46110e-f447-4bad-8da4-f8a35f3f1a22 | checkpoint | Group 11 - No Exit
563cf122-347d-4ebd-8c1c-40a8627cde51 | checkpoint | Group 12 - Exit
8151514f-2616-4570-be51-f64b6e73f90c | checkpoint | Group 13 - No Exit
1d46735f-5240-400f-b3c6-b46760a59171 | checkpoint | Group 14 - No Exit
29a71c26-6468-4835-b8a9-ff5b95d78310 | checkpoint | Group 15 - No Exit
e06217a7-87e5-4cd6-81b2-24096281ba70 | section | Second Test
4077ffad-3327-4088-9785-a359ff6d80df | checkpoint | Fire - Exit signs direct Fire Cell #3 to evacuate via Fire Cell #2 and A01 Building. Fire Cell#2 and #1 evacuate to A40.
11795ac8-4d66-426a-a341-9d9e012d91b3 | checkpoint | Group 1 - Exit
f20a7245-45ba-4c1c-aa19-bba648b9048e | checkpoint | Group 2 - No Exit
ed393053-b389-4d33-be7f-1794fc015ce1 | checkpoint | Group 3 - Exit
ccc1a852-40a6-4476-9e50-f98bca427af6 | checkpoint | Group 4 - No Exit
47c464b5-06aa-4e95-9a3c-cae0ec300753 | checkpoint | Group 5 - Exit
c93b665b-0f52-4db7-96b8-5dc19b77cfd5 | checkpoint | Group 6 - Exit
04f8816e-c1de-417b-a7bf-c773a63319d1 | checkpoint | Group 7 - Exit
d78da39e-20ed-4be9-a6e5-64c948c1c454 | checkpoint | Group 8 - Exit
91b204ce-e8ef-47d1-a138-c45f716db038 | checkpoint | Group 9 - Exit
53c3b0fb-2eb1-4ead-9739-1f0d80401f40 | checkpoint | Group 10 - Exit
2b621618-ea8f-4c42-97fe-3100473457e6 | checkpoint | Group 11 - No Exit
0a649edc-aa8f-49a0-aea2-d4c0e9205c3b | checkpoint | Group 12 - Exit
e4aedbfa-d2e2-46a2-be48-283d9e56aaf7 | checkpoint | Group 13 - No Exit
31811a14-94d1-4b26-a1d6-6ba0ac5b11c1 | checkpoint | Group 14 - No Exit
a19e46ab-e6d8-4b2a-bd14-8e4aafeb9a54 | checkpoint | Group 15 - No Exit
cde8abec-e222-47d7-9469-24c369770570 | checklist | EL04 - A40 tunnel level Fire Activation |  | EL04 - A40 tunnel level Fire Activation
fa08d702-c171-4fd6-bfb7-c931de72d4e7 | section | IST Test
b47645e0-8b87-498f-bb89-518a8f4b2fce | checkpoint | IST Details
b179961e-cb96-5cc9-b735-a2c22752f055 | textbox | Test Method - Activate x2 Smoke Detector in A40 Tunnel Level
13aebfd3-677c-5b55-ba6f-bff55b6d679c | textbox | Area - A40
a1043f7b-52c0-4ac1-b3c4-aadb8f8c2395 | section | First Test
b268c0b0-4ba3-4fd9-8e93-b8447c450641 | checkpoint | Fire - Exit signs direct tunnel evacuation via A01
89fc0c2c-c1a2-481a-910f-80e040733a82 | checkpoint | Group 1 - Exit
cd2e7796-09df-4a56-a7b7-28a734f6cbad | checkpoint | Group 2 - No Exit
bd97cc1e-4d9b-46f9-ad87-63eeaf2875ef | checkpoint | Group 3 - Exit
9974d0c3-fb38-46fd-984e-ba91117ff373 | checkpoint | Group 4 - No Exit
0f7305aa-6f95-4e44-aa6f-1ee7458ddfeb | checkpoint | Group 5 - Exit
1413b941-f447-4b1e-acf2-b47eec9e5485 | checkpoint | Group 6 - Exit
8bf17d80-5e85-4bbf-9997-1ca24ae46ba3 | checkpoint | Group 7 - Exit
cd1ef0e6-3f14-4802-9d00-1f740c75b77f | checkpoint | Group 8 - Exit
30938d16-98bd-41d5-82f4-c1caec83083e | checkpoint | Group 9 - Exit
452258e8-c0f4-447d-9cff-0244a0d36913 | checkpoint | Group 10 - Exit
65e8da5c-fe8c-48f4-9db4-c85d956c1789 | checkpoint | Group 11 - No Exit
2ae6bfb4-ddb5-4d4e-9108-6fa462a86a6d | checkpoint | Group 12 - Exit
b96476b1-4179-4540-9076-b14e236f65ac | checkpoint | Group 13 - No Exit
595c3187-d6ec-4397-9e68-e6f9fb87e454 | checkpoint | Group 14 - No Exit
318bc0e0-50c4-49c0-8ccd-88ac98ee684a | checkpoint | Group 15 - No Exit
34ba0594-2070-4f34-afb8-b793c2d38a8e | section | Second Test
9552e82a-fd7e-4f9a-b678-25a79e16cdf4 | checkpoint | Fire - Exit signs direct tunnel evacuation via A01
fc44da56-3ebf-46b2-bf8a-9b20b36f5672 | checkpoint | Group 1 - Exit
c6ea395d-09c6-46e0-add1-02a82a1438c9 | checkpoint | Group 2 - No Exit
cab0179c-28dd-4519-a03c-0b2b94a80597 | checkpoint | Group 3 - Exit
f89eae59-7499-4d69-92dc-aac979ea829b | checkpoint | Group 4 - No Exit
023687b5-0406-43f3-b03d-c609f116af26 | checkpoint | Group 5 - Exit
4ce21afc-f21e-42ea-983d-b993ebb6b8dc | checkpoint | Group 6 - Exit
3fab3516-1f21-4f94-97f6-d4ee435058f4 | checkpoint | Group 7 - Exit
254ac2f9-bbd5-46a7-9642-b57c87e785c4 | checkpoint | Group 8 - Exit
a3a3544d-2146-4dc2-9b2c-1bc92d2f5f02 | checkpoint | Group 9 - Exit
8c9fe936-0836-4864-af9f-599ad1638e73 | checkpoint | Group 10 - Exit
4a84e48e-0ee2-4345-a405-0ee5c684fb28 | checkpoint | Group 11 - No Exit
ae1ffde4-d0ed-4d9a-9f50-ad31052116a4 | checkpoint | Group 12 - Exit
b17b0155-76eb-484a-8843-dc1f762ff6c0 | checkpoint | Group 13 - No Exit
ad4111f3-e5c4-4cc4-a2ee-7b879a7ae80b | checkpoint | Group 14 - No Exit
72035a05-0240-4cf6-9d0c-907fb7ccd7f9 | checkpoint | Group 15 - No Exit
c6bf87e2-0f38-4d89-83cb-c7d473e3c191 | checklist | EL05 - A40 Non-Tunnel Fire Activation |  | EL05 - A40 Non-Tunnel Fire Activation
5139c0ad-2aa9-4212-ab90-15a7d1db0fb6 | section | IST Test
5ea2a45b-dd9c-4d76-af7a-ab5432ccb03a | checkpoint | IST Details
aa08b2ff-7e6c-5a24-979b-73290d1a93dd | textbox | Test Method - Trigger MCP in Non Tunnel Level
e3939a86-a6bf-57af-aa58-7bb5383d61e1 | textbox | Area - A40
1251a8cd-ddec-4829-849d-1e959089fa48 | section | First Test
82bea3e4-c9c8-485c-9abf-afbc0928dd13 | checkpoint | Fire - A40 Fire Alarm does not impact the tunel exit light system. All lighst sould illuminate EXIT allowing free access between fire cells.
c5e1df5f-c067-40bd-8edd-646cf11b19bb | checkpoint | Group 1 - Exit
64aa068e-a85c-493e-a38b-d6b832a9d015 | checkpoint | Group 2 - No Exit
d3ec6d5f-994b-4597-a068-c463263cbfe3 | checkpoint | Group 3 - Exit
227c16f6-e8b0-4ce8-9a8c-7e42460dd265 | checkpoint | Group 4 - No Exit
10c5dc99-2398-4ff1-b6c7-f4451d58b17d | checkpoint | Group 5 - Exit
03805273-ec3c-4a4c-a36b-629387abd8f4 | checkpoint | Group 6 - Exit
c29c638c-fdab-4f49-a8f6-5e478eb67747 | checkpoint | Group 7 - Exit
450abe4f-10ff-4716-baba-5b1d6a557f2c | checkpoint | Group 8 - Exit
96273da1-d8a9-451c-b509-1274531f7852 | checkpoint | Group 9 - Exit
032ddcb3-877f-4f57-b383-a6e6c671bbe4 | checkpoint | Group 10 - Exit
e4d50cf1-8349-4d9e-a59c-5198948106f4 | checkpoint | Group 11 - No Exit
9beb0848-b74b-4f6d-902f-e829e0f16c57 | checkpoint | Group 12 - Exit
59c167d9-3ff9-400a-8c74-1b81b5a6116b | checkpoint | Group 13 - No Exit
b8098a1b-b03e-45cf-b6bf-689d5ee2090a | checkpoint | Group 14 - No Exit
db540047-415b-473b-8164-b546edbbd79f | checkpoint | Group 15 - No Exit
7ad1ae7e-2688-4da1-b355-01a16fd4901a | section | Second Test
a3360f62-d748-4690-9116-10f139912efa | checkpoint | Fire - A40 Fire Alarm does not impact the tunel exit light system. All lighst sould illuminate EXIT allowing free access between fire cells.
a8ce3f53-5e9c-4144-b5b2-a64aa00afa6f | checkpoint | Group 1 - Exit
06520572-079a-40bd-b4cd-bf182096b8e1 | checkpoint | Group 2 - No Exit
0203e606-fc05-42c6-9713-200ad1553270 | checkpoint | Group 3 - Exit
019c1669-03da-48d1-b23f-58bd029ad0bd | checkpoint | Group 4 - No Exit
00cff6a8-f3b8-4f10-b2d0-ac34bf5ce1e4 | checkpoint | Group 5 - Exit
a5ecdaba-b4b1-4de7-b92e-fbb45de591df | checkpoint | Group 6 - Exit
99631593-2a16-4f65-b633-ce28a0de0d4f | checkpoint | Group 7 - Exit
84faf354-f6be-4bab-9aa2-bb9353a71dfe | checkpoint | Group 8 - Exit
303c39d4-19c5-4188-a03e-3dee6104e331 | checkpoint | Group 9 - Exit
cbad72ad-2909-4f66-8fe3-7ee871a35fcd | checkpoint | Group 10 - Exit
93e0ea3d-b86b-4990-aaea-ab8bf78b6a56 | checkpoint | Group 11 - No Exit
16f8b69d-195d-4112-a84f-ba509687ab9b | checkpoint | Group 12 - Exit
a641abe0-9878-48e3-b2d4-ee4b9188263d | checkpoint | Group 13 - No Exit
5d15618c-e8d1-4db0-9051-5e2457ed87e2 | checkpoint | Group 14 - No Exit
9b5afb15-19be-4de8-9c6a-1917d0757800 | checkpoint | Group 15 - No Exit
c57220b0-fc3a-4b3f-8638-57877cea8e5e | checklist | Electric Fire Pump |  | Equipment -
546dfe0c-7365-4731-9ba1-17bf5700bc11 | section | Factory Acceptance Testing
80ff4841-f4dd-4ae7-9b2a-7c003ddd4d39 | checkpoint | Factory Acceptance Test Report
5eca2ca4-e399-4028-ba6b-502a3b6a33f9 | section | Pre-Commissioning
2b6c7cf4-561d-443e-90b7-caf1adb307ae | checkpoint | Pre-Commissioning Test Report
55f5d78f-d6ae-4e57-92c3-a71ee109ec4d | checkpoint-no-value | Mcconnell Dowell
8257c38e-9e5a-4f4e-9f36-4f6587e1a304 | signoff | Request McConnell Dowell Signoff
ad2b9884-1e24-4304-9595-c1b07292b427 | section | Commissioning
b50aeecc-495b-41f9-86ae-d920b8d7fecc | checkpoint | Electric Driven Pump System Commissioning checklist
b48d4dbf-f9be-417e-a037-a83e5213eeb6 | checkpoint | Electric Driven Pump System Commissioning report
e5c43fa0-c10c-49e0-b3ce-907065732ce5 | checkpoint-no-value | Mcconnell Dowell
6e6a183f-a632-4f03-8ef6-07dfdb4aa6e0 | signoff | Request McConnell Dowell Signoff
3eabf2e3-ec5f-4447-bcc9-e422b38804c6 | checkpoint-no-value | Beca
1ddcef29-37b1-43f2-9ac1-413ba080c46f | signoff | Request Beca Signoff
57defef1-cbf4-457f-9b08-611c63fd9ea2 | checkpoint | Completion and Certification documents
b56d85b4-96ee-4326-a3ad-82fe55b13a2f | checkpoint-no-value | FIRP Signoff
9519d9f2-3845-45b1-b9ac-86d89e31bef0 | signoff | Record of Witnessing
576d3603-aad3-4c16-963f-a03419f538fe | checklist | Emergency Lighting |  | Equipment -
03d41d0c-0d7f-4db3-87b0-502c8058366d | section | Commissioning
915e1623-33e7-43b3-a8a9-246592e994cb | checkpoint | Emergency Lighting Check Sheet
9b975df7-a55c-4498-8e6f-c5810ed73f2d | signoff | Request McConnell Dowell Signoff
8777a7f0-a01c-499a-9a1a-2e760f606dd7 | checkpoint-no-value | Beca
ab63c479-df93-4acf-90d6-083111a998a2 | signoff | Request Beca Signoff
5fc9ff17-731c-4cc1-85e1-1f2a8e4f4c02 | checkpoint | Completion and Certification documents
904edd72-a9b2-4e43-9caf-9deade10166f | checkpoint-no-value | FIRP Signoff
9b9c5744-56d8-4841-a77a-07ba2032355d | signoff | Record of Witnessing
d1d18fc3-503b-4542-9f91-6b3e2109c817 | checklist | Fan |  | Equipment -
273aae04-c211-4cb4-b5d8-7c44fb7b8795 | section | Factory Acceptance Testing
b40d0e16-d3a6-4f81-96fd-f0ee362cd8dd | checkpoint | Factory Acceptance Test Report
3fab8df9-c29c-470e-85fc-c1fda4d98d71 | section | Pre-Commissioning
00c656d8-fc4b-4024-8b07-ea21c9f4a53f | checkpoint | Model Number
f1e99650-fa34-524f-b9ae-c2c2b5fef384 | textbox | Model Number
fc6e5165-9903-428a-8479-89d702b05649 | checkpoint | Visual inspection, no apparent damage
bed9c1af-1635-4272-b856-6042c9e25ae6 | checkpoint | Free of dirt and debris, filters installed
84c02e2d-d414-4efc-96df-c67e1550c6c6 | checkpoint | Impeller rotates freely
5656206e-6606-4ffa-b65c-7efa199e0d1c | checkpoint | Motor/fan vibration isolator in good condition, shipping bolts removed
f822ec3f-4dec-4c13-a6a6-d83e3441fd2f | checkpoint | Access door gaskets installed and not damaged
0d0cd5e7-d280-4f0f-b080-b9fba23804ba | checkpoint | Ductwork complete and leak tested
e29899d1-9d0f-4b2a-9743-790a797a747e | checkpoint | Fire/fire smoke dampers open and accessible
62e5b04e-332e-4b03-afcc-7644247961ae | checkpoint | All dampers (OA, RA etc.) stroke fully
54cfbaa2-285a-4632-9ec1-ec207bab1175 | checkpoint | All protective plastic removed from duct openings
5faa1e09-0373-4089-a7ee-7de6b6d66e13 | checkpoint | All second fix outlets installed
5e8aa284-0fb3-4b3b-9e27-5ab8aa93b637 | checkpoint | All manual balancing dampers installed and locked 100% open
735cfff3-99ac-4409-baee-73dfd17ccd50 | checkpoint | Local isolator installed in accessible position
14914f6a-389e-4df6-8134-9d8247b7e0fb | checkpoint | All power and wiring installed correctly
585513ce-dac3-455e-b6cb-479497d6c073 | checkpoint | Motorised OA, RA and spill air dampers actuators installed and operational
24cb00a9-0785-42f8-88d5-95416c0a9bc4 | checkpoint | VSD programmed and integrated with BMS
a6549201-d927-4e7c-ada7-f9e80ccd5098 | checkpoint | All electrical components grounded correctly
e0c95f4f-6206-4dd3-9ffa-5d041c76b757 | checkpoint | Motor rotation checked
a209da9a-2c33-48ee-9ec5-3d079d1d0a10 | checkpoint | Controls point to point checks completed
1b758c33-430d-4236-b773-411b60cdae73 | checkpoint | Windows and doors installed in areas served
c1b76afe-1f78-42b0-8a05-5ed5d9e17af5 | checkpoint | Outside louvre installed
400df048-d539-4737-b3f6-d95b18de4a17 | checkpoint | Ceiling access provided to dampers, valves, actuators, controls, filters etc.
70721e65-0803-48c0-afeb-e618e00a8a69 | section | Commissioning
3974c995-2e79-436c-8ca3-3d68b445f92c | checkpoint | Fan Commissioning report
02b39031-ae26-41ff-9402-72b09dfc3770 | checkpoint-no-value | Mcconnell Dowell
b60f25d7-dc31-4ba0-9b39-c7081d5810e2 | signoff | Request McConnell Dowell Signoff
73d36526-7441-4328-ab75-1719c960ea1f | checkpoint-no-value | Beca
82744899-fa80-4d67-9abb-3ea669394695 | signoff | Request Beca Signoff
eb54197b-2084-4878-a9e7-d8713b1f1a47 | checkpoint-no-value | FIRP Signoff
5f7960ed-0119-4285-85bb-332bf17a466e | signoff | Record of Witnessing
234d3c3c-80c0-4d98-a822-84af3c645e4a | checklist | Fibre Cable |  | Equipment -
a1f8bdf1-3d48-4d59-adc1-c1dc56510927 | section | Pre-Commissioning
884fb628-b80f-4add-8b51-e73744fa6b60 | checkpoint | Fibre Point to Point Testing Report
9ffa96be-bfe9-4ee8-a617-4b1713b1fec2 | checkpoint-no-value | Mcconnell Dowell
93a0f014-779b-4904-a7c5-bda6b23d25eb | signoff | Request McConnell Dowell Signoff
890ad5b9-78eb-4038-9af4-094e20b22842 | checkpoint-no-value | Beca
84fc95fc-a9f4-4bf6-80eb-20c4fc06a795 | signoff | Request Beca Signoff
92f70ae0-ad4f-465e-97c8-3eaf3af3246f | checkpoint-no-value | FIRP Signoff
8aaf697a-d8be-4d04-b67d-e60f3a4c59c0 | signoff | Record of Witnessing
79ad5ce4-6fa4-4021-94ab-85054e8147cd | checklist | Fire Alarm Devices |  | Equipment -
efb4004d-7447-4612-bf5d-a48274dd959a | section | Commissioning
4ed081bb-644f-430c-b38a-a7534c449e8f | checkpoint | Commissioning test - Fire alarm loop
2236b5c5-055b-4c17-8395-0680caa3a690 | checkpoint-no-value | Mcconnell Dowell
a2c6c961-65d7-460b-9362-c82dcbb8a48c | signoff | Request McConnell Dowell Signoff
8d34748f-6477-448f-a49d-f95a095677b8 | checkpoint-no-value | Beca
9cfa39ec-e9f3-46b6-be28-c4186eddb965 | signoff | Request Beca Signoff
8bd26ce5-977d-495a-b40f-00c1e916f357 | checkpoint-no-value | FIRP Signoff
d178c213-743d-420c-a533-62802f71075b | signoff | Record of Witnessing
7b6c6a2f-1237-4777-8a28-a4dd15626161 | checklist | Fire Alarm Interface |  | Equipment -
c59d4773-9e81-4e14-9a52-28fbc321914e | section | Pre-Commissioning
1b0e528a-9aeb-49a3-a085-cb6a31824cbb | checkpoint | Pre-Commissioning Test Report
cb2739ab-bd36-41af-a139-3ca09c54db48 | section | Commissioning
14c662bc-a8a1-4866-b785-d77f96b5084d | checkpoint | Duct detection operational
6c728ddd-1456-4a01-8b03-ef0317c9b4be | checkpoint | Fire Alarm Switches operational
d3c66541-030b-47bb-b8b7-678883931e46 | checkpoint | MDHO operational
25c6045b-0610-4a78-858c-7ce6d162bea4 | checkpoint | Security auxiliary functions operate correctly to the relay
43945045-b609-47be-9e7b-f9938291d075 | checkpoint | Mechanical auxiliary functions operate correctly to the relay
306478a0-ef2c-4ff2-a874-f999e6b0c064 | checkpoint | Electrical
49f02c5d-8f0e-4a35-b0e5-d511b16c81af | checkpoint | Vertical Transportion Trade
bbfc414d-095f-47c3-a3e7-5db1b91e6174 | checkpoint | End to end Security auxiliary function tests carried out with the respective contractor
55b424e3-0b01-4f3c-b3a0-ea3c05892955 | checkpoint | End to end Mechanical auxiliary function tests carried out with the respective contractor
e3e54f15-5489-4507-b649-f72a0ef43c2d | checkpoint | Check the function of all sounders/lights from the panel/Sprinkler DBA/Flow Switches and Monitored Valves
b121d55a-c94c-4984-bdb4-390559ce1c60 | checkpoint | Carry out a full function test on the panel.
37d29532-88e7-4dad-a4de-df79f5624470 | checkpoint | Carry out an initial survey and complete forms
edaf83f9-1f78-4205-bbaa-d1d8ba26fc8e | checkpoint | No material, plant or rubbish has been left on site
e00cb20c-d306-4a0e-8b28-70ec1feb7eae | checkpoint | Fire Alarm Interface Commissioning report
333651bc-755c-4678-9d42-f09d32257602 | checkpoint-no-value | Mcconnell Dowell
a098401f-7a3b-4de6-a559-2bf2852fa61f | signoff | Request McConnell Dowell Signoff
ff80a774-5afa-48e6-8b33-fdd1de4a280e | checkpoint-no-value | Beca
be33f635-5841-4f70-9f0f-474a92b74c9e | signoff | Request Beca Signoff
b13ef493-4f33-4089-bea6-97e5ce89f96d | checkpoint | Completion and Certification documents
e540d346-ef2d-46b5-ae6c-e34029a4dd9a | checkpoint-no-value | FIRP Signoff
52025c43-9742-4985-b8c8-2c98965468ad | signoff | Record of Witnessing
1b84bcb0-a94d-48fa-8bcb-dc9e0114dec0 | checklist | Fire Alarm System |  | Equipment -
221e0589-2dd7-40fb-85f4-4406a89f6099 | section | Pre-Commissioning
044ef2ca-f409-4e74-b5f6-f8ef131ac8f8 | checkpoint | Fire indicator Panel tested
716251bb-19bc-496c-b5be-e71a3eaf384c | checkpoint | Addressable fire modules tested
c7c0c7d2-a360-4f1e-b158-de7e3811f288 | checkpoint | Record of mechanical device commissioning
deb1dc6f-0453-4756-a5b7-de7a96c7c387 | checkpoint | Record of diesel system testing
b1bea3f9-e39f-45d4-858a-e9c70322ac05 | checkpoint | Record of tunnel emergency lighting testing
c0d4f925-2834-4f8a-8018-236210a3ead6 | checkpoint | Record of lift testing
92f1cd7d-c1fb-45fd-bcff-65f2545693d4 | checkpoint | Record of access control testing
09c77b4f-15c6-422d-9480-9a7c086ab5f3 | checkpoint-no-value | Mcconnell Dowell
73410f06-0c14-4156-9705-947f18f473cf | signoff | Request McConnell Dowell Signoff
9bb4da85-5b90-4e14-8ede-3d7621388ef1 | section | Commissioning
92e43d0c-2f28-4a5d-89f9-3f9e65f406c4 | checkpoint | Panel wiring and panel general tidiness. Tug test all cables
6966edda-93a5-43f9-98aa-32021d1a6490 | checkpoint | FA panel mounted square incl. index and window, make sure both are clean
46d180ed-6bde-4c93-9354-8229f595d2cc | checkpoint | FFCP panel mounted square incl. index and window, make sure both are clean
1d6e9278-6e56-4dad-b3a8-41c2d032fc7c | checkpoint | Index fitted and correctly engraved
c03d77d4-b488-42df-8cc0-ca43b2bf8b09 | checkpoint | Mains fuse is labelled as per NZS 4512 and is the mains connected
8af7d52a-2a98-4338-95f2-4d72dd708510 | checkpoint | Gell cells and battery leads are secure
7a59955e-2382-4ed4-bf19-66de61abeff1 | checkpoint | Auxilliary relays operate correctly, check diodes across coils
88d751df-8de2-4372-a4cd-c0b09c0cb61d | checkpoint | All auxilliary functions operate correctly (air conditioning shutdown, lifts, door releases etc)
e2b3fa16-afe7-44d1-856f-46eba29150ae | checkpoint | Check all ZID / SID, are they correctly labelled, lids on, wiring tidy, etc
9ff3030a-96d8-4753-a249-10695bd66b65 | checkpoint | ZID / SID are marked inside the panel. Power supply, mains, telecom point, etc complete with location sketch
0d6f9d99-2d59-4cfc-b015-4822cf15a807 | checkpoint | Call points and sounders are square, centrally located, in straight lines and well secured to the wall
8cfadca9-d910-485e-9705-f6faf2a2f6f6 | checkpoint | Conduit and trunking is fastened correctly and square to other services
8263fe4a-6be4-4ebe-b63c-2f03acf724fd | checkpoint | Detectors are mounted securely and guards are fitted where necessary
12d3e44a-89d2-49c9-a284-4d7b4474d69c | checkpoint | Detector and call point spacing, height, labelling and coverage complies with the standards
54f4346b-0c4c-41fd-ac94-b3d93d4b447a | checkpoint | All call points operate back to the panel and operate the correct zone
dc86b51e-e4f4-4fde-8a6a-7fe90ff0bb8c | checkpoint | Test smoke detectors with test gas and check they operate correctly - alter sensitivity level as/if required
ec89200c-33c5-445b-b5c8-6ff843dbc268 | checkpoint | All call points and detectors are numbered correctly
21fcc196-651a-488a-ac3c-af5b0fb441b2 | checkpoint | Has 230 V supply connection to ASE / panel been installed and labelled
9a4a5f63-f5c9-4e86-8acd-042eb919663b | checkpoint | Check the function of all sounders / lights from the panel and the sprinkler DBA
81d0a37d-663d-4338-b823-5b58ba231226 | checkpoint | Carry out full funtion tests on panel. Fill in program sheet as displayed. Config down load data.
0d0a8f25-5ab9-4896-9f60-b4f8cf4caf2b | checkpoint | Carry out an initial survey and complete forms
8b132dee-35b4-45ef-91df-581abb91826f | checkpoint | No material, plant or rubbish has been left on site
a5a80292-c5fd-4a77-a0cc-dacb12fee017 | checkpoint | System is operational
35f773ac-4b77-4d28-b42d-7327e2d1ca95 | checkpoint | Site file handed back to project supervisor
fa81bf12-17f3-44f3-873c-ed0e259b9453 | checkpoint | Leave one of the trial evac keys in the Bell Cut Off switch or with the manager
698c0f26-23cc-4fcb-8121-559a276f09ae | checkpoint | Is the system completely finished and ready for BFS inspection and Brigade connection
9c77e6df-5ee8-44c4-b617-854f2b3bbe7e | checkpoint | Testing of alarm at various monitoring stations is to be carried out when the complete system is installed
a4cd6295-140f-4ca4-9e98-887439439ac6 | checkpoint | Fire Alarm System Commissioning report
f9994947-fc3c-4e6b-9628-13961dbd1946 | checkpoint-no-value | Mcconnell Dowell
a58b8026-0960-4101-933c-6b0730e20b02 | signoff | Request McConnell Dowell Signoff
6192d77e-15c1-4f76-9d4d-563aa30adf6b | checkpoint-no-value | Beca
afae8d53-f7e1-4d82-9cc6-c739b00265d0 | signoff | Request Beca Signoff
5fcaa8e2-7c2e-4664-a06c-7e0c39562e94 | checkpoint | Completion and Certification documents
d509b357-356c-4acc-a90b-b076f3890b86 | checkpoint-no-value | FIRP Signoff
ccc51181-f702-4ebc-982f-8e0976ae3fa4 | signoff | Record of Witnessing
1a632a96-ac2a-43f5-ab2c-a11ac73699a5 | checklist | Fire Sprinkler Inlet |  | Equipment -
0f7f81af-1a48-4367-a104-a4ef16e48558 | section | Pre-Commissioning
64468cf6-aad0-4710-adb6-07e3b3b436fe | checkpoint | CABINET DOOR OPENS EASILY
3cc9b244-d915-4d2c-aa37-538efd008d3d | checkpoint | CABINET IN GOOD CONDITION
9b7a0745-ddca-498a-8d6f-88adf565c55e | checkpoint | CABINET BACKING AND DRAIN FITTED
54d03b46-35c8-4484-962d-0a1f85469e5c | checkpoint | DOOR LABEL SATISFACTORY
5fc2d8b1-8672-4abe-a596-5b487ab81e70 | checkpoint | OPEN BEFORE PUMPING SIGN
c44df89e-048c-4a55-8409-64367de749ca | checkpoint | STOP VALVE FUNCTIONAL/HOUSED IN CABINET
587561f3-876f-492b-b04b-51ea1ebb363c | checkpoint | EXTERNAL DRAINAGE SATISFACTORY
7952002c-1f27-42d6-977f-de669445db0b | checkpoint | FSI GAUGE FITTED
18592b76-c4cc-4ab3-a961-9b65083ab7b0 | checkpoint | “BOOST PRESSURE…....” SIGN FITTED
de33b978-ca83-4fe7-9a2a-a805bbf8ec1a | checkpoint | FSI GAUGE SHADED
67ababe7-a1f5-4691-ae77-44801392375f | checkpoint | FSI VALVES/GAUGES NUMBERED
25916ffc-0e00-4caf-b3b1-bde7335737db | checkpoint | ONE INLET PER 1200 l/min (1350 l/min FOR ONE ONLY INLET)
e9d27f07-876a-414d-90cf-be18bc8ba8d3 | checkpoint | DRAIN VALVE FITTED BELOW STOP VALVE
d6835d7f-4b40-469e-aef4-514438c14f44 | checkpoint | COUPLING & HAND WHEEL CLEARANCES COMPLY
5fc4672f-67cc-483d-832e-c88d704ddb0f | checkpoint | QA & Point to Point check of controllers
c311f235-ab85-4456-943f-914ad349262c | checkpoint-no-value | Mcconnell Dowell
cc82099c-86c6-42c6-8d54-6458e1c9a98e | signoff | Request McConnell Dowell Signoff
9121b164-e6e8-47b9-869d-cc9a9086afa6 | section | Commissioning
6bc6af37-48d5-4d6c-90f1-a2e440fe2fdb | checkpoint | FSI commissioning Sheet
2875b9e5-f1f1-460c-bf36-9c42c00cb8a0 | checkpoint-no-value | Mcconnell Dowell
96721de6-bd3c-423f-a52f-868cff646775 | signoff | Request McConnell Dowell Signoff
0923e418-c0ed-4420-8d8b-61bee71ec682 | checkpoint-no-value | Beca
5af2a97a-98d4-4936-8007-003e20065802 | signoff | Request Beca Signoff
58b4fe33-104f-44a0-8e8e-61ba2e65d59b | checkpoint | Completion and Certification documents
d083f8af-fe0f-4209-b661-67c3609ca779 | checkpoint-no-value | FIRP Signoff
e3075799-077f-4e30-ad6a-f066342c7def | signoff | Record of Witnessing
231de980-809b-4c2d-9296-378543cc4873 | checklist | Floor Distributor |  | Equipment -
6b5c5cc3-f803-4279-9b3d-9e319a9e3851 | section | Pre-Commissioning
3c0cd695-2ff8-4af3-9018-da1fe14e6ab3 | checkpoint | Precommissioning report
69540de4-0318-4d42-b255-215c718be2db | section | Commissioning
f602a43f-7b3f-4dc7-93af-5aa4e6f24282 | checkpoint | Commissioning report
5486eb35-dffc-44a2-975e-9e095111ae95 | checkpoint-no-value | Mcconnell Dowell
4aea5338-ccaa-461d-b914-2e310f67f4c0 | signoff | Request McConnell Dowell Signoff
a7b0ca23-b33e-41e3-b694-bb7305d07a21 | checkpoint-no-value | Beca
6b16d4d8-786e-4c82-8b2c-d86462adbb39 | signoff | Request Beca Signoff
340059c1-f6ad-4b43-b133-f7c59e92dc60 | checkpoint-no-value | FIRP Signoff
21c8c557-ec58-4f8d-9e16-e17774c25f87 | signoff | Record of Witnessing
cc896fd1-44dd-45c0-a7ae-9ace203c010f | checklist | Fuel |  | Equipment -
34ee3d9c-3553-4439-bbd4-9e17ea597a19 | section | Factory Acceptance Testing
81947f2c-0c94-4d27-a99a-7149c2915504 | checkpoint | Factory Acceptance Test Report
08cdf972-19cf-4853-91f7-f8764e311a2c | section | Pre-Commissioning
17808293-9d6e-43d6-a41c-b7f968b50dfe | checkpoint | Pre-Commissioning Form
11544301-cee8-425f-bbda-dc6ce9a0e68f | section | Commissioning
19373f7d-1c2d-4f2f-adcc-1c6bc8d8a4d1 | checkpoint | Fuel Commissioning report
dc016235-9c07-4241-9d0a-45bd4c2529b0 | checkpoint-no-value | Mcconnell Dowell
6ea4b761-ba6a-4ce1-a620-82a338a8a496 | signoff | Request McConnell Dowell Signoff
8aa06df7-9b33-4f27-8ac5-fc061b4b7f61 | checkpoint-no-value | Beca
1dfaf5a5-e091-4196-9d7a-731b2a3ffda8 | signoff | Request Beca Signoff
7c7f56de-8deb-4ea8-b596-d50163146853 | checkpoint-no-value | FIRP Signoff
f0fafeb7-f962-49c0-8926-d13dce7222c8 | signoff | Record of Witnessing
3aaf7fad-d22c-4918-9760-81d361f6e0f3 | checklist | Fuel Oil Control System |  | Equipment -
dfe59252-e9bc-4470-ba60-5e406fc87c61 | section | Pre-Commissioning
6d05e0a0-e687-45ea-a900-d4116b36317c | checkpoint | QA & Point to Point check of controllers
bd4273e0-67f1-497e-8a5d-da15a7a853de | checkpoint-no-value | Mcconnell Dowell
88c101e5-b4e6-4e0f-87dc-645e51fa2f69 | signoff | Request McConnell Dowell Signoff
eb3a7a12-2dd7-4d9c-8597-3c6d5e448789 | section | Commissioning
528f77a7-670e-4712-bc25-764e3ee8efb9 | checkpoint | Fuel Control Commissioning Sheet
b66ee410-600a-471c-976e-5daa414d790b | checkpoint-no-value | Mcconnell Dowell
28ac4434-9d27-4d08-acdf-ad2ba376402e | signoff | Request McConnell Dowell Signoff
642d8c97-ac3f-4820-a522-0896691cf0e4 | checkpoint-no-value | Beca
b973d4cc-fac5-4826-b18f-bf41a2035f0b | signoff | Request Beca Signoff
11968195-66c5-4343-89f1-1f4efbfda7d7 | checkpoint | Completion and Certification documents
664e7950-5b8c-4a60-8d28-6f7a22db8fb4 | checkpoint-no-value | FIRP Signoff
588b04a9-e57d-48b1-9776-19455feb8b9f | signoff | Record of Witnessing
7213f3ce-ca62-48c6-8159-62f71236edbc | checklist | Fuel Pipework |  | Equipment -
f3738023-fd72-446e-a329-073199ede49e | section | Pre-Commissioning
af68079a-b1fc-421e-a3a8-8656a32b6789 | checkpoint | Pipework pressure test QA
1bc799b6-4948-440e-8e55-c06f90daac56 | checkpoint-no-value | Mcconnell Dowell
feff071e-e1da-4bb2-960e-10e1c323d95c | signoff | Request McConnell Dowell Signoff
516aeedf-c8bd-4c6a-a1bb-07fcc0af0352 | checkpoint-no-value | Beca
91d387ac-f9e0-4171-bfda-f0443d61a974 | signoff | Request Beca Signoff
46336374-ab99-4667-a469-cf3f060a3f67 | checkpoint-no-value | FIRP Signoff
671dc132-9116-40b2-bfab-2405e492cf9e | signoff | Record of Witnessing
8a021e4c-71af-4bbb-ad72-c7688f8d0a9d | checklist | Fuel Tank |  | Equipment -
7fb22d97-f8bc-4f5f-ba70-e503e2dc79cc | section | Factory Acceptance Testing
4f1213e1-c1a5-45d8-9c26-8cbaf585db2f | checkpoint | Factory QA report
a247f8c5-23e4-49d9-a437-877a3b50601f | section | Pre-Commissioning
c6b3ddd4-485f-4c2d-9e6a-16759fdf665b | checkpoint | Tank installation validation checklist
594fc0cc-ad42-4349-b8e6-da6e63481d66 | checkpoint-no-value | Mcconnell Dowell
82249687-cda5-4f87-8908-76382cc78de7 | signoff | Request McConnell Dowell Signoff
5abd7669-543f-47e0-92ce-136c2a01eb9c | section | Commissioning
66906dce-2533-444f-8a42-c77ab9694d09 | checkpoint | Tank Commissioning checks
fefd19af-0c78-43ef-b510-37a869fb0494 | checkpoint-no-value | Mcconnell Dowell
1e984866-6503-40f5-9a5b-b98e7ee7d508 | signoff | Request McConnell Dowell Signoff
682a865f-09ed-4f6c-a391-a30db0833dc8 | checkpoint-no-value | Beca
19a9f693-e45c-4c26-bda0-c289c5edbbdb | signoff | Request Beca Signoff
e8ed12c4-c730-40fc-9cd3-5d0a7a683b3b | checkpoint | Completion and Certification documents
69613b9f-f9c9-47a3-9619-d6bd9aeefc0e | checkpoint-no-value | FIRP Signoff
0e445675-c9f4-4810-92b6-1ddf887ad1d9 | signoff | Record of Witnessing
871b8080-94fa-4cf1-a345-f013ad491d26 | checklist | General Building Earth |  | Equipment -
992b01ef-403f-4676-b864-569b6fedc337 | section | Commissioning
84a548b6-1f17-4581-81e3-7dd49d3aea9c | checkpoint | Commissioning report
50d0c732-28d1-419f-9606-60db2c234546 | checkpoint-no-value | Mcconnell Dowell
ed0552f7-d092-4961-b095-338f40558300 | signoff | Request McConnell Dowell Signoff
871ed210-1a31-4a58-9fe7-d43e891da6e1 | checkpoint-no-value | Beca
87a0bd31-35aa-4f54-b091-3d688ee0298f | signoff | Request Beca Signoff
ecb1c8ac-0342-49ca-abe9-40934b8d6689 | checkpoint-no-value | FIRP Signoff
e060fd61-5cf9-4dd8-95de-2aa0ed56bd09 | signoff | Record of Witnessing
0310fbc7-66b4-406d-9b9b-de664978f769 | checklist | Generator |  | Equipment -
e393fb40-18a9-46d8-b9ac-45b34ce0f5b9 | section | Factory Acceptance Testing
41c10ac4-9c9a-4e8f-a1d1-12d0ba9e867b | checkpoint | Factory Acceptance Test Report
33c9cb94-a9ce-44f9-800c-cfddc8c88930 | section | Pre-Commissioning
3b99c3da-b04e-41ed-bc68-39492ee25960 | checkpoint | Confirm mains cables entering and exiting generator have been tested
57d6cd98-df3f-4e15-96dd-f030cbd441e0 | checkpoint | Confirm manufacturers instructions have been adhered to
cfe97a13-726a-4b44-b06e-93c0f441cf53 | checkpoint | Confirm all connections are tight
858a4f22-4e88-40cc-88bb-31d2bf195893 | checkpoint | Confirm all control wiring / alarms have been connected
cc086fde-dc33-49e9-8845-aa148e604a44 | checkpoint | Confirm Battery racks are connected
ae542e06-302b-4fdb-9211-b85198b5a93d | checkpoint | Confirm Battery racks seismically fixed
2973f502-6c39-4180-b8f1-2c21720d3738 | checkpoint | Confirm generator seismically fixed
a58f6bf7-6ef5-482d-a3c8-01f69b8c3d82 | checkpoint | Confirm room finished and dust free before energisation
65ee257d-1fa9-4405-bab1-2988e360caac | checkpoint | Confirm any bypass / changeover controls are operating correctly
23ade097-f6e0-426a-bbec-3246ae72a22d | checkpoint | List any incomplete or defect items requiring remedial work.
a1423416-ef5f-41e9-85f0-f470c9e1a981 | checkpoint | Supplier QA Documentation
071f4857-0c2d-4553-bfe9-a2346fd078c5 | checkpoint-no-value | Mcconnell Dowell
2e65d8e3-c0c7-4a23-9cbb-b0d7fb17e76b | signoff | Request McConnell Dowell Signoff
04c24609-50bb-41a6-8370-e9ba414b55da | section | Commissioning
75d3fc9b-f684-42dc-abaf-4f0eafa596b3 | checkpoint | Confirm set up & commissioning completed by manufacturer (results attached)
bc5ccd53-63d7-46e4-911f-1a843d1db66b | checkpoint | Confirm earthing arrangements completed and tested
69896a13-8af0-4fe7-b29c-6b53bcf97d31 | checkpoint-no-value | Mcconnell Dowell
c75bce8d-39b1-40bb-bac6-a22554532663 | signoff | Request McConnell Dowell Signoff
d076183a-cdc5-4e03-b1cb-d8ef74a9ae76 | checkpoint-no-value | Beca
827a5d76-e65c-4cb1-9f07-acdb8e4c4171 | signoff | Request Beca Signoff
47775043-4959-4c4f-9518-2117789d6deb | checkpoint | Completion and Certification documents
f7e768e3-9c59-4f57-819c-8fb1d5f69a9d | checkpoint-no-value | FIRP Signoff
cb95ec52-3070-4b51-b037-9afd6739ecf7 | signoff | Record of Witnessing
6ead1f98-9bd9-4139-9a6d-c841cb124602 | checklist | Generator Control System |  | Equipment -
412fa50d-7065-4565-a860-36e8e4f66665 | section | Factory Acceptance Testing
42377ff6-a908-4bc2-ac89-a70100a63e41 | checkpoint | Generator Control FAT
c3f616c2-7d60-407c-b165-24daa41aa578 | section | Pre-Commissioning
be5bcf41-cfcb-45cb-9864-7b8ad6fb1ccc | checkpoint | Generator Control System Point to Point testing
60520dfb-df1c-41aa-aeb8-4489267eb430 | checkpoint-no-value | Mcconnell Dowell
a417ab50-12a1-4720-9532-b13665433c00 | signoff | Request McConnell Dowell Signoff
7bad8953-05fe-46fd-9f55-07c4c2d03857 | section | Commissioning
868d7d60-3d12-41eb-a0fe-dc9957e64447 | checkpoint | Generator Control Commissioning sheet
68521e7d-2f4c-4c36-95c7-c50ba37474dc | checkpoint-no-value | Mcconnell Dowell
2cf480bd-f8a7-4ed5-ab43-533613bce390 | signoff | Request McConnell Dowell Signoff
e7668bd3-012d-492c-ab73-01e3087f5c3a | checkpoint-no-value | Beca
65f0de19-97ff-434f-9d26-95daf4aaa7f0 | signoff | Request Beca Signoff
eb5fc531-f487-42ee-bb1f-4a792a8d9622 | checkpoint | Completion and Certification documents
0f402ce1-5e6e-4a32-a693-68619e7817b5 | checkpoint-no-value | FIRP Signoff
16d00f4a-072b-44c2-97e5-1174d91d77b4 | signoff | Record of Witnessing
1d458257-3aec-488f-9fe5-977b2466f346 | checklist | H01 - Eden Towns Main Low Pressure |  | H01 - Eden Towns Main Low Pressure
79b7650e-54c4-4dc4-89ca-dfd33cbc4216 | section | IST Test
edc79239-72bc-4599-a2e7-795aca5fd414 | checkpoint | IST Details
ef1d3f4a-ddc7-5dd5-a9d9-d38fb5c310a1 | textbox | Test Method - Simulate low Eden mains pressure by increasing pressure alarm setpoint
38efd23d-1b78-542c-b3ec-f0841b6c18f8 | textbox | Area - Huia Tunnel
159874e0-eb1e-4454-aa4d-79801024fae1 | section | First Test
54952380-5c99-40a1-b7e3-a45df92fbe10 | checkpoint | BMS - BMS Alarm
fc43e5cc-bd78-41de-ba9c-33be931ebd5f | checkpoint | Eden/Kyber Tank fill solenoid valves on all Non-potable and Potable storage tanks CLOSE
f6140af0-d5dc-45aa-b635-e74161ed8dd7 | section | Second Test
4972a24d-acca-4fcc-8761-0407ef7710b3 | checkpoint | BMS - BMS Alarm
dd92d5eb-d6a6-489a-9e00-221d9b7cc369 | checkpoint | Eden/Kyber Tank fill solenoid valves on all Non-potable and Potable storage tanks CLOSE
bb4c0232-4ff2-4bff-a755-b43a2265811f | checklist | H02 - Kyber Towns Main Low Pressure |  | H02 - Kyber Towns Main Low Pressure
7bdc2c65-5841-43bf-8467-eb8d554b3914 | section | IST Test
edae00dd-d45e-44b7-baab-e4163dfb4b2b | checkpoint | IST Details
62f5afa3-10bd-50c0-8bd6-d25f84211261 | textbox | Test Method - Simulate low Kyber mains pressure by increasing pressure alarm setpoint
bfa85652-e685-5ec9-8bd1-4dd25ae12f60 | textbox | Area - Huia Tunnel
53c54090-7a07-4539-9f3f-26aaf8abca19 | section | First Test
18318bb8-4a68-44c8-95a4-c4a608e9663c | checkpoint | BMS - BMS Alarm
537053fe-a545-4a6b-9a09-d18a4a31a778 | checkpoint | Eden/Kyber Tank fill solenoid valves on all Non-potable and Potable storage tanks CLOSE
2e30bb84-291b-4946-b67d-a6e47bdde675 | section | Second Test
dcef5692-2fd3-408d-814b-3ec3067b1c8f | checkpoint | BMS - BMS Alarm
2565db8b-dfaa-4d5b-b12e-a7695687971e | checkpoint | Eden/Kyber Tank fill solenoid valves on all Non-potable and Potable storage tanks CLOSE
c908365f-711a-47fb-8a0d-ba603982b3cd | checklist | H03 - NP Tank High Level/Full |  | H03 - NP Tank High Level/Full
99998138-03df-4347-b211-285683912c7f | section | IST Test
1c9135e0-5381-405f-846e-9bc17706a41b | checkpoint | IST Details
5d53afce-00c6-5d59-a760-1577c92ab9a4 | textbox | Test Method - Simulate overflow water level high through adjusting the hydrostatic sensor reading
c294f363-c261-5c94-bb87-0888f3777d8b | textbox | Area - A40
cad732d1-f0e6-469f-9c88-c7541eb4e50b | section | First Test
05b0f486-34cf-40cf-8178-5bdcb82ef4ce | checkpoint | BMS - Kyber/Eden tank solenoid valves closed
19f406f9-f818-41e7-851b-77067f208f9f | checkpoint | Bore Water solenoid valves closed
2343a08c-282c-434d-9386-7b44bc56ab92 | section | Second Test
e4b20874-1d95-423e-a1dd-66668ad5ed4d | checkpoint | BMS - Kyber/Eden tank solenoid valves closed
24a13da6-416e-4eaa-808d-ec32acb23150 | checkpoint | Bore Water solenoid valves closed
4c1fc05c-e2a8-4a1e-b1f3-b7fdf6565938 | checklist | H03 - NP Tank Low Level |  | H03 - NP Tank Low Level
62ddd1dd-a999-4324-8304-d720781d8e5a | section | IST Test
1495fcba-cdbd-4334-a661-2518d9afa0a5 | checkpoint | IST Details
bb4f658b-652e-5554-ab58-d408701cd824 | textbox | Test Method - Simulate tank low level through adjusting the hydrostatic sensor reading
d505342f-7ffc-5ea8-b8e1-0834f262246b | textbox | Area - A40
4e0db525-7361-44f6-a00b-62b6bcad6415 | section | First Test
594b4d18-d8e2-4131-a09c-3df2f70be9da | checkpoint | BMS - BMS Alarm
93cf6a2b-5c15-459c-a9ca-f091743cb614 | checkpoint | Lock out NP water booster pumps
fb5665a2-7f7f-4d3a-ad2b-9b9b078221ab | section | Second Test
ffc14608-96a4-49d7-ad17-55d82f1eb370 | checkpoint | BMS - BMS Alarm
97bdb902-776d-4d44-a639-139acb365d40 | checkpoint | Lock out NP water booster pumps
30971bca-5735-41b3-9ac0-1652ea1aad7c | checklist | H04 - Non Potable Tank Towns Main 1 fill trigger |  | H04 - Non Potable Tank Towns Main 1 fill trigger
4ff29c4c-0b1d-4e51-ab29-35d9178d79ec | section | IST Test
6e15a9dd-60a9-4773-8eea-1bb7f89f1263 | checkpoint | IST Details
36ab8fb4-9cda-5cd2-874a-2ff523a61449 | textbox | Test Method - Simulate mains 1 fill tank level through adjusting the hydrostatic sensor reading
8c57b2a8-1979-5175-8298-a9b9ea1f1500 | textbox | Area - A40
fc1f7191-6db5-4c28-8d54-844f10e4ed69 | section | First Test
aeaebcf1-0ae3-46b0-bb8a-03b0c90070d6 | checkpoint | BMS - BMS Alarm
4faaeeb5-42e1-4a40-87c4-ddebd56da29a | checkpoint | Kyber/Eden tank solenoid valve opens
63e2fc8d-bb45-407e-aff8-937525344a01 | section | Second Test
5797a3dd-948a-4a7f-9f2a-0bbe76b9e45d | checkpoint | BMS - BMS Alarm
b6c550fe-8e00-437a-8bc1-c3476a795487 | checkpoint | Kyber/Eden tank solenoid valve opens
1a3797ec-fae9-4807-b628-14b6d2eff610 | checklist | H04 - Non Potable Tank Towns Main 2 fill trigger |  | H04 - Non Potable Tank Towns Main 2 fill trigger
06866a7f-c811-4216-9519-672702b25891 | section | IST Test
2a8c9a5b-a57e-499d-86f3-7f4e23b45b51 | checkpoint | IST Details
9d89ff56-2c54-5968-ac5a-9d31301ef6aa | textbox | Test Method - Simulate mains 2 fill tank level through adjusting the hydrostatic sensor reading
2eb76aa8-9e78-5353-90cb-cbf9b93cd3d4 | textbox | Area - A40
5aa9a5b5-80d4-49bb-a4bb-8a3fe6a2b069 | section | First Test
3ee015e8-2e7d-41b8-9cc4-729b16e009cf | checkpoint | BMS - BMS Alarm
eea15abf-fd4a-4358-a54d-0f3bb13c411d | checkpoint | Grafton tank solenoid valve opens
f296f75d-9af7-4db5-9e03-3eb0bd1cec03 | section | Second Test
87526802-6f71-49a5-8951-9aa191b042ac | checkpoint | BMS - BMS Alarm
1141e23e-0b39-41b9-a024-7b1de05a89f9 | checkpoint | Grafton tank solenoid valve opens
fa88a4f0-e6b4-4a22-8293-7575d8bfa3c7 | checklist | H04 - NP Tank Overflow |  | H04 - NP Tank Overflow
c86e0e35-1a21-4a71-9125-7598ac5d0592 | section | IST Test
81b95e7c-3dc6-4b22-be1e-d49915059316 | checkpoint | IST Details
cc73ef63-b6a8-5f9e-abc5-85321c5f9fe2 | textbox | Test Method - Simulate overflow water level high through adjusting the hydrostatic sensor reading
776fdef3-b774-56d5-b6bf-9b4a9335e4f7 | textbox | Area - A40
2833f698-1d0f-4cc3-a753-c5d5d3394386 | section | First Test
2e8074a5-009c-4e7b-b98b-2cf284ac0cba | checkpoint | BMS - BMS Alarm
06d6dc1a-6c05-4ecb-822a-b6a6462897bc | checkpoint | Close fill valves to tanks that alarm
098c90e4-74f8-429f-87da-af56300e8343 | section | Second Test
7e2db102-3621-401e-8fda-f6db51da31bc | checkpoint | BMS - BMS Alarm
ca83b95f-f6bf-4ba2-b94a-1676fec7d353 | checkpoint | Close fill valves to tanks that alarm
a04cfe9a-9139-409a-9cf9-5f8a82327c7e | checklist | H05 - Bore Water Chlorine Dosing Unit Fault |  | H05 - Bore Water Chlorine Dosing Unit Fault
759e6552-56df-497a-b887-0551db1dc96d | section | IST Test
2d7042ae-b063-4123-88a2-b0176b08e6d6 | checkpoint | IST Details
184f9ffb-ec88-5080-8e96-25c854094a53 | textbox | Test Method - Simulate Fault at dosing controller
1ee18e9f-4ef8-599a-b94b-b50f817a0374 | textbox | Area - A40
7099281b-22e6-48b4-a740-171f65f96e74 | section | First Test
79adbbab-5622-484d-b242-dca2def43c6e | checkpoint | WTP - BMS Alarm
cf8ff20d-7f95-444b-b7d1-e5d0e38a64f3 | section | Second Test
f7af665a-f2a6-4b69-8655-01001252b809 | checkpoint | WTP - BMS Alarm
f0aad2bd-51f2-4f34-8b97-9935ba52e390 | checklist | H06 - Tank Isolated for Maintenance |  | H06 - Tank Isolated for Maintenance
a96cef15-086a-4b9f-a0ea-d546bb4cc931 | section | IST Test
192f6b9e-e26a-482c-81be-8a1797bd2adc | checkpoint | IST Details
c4e965b7-b301-5689-b62c-b0d579444a35 | textbox | Test Method - Lock out tank for maintenance via BMS
e964c6b5-b6b9-527c-ad4d-b480e0757253 | textbox | Area - A40
b326cebd-96b7-4bee-bd55-37603d6afe6e | section | First Test
4558e5a3-a732-441a-acbe-2dfbd6596db2 | checkpoint | BMS - BMS Alarm
2e0b316a-ad7d-405a-8aa5-dc272d992320 | checkpoint | BMS - Kyber/Eden tank solenoid valves closed
9cb3f548-ced2-4acc-b9e2-9cc9a06e105e | checkpoint | BMS - Bore Water solenoid valves closed
cbc36c14-4acd-47c3-88c6-47b50ab6b976 | section | Second Test
05416371-3981-4551-a0e0-0d638f8348fb | checkpoint | BMS - BMS Alarm
8e865291-122b-4be2-8505-913689ef7db9 | checkpoint | BMS - Kyber/Eden tank solenoid valves closed
2631a0e1-c054-4abe-8b72-d8d6f9aba173 | checkpoint | BMS - Bore Water solenoid valves closed
5468d723-fe45-44e3-a924-1d45d7905852 | checklist | H07 - Seismic Trigger |  | H07 - Seismic Trigger
38cff931-d147-4b5a-b5d4-b66e979cadb5 | section | IST Test
fda85271-f765-4880-b8b7-4c4435778b1d | checkpoint | IST Details
3af006ab-63ba-51ab-9e87-88c871503266 | textbox | Test Method - Trigger Seismic sensor
9131571b-c81c-500c-9648-1291c95a2c54 | textbox | Area - A40
a4011324-4d64-49f3-8e47-9bc734bb8bc0 | section | First Test
e7535ecb-ca22-4dcd-b9ed-5032ca82d73e | checkpoint | BMS - BMS Alarm
3e7d74d6-08a9-4f33-9da8-7b94235c44aa | section | Second Test
6e780553-7b66-421d-a966-e9ffdc69a8e7 | checkpoint | BMS - BMS Alarm
4ae25036-dadd-48c1-9ac4-8bb41aabf263 | checklist | H08 - Operational Tank Level Inbalance |  | H08 - Operational Tank Level Inbalance
2928f8b8-cf22-48d2-ac0c-f9c42ac4b026 | section | IST Test
9e9a9fef-8aa7-4d58-8a5f-f5f5bffe5bdb | checkpoint | IST Details
3b59b668-104a-5c42-9946-401b41b939ab | textbox | Test Method - Simulate imbalance via hydrostatic sensor inputs
c37b5fa7-fdc2-5468-9f65-e696caade0d6 | textbox | Area - A40
7c370794-b415-413b-8c15-5a2e34a1c3ee | section | First Test
97ff4840-87fb-4672-9317-6dc1e5f4083f | checkpoint | BMS - BMS Alarm
89b4affe-24c6-401c-82d1-0f7dd6c55fe4 | section | Second Test
0a60d201-e310-4c24-a6e7-5e1ebeccf917 | checkpoint | BMS - BMS Alarm
1f336fb1-1a0b-4b11-8d60-1353f9ced45c | checklist | H09 - Non-potable booster pump fault changeover |  | H09 - Non-potable booster pump fault changeover
a58ce2b2-3782-4d21-8050-e7b9c948db16 | section | IST Test
19906556-d6b3-48e1-8837-f841a53efdea | checkpoint | IST Details
b8194fd5-58f7-5fcb-bc5e-aeec13054e3f | textbox | Test Method - Fault each duty pump when operating by unplugging differential pressure sensor or via VSD fault contact
1fea91aa-afcd-5ace-825d-a32b9d9fae22 | textbox | Area - A40
5c177c9d-7828-4a34-bfe7-f9ed3ef8f371 | section | First Test
e79b57fb-9a37-400d-a778-11616d21f319 | checkpoint | BMS - Lag pump becomes duty pump
0f839ad1-6f27-4f32-b7b9-2b0271b4e0b4 | checkpoint | BMS Pump Fault Alarm
ead89e80-3d0d-4b91-9d17-e78deb9fb82e | section | Second Test
f6af4098-cffe-4413-8b2b-f8e9bc7a2cca | checkpoint | BMS - Lag pump becomes duty pump
526b687c-52c7-4d96-9c92-76b2f8a6fdd5 | checkpoint | BMS Pump Fault Alarm
91681afe-e4ef-44ee-9bce-0b79dad0e356 | checklist | H10 - WTP booster pump fault changeover |  | H10 - WTP booster pump fault changeover
0d08d9e2-eab7-439d-a3c2-2be0354f9ad9 | section | IST Test
eee0a4a4-be18-4db0-bc79-076448d062b0 | checkpoint | IST Details
77839fba-7478-5b88-a054-b079c8610740 | textbox | Test Method - Fault each duty pump when operating by unplugging differential pressure sensor or via VSD fault contact
be619c99-b19b-5749-9834-afe11676719b | textbox | Area - A40
504ef3c4-3065-4f05-9b31-e2fa9a0e077f | section | First Test
5db154ec-538f-480b-802e-583889cc08a1 | checkpoint | BMS - Lag pump becomes duty pump
35a65c7b-d8d1-491d-90bd-ae847b787008 | checkpoint | BMS Pump Fault Alarm
f921835e-7218-4c2d-9605-0da107ec466e | section | Second Test
2eea746e-e66f-422a-bb2a-c9395cdbe9e6 | checkpoint | BMS - Lag pump becomes duty pump
63f85d0e-d5bb-4a29-ac21-aa59813a0549 | checkpoint | BMS Pump Fault Alarm
355622a8-943e-4633-b15f-ef6574c26e01 | checklist | H11 - Potable water booster pump fault changeover |  | H11 - Potable water booster pump fault changeover
407f0955-6860-4138-a927-be0f5513d4ba | section | IST Test
9f2e6bed-3bbb-467e-873e-74ea33cfee5d | checkpoint | IST Details
3ee02039-7388-5ac7-882b-b239b517c2ee | textbox | Test Method - Fault each duty pump when operating by unplugging differential pressure sensor or via VSD fault contact
271708f7-52f3-5a44-a6ad-24766ca9a610 | textbox | Area - A40
78cfe855-ee36-42c3-b29e-980a1b0dd600 | section | First Test
610e53d2-d75d-4207-aa2c-79ac0bfd04a7 | checkpoint | BMS - Lag pump becomes duty pump
69fa4ea7-b325-4dc5-a4c9-6ebc635d1a44 | checkpoint | BMS Pump Fault Alarm
f0c4d5fd-4163-4d07-9ffd-8e78a506a500 | section | Second Test
a65034b2-e06f-4b57-9358-d83dcdbf0a1c | checkpoint | BMS - Lag pump becomes duty pump
bb11d21f-d194-4649-bb84-ab3b85c670e4 | checkpoint | BMS Pump Fault Alarm
724bbc45-3102-408c-80a8-de238847cf4a | checklist | H12 - Monitored valve tamper |  | H12 - Monitored valve tamper
9f13a022-b6f2-431c-8bd5-47e736b67c6d | section | IST Test
00afae94-2f92-4ca3-82fc-3fb57e480bb0 | checkpoint | IST Details
06caad1a-ec2b-5d44-beb6-829c01d5b6a4 | textbox | Test Method - Close each monitored valve individually
5b25d57d-7a93-53dc-b365-8cd78953f326 | textbox | Area - A40
ebd4d16f-44f5-4f6c-b3d3-0f834388764b | section | First Test
534ab4b3-9745-4a9b-9c7a-9d41820d41f2 | checkpoint | BMS - BMS Alarm
41e41e96-20d3-4e82-8ab1-742655dffec7 | checkpoint | BMS - Sprinkler DBA Fire Alarm
820cbd89-8a69-443a-9f80-678aad336c5b | section | Second Test
79d8c4c6-e29e-4051-a279-9f1279e80887 | checkpoint | BMS - BMS Alarm
b781159d-7903-4ca2-b95d-11a5b6a60bb0 | checkpoint | BMS - Sprinkler DBA Fire Alarm
e6fda1ce-5665-448a-b2b6-9d834743102b | checklist | H13 - Sump Pump Fault |  | H13 - Sump Pump Fault
dd2aeaa7-555b-4339-a709-6d1a9052e1a0 | section | IST Test
e2b69aa3-aab0-4945-bb86-f136c803476e | checkpoint | IST Details
5ed123ad-4dd2-5948-a5fa-10b0dd1d61d3 | textbox | Test Method - Simulate pump fault condition
43cb299f-4f8a-5edc-807d-bf00aec5cbed | textbox | Area - A40
96228aef-a1fd-4ee5-a55c-af5b06cdd140 | section | First Test
55919a8d-056b-48e3-a988-b60c07559265 | checkpoint | BMS - BMS Alarm
2a605209-891e-4370-aa5f-751d17e5cd93 | section | Second Test
608c1c72-3290-4325-a722-2a2c47f270e5 | checkpoint | BMS - BMS Alarm
d104343e-dfa6-4cf3-8ed1-cc69d4d51d1f | checklist | H14 - Sump Pump Fault |  | H14 - Sump Pump Fault
fe76a5d1-e74d-4d45-9cc0-d7785f03a916 | section | IST Test
f2e41f17-37b1-427c-bd5f-dc2adfb1a796 | checkpoint | IST Details
e9e0375f-7ccb-573f-8201-69022ec2c6db | textbox | Test Method - Simulate pump fault condition
8e2ed60a-7a50-5c90-8782-8ed3b82788f8 | textbox | Area - A40
3d908fd9-d3df-4798-8c1d-d9ef314db08f | section | First Test
9f0c2d9a-8e3b-4dee-8eb8-1bbcbdb44c3f | checkpoint | BMS - BMS Alarm
57d7506f-0a49-44ad-b4b7-6142364d266f | section | Second Test
900a6fca-75f1-458b-b6ef-cb14896b8736 | checkpoint | BMS - BMS Alarm
31b2c7fa-827a-4e49-ab4c-b928e187a1fb | checklist | H15 - Sump Pump Fault |  | H15 - Sump Pump Fault
9a45d107-f15f-4561-ab90-d29fc59cd71f | section | IST Test
06ff19fd-d1af-4c72-beb0-bfb6e2175cfb | checkpoint | IST Details
0b8b1d56-f059-5ace-9b90-ac885bc635e0 | textbox | Test Method - Simulate pump fault condition
f9887bb7-7a23-5a41-96d8-aeb4919f0a8a | textbox | Area - A40
cdd2254f-94de-4260-9736-8012c03e2c84 | section | First Test
1148d531-d544-4581-bbe0-a03ca6eeccd5 | checkpoint | BMS - BMS Alarm
c9b1e870-503e-4707-a271-b9b730f8d316 | section | Second Test
98c57bdf-ee9d-44af-9222-2dc07828a254 | checkpoint | BMS - BMS Alarm
2c51b056-cc31-418c-bee8-230885fc0286 | checklist | H16 - Sump Pump Fault |  | H16 - Sump Pump Fault
a6539d13-8b4b-46e6-8a88-689af480dd4b | section | IST Test
b2081912-daa4-4c5c-ae59-90e7ea544f85 | checkpoint | IST Details
9e037362-d16d-5ba6-a152-10715c029cdf | textbox | Test Method - Simulate pump fault condition
e1a8797c-9cdb-571a-bd8a-80c71eb532a6 | textbox | Area - A40
6af3d1b3-1611-468b-87b2-ebed4d9f3d24 | section | First Test
f02c0db6-c627-4d40-bfdd-e5b27715cb96 | checkpoint | BMS - BMS Alarm
c216864e-3c67-48ae-a2a9-8c092c9af351 | section | Second Test
7e81e0f6-631f-406f-9015-c54f76ead648 | checkpoint | BMS - BMS Alarm
6a494f3d-9aed-44f1-a5a5-ae900afab584 | checklist | H17 - Sump Pump Fault |  | H17 - Sump Pump Fault
b603d8e3-75dc-4cae-8f36-956ab74d5d5e | section | IST Test
b47d7b56-4ee8-49ab-92c9-261b88ef1123 | checkpoint | IST Details
694fdfda-04d8-5b1a-b898-169994ec3c8e | textbox | Test Method - Simulate pump fault condition
3270e87d-b9cb-52aa-8658-25182fe451b7 | textbox | Area - A40
b35c5fd7-1aa8-475d-83bc-0ac77b2bddf8 | section | First Test
bc4f44ab-1622-43c6-b172-ef4bd0aefb2d | checkpoint | BMS - BMS Alarm
095d623a-c0d8-460c-aab6-9f3a6ac0f09f | section | Second Test
559b2774-2da3-4b68-a2c7-01785bf306f0 | checkpoint | BMS - BMS Alarm
510a209f-1d5e-4216-8f91-598c5d558be7 | checklist | H18 - SSPS-005 continues to run and pump to sanitary sewer after SSPS-001 to 004 reach stop level. SSPS-005 stops once sump low level is reached. |  | H18 - SSPS-005 continues to run and pump to sanitary sewer after SSPS-001 to 004 reach stop level. SSPS-005 stops once sump low level is reached.
945cb284-31cb-4d49-a892-0b364816292c | section | IST Test
9b4fb09c-86f0-4ad5-bbf6-1ba6c035248b | checkpoint | IST Details
696076d6-4c1b-57ae-a5da-6c7ddf5d81c7 | textbox | Test Method - Allow SSPS-001 to 004 pump down sump level and stop.
8f64e10c-495f-5ab3-8e7a-5df787cf858f | textbox | Area - A40
ee97bc4e-50b0-4ab8-b0d8-36aae65ac29b | section | First Test
981755cc-1d6c-4b25-aba8-01d39b6cf918 | checkpoint | BMS - SSPS-55 5 runs untilk sump low level is reached.
f52bb662-f572-42bd-ab1c-d7adc1159c53 | section | Second Test
75a17d99-86a6-42cc-aa6d-6b294ae153d5 | checkpoint | BMS - SSPS-55 5 runs untilk sump low level is reached.
ba4e6914-680f-4f6c-bf16-7ab97eea7396 | checklist | H19 - Sump High Level Alarm |  | H19 - Sump High Level Alarm
c59684ea-68d6-48d7-905f-1f984608f279 | section | IST Test
e52a6751-d2a9-43d8-9323-caf5974fabd8 | checkpoint | IST Details
65530f83-8d3e-5c0c-a98c-8869d47af1e4 | textbox | Test Method - Raise High level alarm float
c0c5b738-be6e-5249-91cf-3c39cdce4184 | textbox | Area - A40
ffe66cab-a07d-4b17-9e48-b4b76a5e220d | section | First Test
87766e70-cc68-4e12-9a2b-fcec83d600b1 | checkpoint | BMS - BMS Alarm
42a15179-8e97-4aec-8bc5-5edcdd00db25 | section | Second Test
07d70102-d2cd-49c5-956e-2039bf9b384a | checkpoint | BMS - BMS Alarm
b0a21c42-ddd4-4330-b799-6eac98a90629 | checklist | H20 - Sump Pump Hydrocarbon Sensor |  | H20 - Sump Pump Hydrocarbon Sensor
1f2e2e8d-e64a-4be8-ac7d-082cabeb425d | section | IST Test
5d7a068f-aa97-4111-a7ac-ab120f97b03c | checkpoint | IST Details
5027a021-525d-59aa-8d13-015c1420e403 | textbox | Test Method - Trigger hydrocarbon sensor
009de892-d4ad-50d2-957b-8c9ddfea61aa | textbox | Area - A40
53cb59ac-3942-459e-b029-de33304ab39f | section | First Test
d12c746e-6ff1-408f-a494-2e132558c1b6 | checkpoint | BMS - BMS Alarm
e19131e6-dc80-41f4-82d7-ce966baf8ace | checkpoint | Lock Out Sump Pumps unless HL alarm triggered
092f372f-e23c-44b2-a0a7-7eade7f642b0 | section | Second Test
54cbefca-3ee9-4b1c-a847-64f80bc47090 | checkpoint | BMS - BMS Alarm
fe5ed8cf-21eb-47cb-8f7c-dce587c57ed9 | checkpoint | Lock Out Sump Pumps unless HL alarm triggered
a570edee-e1ca-4650-b8d7-df97108e692e | checklist | H21 - Valve Position Feedback Contradicts signal |  | H21 - Valve Position Feedback Contradicts signal
422fbb77-11ff-41c7-a993-6b08c9cbf3aa | section | IST Test
3682d41c-769c-4b91-b48a-3f57cbe0c7a1 | checkpoint | IST Details
dd71cfb8-0d44-55b8-b376-7e2dd2534515 | textbox | Test Method - Remove power to valve. Command valve to open or closed position
6930051c-d99a-5504-962f-d4df5eaa557b | textbox | Area - A40
cc5dcb52-2c6a-4032-aef6-e930d41959c2 | section | First Test
94dbeaf6-f0ba-4c7a-8e75-71e2f2072b38 | checkpoint | BMS - BMS Alarm
ff3daf57-4bd8-47af-89e2-9501eb51f80c | section | Second Test
03d9c526-0661-4f6b-b25b-d830c0b2ec6b | checkpoint | BMS - BMS Alarm
e44695d0-6207-45c7-8be0-2f4d895155f2 | checklist | H22 - Draw Down Exceed Makeup for 30 mins any tank |  | H22 - Draw Down Exceed Makeup for 30 mins any tank
95058f86-1333-4bbc-8838-42419e556cfb | section | IST Test
26c1478b-fdd5-49cc-be11-208977b42add | checkpoint | IST Details
7eaad8d5-dea5-5c1e-8214-47f2b89374ec | textbox | Test Method - Potters to simulate via BMS
75c25188-4966-5d91-a1e3-115363322e9e | textbox | Area - A40
6082c148-515a-4c73-a6ab-99e424f3c925 | section | First Test
6cb60cbe-1673-4267-a8d5-c1875cdd0c00 | checkpoint | BMS - BMS Alert
d1a5a12c-436b-4395-9085-4786d5eb9895 | section | Second Test
59d042e0-fb8a-4a40-b28e-961d2d074626 | checkpoint | BMS - BMS Alert
d5a39d9b-825b-4763-a697-99cce2411478 | checklist | H23 - Bore Pump Locked Out |  | H23 - Bore Pump Locked Out
372b5abc-13e1-4657-9064-28be44fe6041 | section | IST Test
97296b9c-546c-450d-acd7-dce8f0f953f0 | checkpoint | IST Details
ee262eee-3379-51e6-a000-22af9aa80b09 | textbox | Test Method - Lock out bore pump
91f18302-b157-5e7e-91a5-d193f10f0246 | textbox | Area - A40
c39f00aa-bdf5-4d46-a590-3fd518c50b7d | section | First Test
440857e3-a3a2-4edf-8c1f-b15d06461afe | checkpoint | BMS - BMS Alarm
03a362d3-18c5-444a-b96d-1fea5d1cb4d3 | checkpoint | BMS - BMS Alert
a5bcf55d-c080-458b-a149-8bf473d000c4 | checkpoint | BMS - Stop Water Treatment Plant / Raw Water Feed
afaa69bb-2cef-4d7c-969d-04230c9386e5 | checkpoint | BMS - Change Primary Water Makeup to Tanks to Towns Mains
0f8c5643-3830-49e2-a808-67408d38f92d | section | Second Test
d8ba8400-168c-416c-a2cb-69138854440d | checkpoint | BMS - BMS Alarm
fecb8011-cabe-4dfe-8960-a77debdd6bfd | checkpoint | BMS - BMS Alert
f19dfe50-c671-4615-a554-40d37b3b8e9b | checkpoint | BMS - Stop Water Treatment Plant / Raw Water Feed
e506439f-a9ad-4831-9a0d-62ce2351d01f | checkpoint | BMS - Change Primary Water Makeup to Tanks to Towns Mains
25ed9f6c-3e6b-4ea2-9100-c7504c86bfbb | checklist | HMI SCADA |  | Equipment -
7b2a4736-60b4-4998-9c4f-222478abf436 | section | Factory Acceptance Testing
02c7aee9-075c-4d07-9ff9-a61c07dd683a | checkpoint | Factory Acceptance Test Report
3b9454e3-b1dd-4014-8a80-b041b9f1168e | section | Pre-Commissioning
8a67c432-11d3-4550-808d-022d9d41b341 | checkpoint | HMI SCADA Point to Point Testing Report
99754473-66aa-4c25-a722-e3035644f11a | section | Commissioning
a4323971-8ed8-45de-8453-c0ed62526a05 | checkpoint | HMI SCADA Commissioning report
71572997-9486-45af-a48d-5beea770da90 | checkpoint-no-value | Mcconnell Dowell
08ffb6c9-6ed3-4bdf-88d7-f964b7f4b09a | signoff | Request McConnell Dowell Signoff
afbeee35-c7fd-43b0-bb0b-e5d65f3ef87c | checkpoint-no-value | Beca
5fbdb281-c2bd-4d53-abc8-25132c75f151 | signoff | Request Beca Signoff
d743a1e4-13cc-4189-80dc-88eee083bd86 | checkpoint-no-value | FIRP Signoff
579b87fa-2f53-4673-8134-c74f74714b8b | signoff | Record of Witnessing
916464ee-dd23-4eb0-8887-1bfc8c32d234 | checklist | Hot Water Cylinder |  | Equipment -
6346c42d-fe18-4d3c-964c-ca2ac1049e18 | section | Pre-Commissioning
8ee89ae5-0a84-4f99-a0cf-83af3cf419d7 | checkpoint | Seismic Restraints installed securely including timber chocks
22883018-fd52-4be1-bf78-bd318c1730de | checkpoint | Water on- no leaks
232e271b-dcda-46f4-9f5f-8112d00ba078 | checkpoint | Cold Expansion valve operation checked
2859f146-ba26-4f7a-8dd6-f0772ffda461 | checkpoint | TPR valve operation checked
bc96b11b-eff0-414f-97be-fbf10c311363 | checkpoint | Waste connection watertight
dde74951-1d99-451b-8892-9ac3be477b91 | checkpoint | Pipework securely fixed
03948530-1b1c-4a5f-9e43-9bf99ffb526f | checkpoint | Lagging to hot pipework
c166f4e4-8fc4-4c54-8530-3e14968fbc19 | checkpoint | Wiring complete (by electrician)
71db1ca5-0b43-4453-a97f-55c3c5b8271d | checkpoint | Tempering valve set correctly – water temperature checked
7568ea17-2cba-406f-84f1-c76aea907ffa | checkpoint | Isolation valve solenoid interlinked with underbench sanitary drainage pump (if applicable)
8ea7ce24-9794-4ece-905d-3f74a969ea5e | checkpoint | Separate un-tempered line to kitchenette (if applicable)
72d37d62-a20d-49c4-8186-31199fb8954a | checkpoint-no-value | Mcconnell Dowell
ca92ef81-6802-4c88-9d28-a59f69f5097c | signoff | Request McConnell Dowell Signoff
aad59a2d-8cd2-4d17-addc-5a2d0726ac33 | section | Commissioning
8b4f6030-9d24-47bc-807f-c6e8987c5859 | checkpoint | Commissioning and tempering check report
782755c2-de85-4f7c-879a-b8c2fdc4d644 | checkpoint-no-value | Mcconnell Dowell
fe595161-97b6-4fa5-b86f-1c2e8e1961c5 | signoff | Request McConnell Dowell Signoff
6c15841a-fb3e-4063-96c8-a085bca8cbf0 | checkpoint-no-value | Beca
a7fba4b4-6902-4385-a395-962e42dea26c | signoff | Request Beca Signoff
26cad0f5-a4c9-47ce-92f4-25f08f85c4e9 | checkpoint-no-value | FIRP Signoff
d0ba198a-22ce-4bbb-a2a0-f41444a6ac08 | signoff | Record of Witnessing
d8dd53b6-f62a-4ad4-9644-6eb34b4f7c86 | checklist | HV Switchboard |  | Equipment -
161cdd00-3258-4706-803a-c6657373fe61 | section | Factory Acceptance Testing
27e6088d-ddbb-4488-81f6-5e207b5fe46b | checkpoint | Factory Acceptance Test Report
a17ec376-9f4d-4ffe-9b77-88ba320e0e56 | section | Pre-Commissioning
239cd263-3e05-4468-8e10-7ce7e8eeffa9 | checkpoint | Pre-Commissioning Test Report
53102b26-4d9c-416f-8c48-b2514227788a | checkpoint-no-value | Mcconnell Dowell
166130a8-6825-44a9-98cc-6130805634a0 | signoff | Request McConnell Dowell Signoff
12900f56-5ef8-47e7-9ab8-457444c75976 | checkpoint-no-value | Beca
9d00d2cb-5cc2-4fa9-821c-0b38ac715a90 | signoff | Request Beca Signoff
db3f0ff8-32ca-4ec0-8c8e-d77bd34b9445 | checkpoint-no-value | FIRP Signoff
3bd57108-13f6-4180-bd9a-67f431b73c61 | signoff | Record of Witnessing
86566d85-a63d-4833-a184-967c683453d3 | section | Commissioning
16880908-8ad8-4ecb-8bde-7aa164fe980b | checkpoint | HV Switchboard Commissioning report
4c80bc7e-e901-417d-8eda-3fbb7daf28ae | checkpoint-no-value | Mcconnell Dowell
b35fe660-279c-4fc5-95b4-c1577a9bd282 | signoff | Request McConnell Dowell Signoff
ae80da7f-6059-4376-9cf0-6a08bffadb91 | checkpoint-no-value | Beca
6835db1d-1988-4772-9962-b3191e8655fc | signoff | Request Beca Signoff
be239ab3-d154-40c0-b5d5-43a5ba89511f | checkpoint | Completion and Certification documents
5ba5131f-a947-4346-8534-d5648d66c2b5 | checkpoint-no-value | FIRP Signoff
2f793958-9c58-4c0d-a611-4fd7781c847b | signoff | Record of Witnessing
c55906ee-3822-4225-94b2-8ebcc077c85b | checklist | Hydrant Pipework |  | Equipment -
337a3f41-a6ab-41cb-aa85-929ea3f0e889 | section | Pre-Commissioning
cc6b06ff-fd07-4c0e-aa81-204d4691e78d | checkpoint | Building Hydrostatic test form
fd794cbf-3a99-4f97-a043-4d9709936f98 | checkpoint | Monitor valve Pre-Commissioning Check
85b3a006-5694-427c-94a6-67559c777214 | section | Commissioning
8669a57c-07a6-4943-a9ce-15412760ece6 | checkpoint | Installation of all hydrant pipework
0e512df3-1aa1-4da0-83e6-2959fe6c43b6 | checkpoint | Pre commissioning check of monitor valves
0d986171-280c-4e91-8a7e-f5e29482af8e | checkpoint | Complete commissioning sheets prior to Nova Flow/AON Inspection.
cacf6438-eb57-46fc-9cf9-44683699faff | checkpoint | Building Hydrant Hydrostatic Test Form
b84fda93-6a32-480e-a6bc-307f895ade0c | checkpoint | The system has been installed by an approved contractor.
2d32aac1-8f5d-4c45-bcbb-d98f3a597d95 | checkpoint | There exists a testing and maintenance contract with an approved contractor.
36019eaa-08ad-4c03-b3c8-0dfcec2174d1 | checkpoint | There is at least one outlet per floor including the roof and mezzanine.
44cc2402-33aa-4468-b90e-2d766c493b3b | checkpoint | The main waterway has a diameter of 100mm or greater.
69f9443e-5e56-40a4-b398-dc9837893d36 | checkpoint | Single pump systems do not supply more than 15% of pressure required.
fe5242ea-2282-4e07-99e7-1c1aac69044b | checkpoint | System is kept charged with a positive pressure of 15kpa or greater.
3bc868e4-f6e2-49a1-bfc4-c8dd866119a1 | checkpoint | Every point on floor is within 50 m arc of at least one outlet
da69938a-bff4-4515-8da5-fc46ad355eff | checkpoint | Charging line is not less than 25mm in diameter.
9ff8aa10-2ca7-4882-8287-66b3f37da7b3 | checkpoint | The charging line is controlled by a locked open quarter turn valve.
0d0c0b55-7bb4-44f1-a82e-75907525e8ab | checkpoint | Inlet axis height is between 600mm and 1350mm above the ground?
e8ec6314-c0ec-4bfd-b2ca-edbdd9c04d09 | checkpoint | Clear space around inlet is 1200mm front, 300 mm each side, 2000mm high.
1696b5fd-5589-473e-9b1b-11977e657ecb | checkpoint | Clear space around FSI valve handle is 150mm min.
a7f5fd8d-0d81-422e-8549-0b833b7c58fb | checkpoint | FSI is within 18 meters and in clear view of suitable fire appliance parking.
162b3808-c8a5-4e37-960a-32dc3ca5b96b | checkpoint | There is adequate space around the FSI to allow efficient use by the fire service.
bcd1801c-e848-4e9b-a4bb-463fdb5605a4 | checkpoint | Drain valve is operable and piped to waste?
6e9f97be-8b50-431a-97b3-4d8173d53a0e | checkpoint | Inlet assembly has the correct number of 70mm male inlet couplings.
e2be2409-cc2e-4b80-9144-36da9c73a124 | checkpoint | Pressure gauge in the FSI is marked with minimum Standing pressure (wet riser and charged riser) Gauge is calibrated in Kpa.
4c8b6914-6f65-485b-a302-cde0f03d91e2 | checkpoint | Remote pump start buttons present in the FSI (wet riser and charged riser)?
e9c97d02-eb32-4f3b-b150-4253531bfbc1 | checkpoint | Pump running indicators in the FSI red bezel?
628a19f5-293b-499c-97d1-1f1debae17c8 | checkpoint | Accurate, legible system details/diagram in the FSI?
13bf2035-1a67-492d-b1b6-9b14a2e0a2ad | checkpoint | FSI assembly is housed in a waterproof enclosure?
3f52014f-ebab-4c0a-86d7-450556886283 | checkpoint | FSI protected from falling glass.
2e32ca3e-fc29-471d-8571-1331f4c70ba9 | checkpoint | Clearance around handle is - 150mm in all directions.
10d8b315-6df0-41b6-845a-d6ec102f54ed | checkpoint | Couplings are 70mm female instantaneous (not 65mm).
4e68efa9-59b9-4940-9360-07c26e9aa8b4 | checkpoint | Outlets are between -600mm and 1350mm from the floor.
4626b270-83d4-469a-aa05-787ca7b9b5ba | checkpoint | Clear space in front of outlet is 1200mm and 1200mm high.
de45a14e-7794-491d-8cdd-2bb6a5d47e8a | checkpoint | Outlets are located to allow ready and efficient use by the fire service.
6d844069-6225-40b8-a612-570ae2dfe3e0 | checkpoint | Outlet enclosures have a fire rating of 60/60/60.
19aedd0a-1db9-4ade-b65f-5fed381e487c | checkpoint | Each outlet assembly incorporated 2*70mm double lugged female hose couplings.
c89b2f7c-7e60-4307-b0ed-8f66d312343e | checkpoint | Each Coupling is controlled by a lever operated ball valve.
73fa6cc4-4769-4fc1-9b04-60776bb7d58a | checkpoint | Couplings are positioned on the horizontal axis or with lugs at 90 degrees to a line drawn between the axis of each coupling.
b212b412-594b-43aa-8c96-36a810cffe6e | checkpoint | All signage is safety red and white with red the predominant colour.
9901c41d-9c53-40f0-a75d-2b49f2237451 | checkpoint | FSI is clearly identifiable.
c2bec8df-1af7-430a-83e0-276faa18a056 | checkpoint | Pipe associated with the hydrant system is clearly identified.
469881a0-0f6d-494a-8f1c-eb699b326cc3 | checkpoint | Pressure gauges are clearly labelled as to their function and normal position.
195bb96b-9a6c-4cee-975e-d99213a934d8 | checkpoint | All doors along route to pump room are clearly marked.
95551245-7815-4a95-be5f-7797c23d066f | checkpoint | All valves are clearly labelled indicating their normal position.
72ac8950-804e-4d86-8a7f-62541c6f87e8 | checkpoint | All outlet enclosures are clearly identified.
2be6f02a-d1e4-422c-823b-ba42fae5f11e | checkpoint | Hydrant Commissioning report
620a08d3-74cb-49e5-8e6c-cbf50d8a17aa | checkpoint-no-value | Mcconnell Dowell
156c00b2-6079-4d51-8fd5-dc13159b5a06 | signoff | Request McConnell Dowell Signoff
94958a13-b370-4e77-8eb3-323a7dcb4572 | checkpoint-no-value | Beca
79cad407-017a-4e1e-b560-dd6062a4b254 | signoff | Request Beca Signoff
4d08cc79-c232-449f-8458-c4ac55c9ffd1 | checkpoint | Completion and Certification documents
a1e22737-29bb-437c-ad5c-e69d269b8557 | checkpoint-no-value | FIRP Signoff
d0af3493-b450-42c4-b4a3-5ec8462dac1c | signoff | Record of Witnessing
a4c40fd8-6f1b-4c49-96a1-e07dde792e48 | checklist | Lighting |  | Equipment -
126ba638-9485-43f6-a65b-d39829e2e69b | section | Commissioning
ed8a60d7-12b4-4447-b38a-2b0f36d7029d | checkpoint | Lighting Control Check Sheet
38a5249d-e1fe-40fd-bd17-7b5545940343 | signoff | Request McConnell Dowell Signoff
faee1ba8-7bc3-41fa-b942-97e839b59a0f | checkpoint-no-value | Beca
f499ea9e-bf31-421f-bb16-6eb02cc4165b | signoff | Request Beca Signoff
5dd07584-204a-40ad-8067-d48114887598 | checkpoint-no-value | FIRP Signoff
fdb81371-5462-4f1d-8a7a-fcf34d8166d4 | signoff | Record of Witnessing
b3c3a548-5588-485b-b4c8-16e05ced1414 | checklist | Main Switchboard & Mechanical Main Switchboard |  | Main Switchboard & Mechanical Main Switchboard
a8573770-387e-438a-87cf-2bb957d8304a | section | Factory Acceptance Testing
b6140347-7f12-43ba-9efb-29de799f01ac | checkpoint | Factory Acceptance Test Report
6387ef4c-0211-44cb-8609-0e56bec7ef22 | section | Pre-Commissioning
1bb9638d-9221-4270-8ca7-60b77ab26e96 | checkpoint | Main Earthing Check Sheet - QA form required
41758812-29eb-4bac-b1b8-720ead8d7591 | checkpoint | Earthing Bonding Test Sheet - QA form required
6aade267-9fb8-4695-9bd2-664fb57d1043 | checkpoint | Mains Cabling - Visual Check
011a44c9-71b0-43d9-bb1c-5b62d0b47a95 | checkpoint | Mains Cabling - Continuity
75d64816-45d2-5f03-97bf-c5e3387fa589 | textbox | Continuity:
1b516f4b-3b5d-4cff-9044-fb42233ac0c2 | checkpoint | Mains Cabling - Insulation Resistance
4a306109-b0e1-5f0a-8be9-31ef99b40fdd | textbox | Insulation Resistance
9d6bfde4-6c54-4805-b395-bc62d28cc06e | checkpoint | Mains Cabling - Check Terminations
57fb3145-6c0a-482b-9f73-8912d09bada9 | checkpoint | Mains Cabling - Power On
71d1b58c-b37a-4733-bf9d-f1a165a94560 | checkpoint | Mains Cabling - Test Voltage
f4e77327-dc66-5e44-b030-c9ebf29e1ea7 | textbox | Test Voltage
a2450daa-003c-46ee-b0bf-ceb5ebee5625 | checkpoint | Mains Cabling - Confirm Polarity
89dc471d-a9c0-430c-abc3-c669bdaf54ce | checkpoint | Mains Cabling - Confirm Phase Rotation
98601251-ea57-4067-af75-6dbaf283e7dd | checkpoint | Mains Cabling - Confirm Circuit Ready to be put into service
1514a63a-0cbd-4b70-b0d2-626ff569add1 | checkpoint | Main Switchboard Pre-Livening - Confirm MSB room / position meets regulations and is finished ready to house a live switchboard including weather tightness.
745603d8-39a0-43ab-a81f-06305f4ea0b1 | checkpoint | Main Switchboard Pre-Livening - Confirm MSB is securely fastened
3ee63c6a-eb67-4ca8-9267-5030993a3b12 | checkpoint | Main Switchboard Pre-Livening - Confirm supplier has completed all Site Testing once shipping breaks connected, attach results if available
f3bf87c9-d822-4d3b-b20c-a4aef5d623f6 | checkpoint | Main Switchboard Pre-Livening - Confirm there is a removable link between the earth & neutral bars
a0a48fa6-e596-4b7b-8753-fc47f6479b31 | checkpoint | Main Switchboard Pre-Livening - Check that the MSB has an identification label matching the single line diagram
c319ea34-12d3-4596-84ea-8d21ee2e6d3e | checkpoint | Main Switchboard Pre-Livening - Confirm Main earth is labelled
f6d368ec-81df-407b-a086-36043c0a93e8 | checkpoint | Main Switchboard Pre-Livening - Check that there is an earth bond to the case of the switchboard
50a43b10-34e8-434e-83f2-38eeeb047473 | checkpoint | Main Switchboard Pre-Livening - Check that metal work is undamaged and free of corrosion
0e797882-58c5-4771-83a4-e9a16d951e9a | checkpoint | Main Switchboard Pre-Livening - Check that MCB/isolator ratings match the switchboard schedules / SLD particularly if the device has an adjustable setting.
fc8d521e-b532-4c94-b5b9-14a676bcabec | checkpoint | Main Switchboard Pre-Livening - Check that all circuit terminations have phase identification
15cafb12-dad3-4657-a97f-3b80d7895d34 | checkpoint | Main Switchboard Pre-Livening - Check that circuit schedules have been fitted
b453f4fc-6266-42d1-be69-b0a6d01e53eb | checkpoint | Main Switchboard Pre-Livening - Check that all out going Circuit Breakers are "locked off" or tagged prior to energising submains.
ffba58db-36a1-488a-9b3d-7379dd21a677 | checkpoint | Main Switchboard Pre-Livening - Connections all tight including MCBs note torque settings
1ca902dc-6be4-480d-a3ec-c9127cbafadf | checkpoint | Main Switchboard Pre-Livening - Test Insulation resistance between bus and earth is greater than 50 MΩ and record results.
8ffc3d55-5c69-5085-9bf7-abb94e06755d | textbox | Insulation Resistance
3fb938b5-d393-4271-b9e3-b31fe5e1aadf | checkpoint | Main Switchboard Pre-Livening - Confirm Switchboard ready for inspection by Independent Inspector
5ac48e02-d88a-4833-b38e-e5cc5573e489 | checkpoint | Main Switchboard Pre-Livening - Once Inspection Complete Confirm Switchboard is ready to be livened
53728eef-d0e7-4979-8978-54e720a090e3 | checkpoint | Main Switchboard Pre-Livening - List any incomplete or defect items requiring remedial work.
e750cc32-9def-4c3b-9889-d40defc8f5da | checkpoint-no-value | Mcconnell Dowell
8f9eb89b-948a-4350-8df9-9915120e5bb1 | signoff | Request McConnell Dowell Signoff
7e0e8a92-6441-4817-9839-bdacf25fe4cd | section | Commissioning
e1357618-54d6-4900-aa6f-278b0e4c3ee1 | checkpoint | Main Switchboard Post-Livening - Confirm Correct Voltage present - R-W
9c671752-0e48-4433-ac35-c542d874b0f3 | checkpoint | Main Switchboard Post-Livening - Confirm Correct Voltage present - R-B
7eca8528-b727-48a8-aa54-30037d6367f0 | checkpoint | Main Switchboard Post-Livening - Confirm Correct Voltage present - W-B
9c41f924-a002-465b-9ddb-721aaef706db | checkpoint | Main Switchboard Post-Livening - Confirm Correct Voltage present - R-E
82bb5492-2b00-4c41-8d34-72cbe1c9f391 | checkpoint | Main Switchboard Post-Livening - Confirm Correct Voltage present - W-E
8195e4f9-1644-4a72-808d-a07439e00877 | checkpoint | Main Switchboard Post-Livening - Confirm Correct Voltage present - R-N
2b095e20-b0de-4f0f-adc3-265802bf89c6 | checkpoint | Main Switchboard Post-Livening - Confirm Correct Voltage present - W-N
69c7eff7-2494-4ed8-a5c5-de4e127e4133 | checkpoint | Main Switchboard Post-Livening - Confirm Correct Voltage present - B-N
f7f844b7-8431-427e-b94a-4983518847ad | checkpoint | Main Switchboard Post-Livening - Confirm Correct Voltage present - B-E
56beba3e-1262-46fc-9199-c7325bf819e8 | checkpoint | Main Switchboard Post-Livening - Confirm Correct Voltage present - N-E
1a20cc12-81ac-4ebc-954e-677285d63172 | checkpoint | Main Switchboard Post-Livening - Confirm Polarity and Phase Rotation - R
10c5d963-a10a-4d26-bc4b-4edc749e4940 | checkpoint | Main Switchboard Post-Livening - Confirm Polarity and Phase Rotation - W
34001598-6dee-42c7-9e69-b8e1befbfe0f | checkpoint | Main Switchboard Post-Livening - Confirm Polarity and Phase Rotation - B
27de7f92-2997-4d49-be95-e8ccc4dbbdbd | checkpoint | Main Switchboard Post-Livening - Confirm Polarity and Phase Rotation - N
66bc9fa4-0046-462c-9515-d745d49a0e89 | checkpoint | Main Switchboard Post-Livening - Confirm correct control voltage is present
0196daff-38d0-5fe7-a266-5f24e3464964 | textbox | Voltage
81517d1c-8f86-475a-920b-4b04ec6ff378 | checkpoint | Main Switchboard Post-Livening - Confirm all meters / monitoring devices are set up with correct parameters
a19fe9a6-813f-41c7-9710-2337abf2509e | checkpoint | Main Switchboard Post-Livening - Confirm Phase Failure Relay set up correctly (If applicable) Time, Voltage Lag etc.
c4f24e45-bb70-4020-b2b9-1ebc753afb83 | checkpoint | Main Switchboard Post-Livening - Confirm all switching devices (ACB's, MCCB's, MCB's etc) are switching correctly
25cfbc91-3bef-4882-9dea-cf58fb5fe22e | checkpoint | Main Switchboard Post-Livening - Confirm all Auxillaries Switching correctly
013163a0-d275-40cc-bf15-fa141a9bd142 | checkpoint | Main Switchboard Post-Livening - Confirm all point to point tests on controls cabling to external sources complete Incling PCMS interfaces
8d79b002-00f1-424b-b05a-39ac54b58fd0 | checkpoint | Main Switchboard Post-Livening - Confirm all adjustable circuit breaker settings are recorded on switchboard commissioning sheet
d4afe415-5cf2-4459-98ee-f658aa188ce6 | checkpoint | Main Switchboard Post-Livening - Confirm Castell key switching sequence if applicable
706e9673-a4aa-49eb-bf8c-dc898a77b8fc | checkpoint | Main Switchboard Post-Livening - Confirm Switchboard ready to be put into service.
da331163-f94d-41ee-91d2-265dc48b275c | checkpoint | Supplier Site Acceptance Document
22488e86-f4d2-40a6-9a96-11e1465046d4 | checkpoint-no-value | Mcconnell Dowell
0996ce1b-1a01-452d-b152-cb0da1bac00e | signoff | Request McConnell Dowell Signoff
0d2e0e7b-dbf4-4f62-a324-fa2e0effa470 | checkpoint-no-value | Beca
54d07504-44fa-43f6-a3fb-7206994299a2 | signoff | Request Beca Signoff
5128d258-ff04-4a9f-b669-f02b2fde8589 | checkpoint | Completion and Certification documents
97194336-5cae-44c5-945a-d93bd1d6d39e | checkpoint-no-value | FIRP Signoff
20a3390d-6b9c-4b95-97de-bb5b24de6058 | signoff | Record of Witnessing
775293df-5abb-4e6a-b9b0-b6d70bf7ad44 | checklist | MCC |  | Equipment -
7016aa8b-c9e2-4ad5-81c8-cc14cf6b341c | section | Factory Acceptance Testing
ad589292-4e70-4d9f-a0bb-245274a8290f | checkpoint | Factory Acceptance Test Report
f1bb555b-8bd3-49cb-88c5-182fc3092b31 | section | Pre-Commissioning
8af08f75-68ea-424d-a1df-d1eed6e1f9cb | checkpoint | MCC Check Sheet
18190098-d96c-406f-b790-e6bda989d773 | checkpoint-no-value | Mcconnell Dowell
0104dd52-13ed-40dc-ae58-883dd28f0b3e | signoff | Request McConnell Dowell Signoff
d04dff62-cf13-407f-881a-13809aaaf0e7 | section | Commissioning
d3edc723-22bd-4b23-ad5a-88bf9c379cb0 | checkpoint | MCC SAT check sheet
d3d27ca2-fcc6-4bee-95a6-f147bfeda98f | checkpoint-no-value | Mcconnell Dowell
27e0957e-d099-4229-9731-2a9eab56a6f4 | signoff | Request McConnell Dowell Signoff
cd9113b9-1c8b-457a-823a-835f7f00ef67 | checkpoint-no-value | Beca
5058641b-3870-43c0-9524-06086ae30b3d | signoff | Request Beca Signoff
4db50d5b-962f-4b15-8caf-bad871942e00 | checkpoint | Completion and Certification documents
24bc8976-fa5f-4a7a-8705-aaea4fcb12eb | checkpoint-no-value | FIRP Signoff
29aa380c-0237-459e-9d0b-e2ba05d2ad13 | signoff | Record of Witnessing
f44d4dee-9db5-484e-b8a9-72a8abfee9f7 | checklist | Medical Gas |  | Equipment -
1c5b7840-fa4a-4839-808c-157523174062 | section | Pre-Commissioning
4d27f0f1-7fc3-4a99-9639-1e5c1a140fc5 | checkpoint | Pipework Check (Medical Gas) First and Second Fix
cb04c4bb-a966-42a2-a4c9-c1969f66466e | checkpoint | Pressure Test
23091a55-7c12-4326-97be-678907803d88 | checkpoint | B1 – Pipeline Carcass Test Sheet
420cbd88-2a73-42bd-868c-52a332bb8ecc | checkpoint | B2 Contractors Cross Connection Test Sheet
7f0600fd-02c4-4a8c-b0b1-6e3f18e1068c | checkpoint | B3/4 Pipeline System 2 nd Fix Leakage Test Sheet
91ba1bd2-fc89-4a8e-bedd-e759c65c963a | checkpoint | B5B – Line Valve Assembly & Leakage Test Sheet
996b4ecc-ab0c-4275-90e8-64d550c32e2e | checkpoint | B6 – Commissioning Cross Connection Test Sheet
3f1b31e5-0dd1-45a6-a5e7-794e7bc39e71 | checkpoint | B7B – Function Test of NIST Connections Test Sheet
9bcd3509-3caf-4ca0-949a-195d780390cb | checkpoint | B8 – Design Flow Performance Test Sheet Test Sheet
e774cef1-8b0f-4313-8a5b-1e474e91d511 | checkpoint | B9 – Sources of Supply (Duplex Pressure Reducing Panel) Test Sheet
4d5369ac-daf0-4012-b168-637b33bec211 | checkpoint | B10 – Safety Valves Test Sheet
62c2a098-5f43-41e9-9248-d5d581285efb | checkpoint | B11B – Warning Systems – Plant Test Sheet
16fbfc0a-a5ed-4bc5-8c4e-dc1744263952 | checkpoint | B12 Verification of Drawings Test Sheet
1facd61c-d72f-4707-b55b-4b8e62b1b268 | checkpoint | B13 – Purging & Filling Test Sheet
93cbcade-06f9-499c-9050-c4ca517b6ac8 | checkpoint | B14 – Quality Test Sheet
c232c009-5287-4065-94c0-b9fed22258e9 | checkpoint | B15 – Gas Identification Test Sheet
8778d4da-71b9-45d9-a5b4-e077c1d1314b | section | Commissioning
cf10e8d1-14d7-41bb-8b09-dd5bf3053119 | checkpoint | BMS Device Commissioning report
6800e08c-af90-497f-8937-5a636d776315 | checkpoint-no-value | Mcconnell Dowell
006ce436-7157-4d7e-8122-fe8f85fb1063 | signoff | Request McConnell Dowell Signoff
f383574d-2881-41fe-97dc-0342032a052e | checkpoint-no-value | Beca
320975e3-1af6-488e-ba2a-95c4eca8cc7f | signoff | Request Beca Signoff
498aa97f-55d3-439e-bf9a-a987024a1b33 | checkpoint-no-value | FIRP Signoff
fc48cd3f-cb06-4f61-9ac4-ed804977a27a | signoff | Record of Witnessing
3c7d91cd-b4ea-4b8c-bbf0-d2c34f2ec2a7 | checklist | MG01 - Oxygen Leak - Simulate an oxygen plant leak within the Gas Bottle Storage Room |  | MG01 - Oxygen Leak - Simulate an oxygen plant leak within the Gas Bottle Storage Room
a1c7c5ff-22c6-4476-bf75-f29d1537069a | section | IST Test
5ba12f0a-87fc-40e3-abba-3a8e83c71128 | checkpoint | IST Details
7df56a54-d779-5f27-8688-7f3115bfdab7 | textbox | Test Method - Release O2 gas near sensor until alarm level reached
caa5451e-3ae8-5d5d-8423-e68624704972 | textbox | Area - A40
64f90b3a-a645-463b-b63e-bd98e34c7bd7 | section | First Test
a69ceb46-2f78-4d12-ba1b-38b0e520873a | checkpoint | BMS - Plantroom MGAP Alarm
423542f0-6366-46ae-b78e-c5cb2a5cc954 | checkpoint | Mech - Control Room MGAP Alarm
9ea5b37d-2edc-4b63-bf0e-0060c3da7845 | checkpoint | BMS - BMS Alarm - O2 Leak
2e44cd81-1652-4cb3-acc7-469e8b19046a | checkpoint | BMS - Email to ADHB Personnel
9534bbe1-b4ec-49d9-9bda-bb6e7d693d71 | checkpoint | BMS - Plantroom Vent Fan Boost Mode
8f06bb96-89ca-416e-a5e2-80f9c61167eb | checkpoint | BMS - O2 Solenoid Valve Shut Off
29006162-4aaa-4b4f-a763-2f389fdc4b72 | checkpoint | BMS - Room Gas Warning Light
00a28fc0-11d7-488d-aa3d-81245f84975e | checkpoint | BMS - Room Gas Warning Sounder
6e2fd928-5e2c-4f07-9e32-c828fafeed3f | section | Second Test
3bf8cb7d-2382-46b2-aeb8-7d23e2839798 | checkpoint | BMS - Plantroom MGAP Alarm
a2a354f6-385e-481f-8f7e-40edee6c4817 | checkpoint | Mech - Control Room MGAP Alarm
675287fd-980a-4192-9e12-a25004c04f0d | checkpoint | BMS - BMS Alarm - O2 Leak
78cd4fe6-873a-43ad-b772-9620b35739ec | checkpoint | BMS - Email to ADHB Personnel
fc2ac219-89e2-413d-baab-558f80ca2be8 | checkpoint | BMS - Plantroom Vent Fan Boost Mode
a2074eae-31e8-4a58-95c6-186fadf715d3 | checkpoint | BMS - O2 Solenoid Valve Shut Off
208faac7-4c47-4702-98cd-5dc66e5a2979 | checkpoint | BMS - Room Gas Warning Light
2bd12fe2-1736-4976-9c15-fa7a62adb2ae | checkpoint | BMS - Room Gas Warning Sounder
6040bd6c-8bdd-43b3-a7e9-5ba3ee13a66e | checklist | MG02 - Loss of Power at MCC - To verify ATS transfer on loss of primary supply to replacement supply. |  | MG02 - Loss of Power at MCC - To verify ATS transfer on loss of primary supply to replacement supply.
4c3d73d2-b9e3-40b1-af59-f5d935d99fe0 | section | IST Test
cca61acb-c57f-44e1-910f-eec3547abb12 | checkpoint | IST Details
2bdf1d0e-4cf6-5fd8-b00e-804aa074bf37 | textbox | Test Method - Isolate normal supply to ATS [A40-02.0-MSSB-001]
0b78271d-b83b-5c02-b0cb-a257e2846ec2 | textbox | Area - A40
a95dfa33-5af0-449e-8131-33902c610335 | section | First Test
c55b2555-43c5-4b0f-9855-12a4a49edbbb | checkpoint | Mech/E4M - ATS transfer to secondary supply [A40-02.0-MSSB-002]
b3c59c4f-9e9b-47bd-bd0a-f3046222065f | checkpoint | Mech - Plantroom MGAP Alarm
cb8599a3-4334-4e7d-aedd-b208b95c04bb | checkpoint | Mech - Control Room MGAP Alarm
44de969d-ce42-471a-aa82-d0b275dfce27 | checkpoint | BMS - BMS Alarm - On secondary supply
57fa4471-5fdc-4586-b03a-bce14eb2e0c2 | checkpoint | BMS - Email to ADHB Personnel
2af21aac-3062-41a2-8f9b-c8ed9750245b | checkpoint | BMS - O2 Solenoid Valve Shut Off
1976b29b-c199-4656-ad1d-512ab863ead9 | section | Second Test
fff027ac-1599-4b19-ae78-ebd3d6772e2e | checkpoint | Mech/E4M - ATS transfer to secondary supply [A40-02.0-MSSB-002]
f95a6bce-3309-44e4-b416-1cb18b5d35e4 | checkpoint | Mech - Plantroom MGAP Alarm
e848c77c-a643-4535-b930-4f2ed80f0417 | checkpoint | Mech - Control Room MGAP Alarm
e3ca52f6-f00e-43b9-969e-5f629f83603f | checkpoint | BMS - BMS Alarm - On secondary supply
7675f0f6-bc34-4fce-93f7-0755e4e628c5 | checkpoint | BMS - Email to ADHB Personnel
3b3677f2-d644-4af6-b78d-00e8b74a8c32 | checkpoint | BMS - O2 Solenoid Valve Shut Off
e21176a2-82fa-44d7-8f8d-85080bc9a666 | checklist | MG03 - Reinstate primary power supply to MCC-006 and verify ATS transfer back to primary supply. |  | MG03 - Reinstate primary power supply to MCC-006 and verify ATS transfer back to primary supply.
1f40a893-08b5-4ab4-9733-b72e3d0038eb | section | IST Test
e8e0f560-878e-4e4c-bfcb-44983a8ea3cd | checkpoint | IST Details
3f1a93cc-2abb-519a-b1bc-086cee6df6bb | textbox | Test Method - Reinstate primary supply to ATS[A40-02.0-MSSB-001]
8b9746a3-096a-551b-a9b2-07e63604a5b5 | textbox | Area - A40
f9d8b6e8-9cac-48f0-91b5-cb9c1539237f | section | First Test
023cb2f6-ec20-4502-be16-64f549216f51 | checkpoint | Mech/E4M - ATS transfer back to Primary Supply after xxx sec delay.
37e90856-0675-4dd4-b144-8fd29c5bb35e | checkpoint | Mech - Plantroom MGAP Alarm
7384ef95-594a-460b-a439-153734384c6f | checkpoint | Mech - Control Room MGAP Alarm
e9eb8f05-be46-4d49-bf9e-fb09225023e4 | checkpoint | BMS - BMS Alarm - Normal - Primary supply available
0e766455-c78a-4da7-92b6-2a78eef08f46 | checkpoint | BMS - Email to ADHB Personnel
9d4e33a4-ae64-47f6-9141-3e4ee8c0291f | section | Second Test
6f36ddde-a56a-4437-9467-aaa8b587a727 | checkpoint | Mech/E4M - ATS transfer back to Primary Supply after xxx sec delay.
f69e906d-3e53-4dc7-aea8-54e7e4791c2c | checkpoint | Mech - Plantroom MGAP Alarm
eab5fe0a-2d42-4e3e-b59b-95e0e48fca78 | checkpoint | Mech - Control Room MGAP Alarm
d982e0ed-6761-4229-b8d0-3b2aff9d47a2 | checkpoint | BMS - BMS Alarm - Normal - Primary supply available
483ce68e-8ea4-4c3d-b069-7ac4a45de28c | checkpoint | BMS - Email to ADHB Personnel
e616b956-91f8-4b83-b1a7-2992729c4442 | checklist | MG04 - Oxygen Duty Bank No1 Empty. Auto Transfer to standby |  | MG04 - Oxygen Duty Bank No1 Empty. Auto Transfer to standby
17ec800a-58eb-44c4-9d20-6d7e7b6e1d64 | section | IST Test
fb299999-2919-48d5-b7b5-b7df401005b2 | checkpoint | IST Details
c2947de0-4891-524a-a2e9-cb5fa9431556 | textbox | Test Method - Isolate duty bottles and draw off some O2
e24fe01d-24a8-51e7-87ca-2c0f03a4252a | textbox | Area - A40
96d7fa11-1740-4538-bc6d-632692b4dd0b | section | First Test
4235f23c-42ff-4a12-84bc-62b66f88b0d5 | checkpoint | Auto transfer to Bank No.1 standby set
e2f6e0b8-a9fd-4a2d-b22c-b4097ab7679f | checkpoint | Mech - Plantroom MGAP Alarm
0bcbf02b-5ef7-495f-96ef-0926677bdbb3 | checkpoint | Mech - Control Room MGAP Alarm
df980c92-96e4-4dae-a826-e992de0a5de8 | checkpoint | BMS - BMS Alarm - Bank No.1 Empty
81729edc-cdf9-4cc9-a0cd-832905bd5580 | section | Second Test
520e34bc-352d-4fc3-96f6-805752f2f54e | checkpoint | Auto transfer to Bank No.1 standby set
bcd1543b-7557-4e09-b6ed-eb958f6a83ba | checkpoint | Mech - Plantroom MGAP Alarm
fe541a9a-28a3-4454-8e6f-a978074fa8d2 | checkpoint | Mech - Control Room MGAP Alarm
18249ef2-97f8-4733-ba4c-f87b067b6434 | checkpoint | BMS - BMS Alarm - Bank No.1 Empty
c00cbe02-76cb-4df6-9bf6-65af77d6806a | checklist | MG05 - Oxygen Standby bank No.1 below 10% capacity |  | MG05 - Oxygen Standby bank No.1 below 10% capacity
f6642f6e-03d0-4bfe-97a9-cd21a01de028 | section | IST Test
ec733239-3846-4535-9dd5-04f9a933faaa | checkpoint | IST Details
4631b1c6-3d41-588d-a21b-d56269ef1120 | textbox | Test Method - How can this be simulated? MEDGAS Ltd to confirm
20b71cb4-2f09-5956-ab6c-0ed6c876aa6f | textbox | Area - A40
367edacd-0380-4af8-b12a-96c3365edb6d | section | First Test
f0a7e937-145d-4039-ab62-13160f0cfa61 | checkpoint | Mech - Plantroom MGAP Alarm
28fb2ef5-3ea2-41bf-9774-d9d7839b643e | checkpoint | Mech - Control Room MGAP Alarm
b4333217-641f-413c-b530-355926151d8b | checkpoint | BMS - BMS Alarm
bb2fff39-afe0-447e-a6e4-9287297773af | checkpoint | BMS - Email to ADHB Personnel
21a43bc8-e6bd-40f6-8049-c54fba24cbee | section | Second Test
e4dfdeaf-e629-491f-aaee-75a5aba12d94 | checkpoint | Mech - Plantroom MGAP Alarm
116ce567-0119-4dcd-9257-f1cc37854974 | checkpoint | Mech - Control Room MGAP Alarm
4311684a-41bb-4333-b4c9-0cf81d4aee89 | checkpoint | BMS - BMS Alarm
623b4adf-659a-475d-b5af-766d54033bb5 | checkpoint | BMS - Email to ADHB Personnel
7079c655-4786-4e0d-b03a-44a5715e18a4 | checklist | MG06 - Oxygen Duty Bank No2 Empty |  | MG06 - Oxygen Duty Bank No2 Empty
d0f82953-67b9-4c28-a48a-f58d085b26f7 | section | IST Test
d9d35e4c-2a6d-4b30-96a6-5099c2cb078f | checkpoint | IST Details
08486f83-b662-5a8e-ad0d-ba059a23c94b | textbox | Test Method - Isolate duty bottles and draw off some O2
40590b91-0b5d-5ce9-a7d4-f16a9f37987d | textbox | Area - A40
5eb3e39c-c8e3-4e59-8971-a7fb08b905d6 | section | First Test
bc9c3642-9659-4168-91c8-8b1e7b8a6a82 | checkpoint | Auto transfer to Bank No.2 standby set
ebdba718-656f-4bfc-858d-12fec57eb565 | checkpoint | Mech - Plantroom MGAP Alarm
1eef0743-23b7-4e90-810e-47b730338e92 | checkpoint | Mech - Control Room MGAP Alarm
abfe72b3-f49e-4424-a459-be43016e3632 | checkpoint | BMS - BMS Alarm
07dd3359-d1c7-4464-be16-373c6bab51a8 | section | Second Test
142869f5-950e-42f6-b470-d54a27127589 | checkpoint | Auto transfer to Bank No.2 standby set
4eeeedc4-8f17-41d7-9cf0-4f182b850a56 | checkpoint | Mech - Plantroom MGAP Alarm
f047433f-f23e-4743-b13a-800050925da4 | checkpoint | Mech - Control Room MGAP Alarm
068e4050-967c-4c65-af87-f7c7c64dbf58 | checkpoint | BMS - BMS Alarm
4500518e-c244-4f6a-8c58-8412055adf41 | checklist | MG07 - Oxygen Standby bank No.2 below 10% capacity |  | MG07 - Oxygen Standby bank No.2 below 10% capacity
4778e504-8d57-45f2-a222-31b168743b3b | section | IST Test
ce44b059-be56-48eb-9918-9a7a3fecb732 | checkpoint | IST Details
474212b7-32e8-59c8-a684-bc9dc8cdc43c | textbox | Test Method - How can this be simulated? MEDGAS Ltd to confirm
5fa0bd6c-a405-5e0d-8d15-6d1fd5510c08 | textbox | Area - A40
bc61c21e-f9a4-4bab-9083-8748781013f1 | section | First Test
63ccef1f-c037-46b5-90fb-54a370759289 | checkpoint | Mech - Plantroom MGAP Alarm
790ff713-e2d0-4e4a-84bd-6ed653b6a034 | checkpoint | Mech - Control Room MGAP Alarm
f50b69b5-234d-4ab1-94cf-d37917368702 | checkpoint | BMS - BMS Alarm
6677270e-4544-45d2-88ed-4c5df8d1fcc9 | checkpoint | BMS - Email to ADHB Personnel
24ccb75b-dc54-4e9f-8b52-9cb4027dfa74 | section | Second Test
11f68bfb-eda1-410d-b90e-55b4d8f65710 | checkpoint | Mech - Plantroom MGAP Alarm
d96d1ded-5b38-4d2c-83b9-ec7914c01eb2 | checkpoint | Mech - Control Room MGAP Alarm
c8035b94-3385-4985-89e5-13f7d60ffb55 | checkpoint | BMS - BMS Alarm
679b1aec-55fa-4672-a200-168b25cc57e7 | checkpoint | BMS - Email to ADHB Personnel
0559b5c9-dc07-40b8-a247-5b11c7398635 | checklist | MG08 - Oxygen pipe low/high pressure |  | MG08 - Oxygen pipe low/high pressure
9240d7f4-53c4-47c1-8b47-1ce1afbdc0ab | section | IST Test
e64b35a1-fad8-4ff1-8c1b-bb649fed0f8e | checkpoint | IST Details
f4fa5018-49ea-5123-8d1c-68992875c723 | textbox | Test Method - How can this be simulated? MEDGAS to confirm
3f00c6b0-1e17-5748-aa47-9e1393c6c529 | textbox | Area - A40
13a098fd-1c7b-444e-9e10-01fd0ef5d386 | section | First Test
446a4aa6-ff50-4c8c-bd93-a48e00eb6a38 | checkpoint | Mech - Plantroom MGAP Alarm
131b7e67-59f8-4b3d-81aa-935536abe1b3 | checkpoint | Mech - Control Room MGAP Alarm
0884ba62-035c-4bfe-88c8-e5f25c5b4bf2 | checkpoint | BMS - BMS Alarm
82c097b9-8cf0-4335-93f1-a2d08a504f70 | checkpoint | BMS - Email to ADHB Personnel
b8eff37b-5be7-4c94-9ded-e7be6929b45f | section | Second Test
9de365b3-7929-4c42-9341-8dc10ff1af88 | checkpoint | Mech - Plantroom MGAP Alarm
80965479-3aca-4b15-8fdd-d8adc037e08b | checkpoint | Mech - Control Room MGAP Alarm
c9d98a31-756a-4fa0-a903-1ae2f2e23a18 | checkpoint | BMS - BMS Alarm
86b2bc29-08f3-42f1-ab4a-8008a7a4d23f | checkpoint | BMS - Email to ADHB Personnel
d0f1c323-d717-42a1-aa97-d2441ee7b7d1 | checklist | MG09 - Low delivery pressure at existing VIEs or VIE fault. Supply from A40 Manpacks |  | MG09 - Low delivery pressure at existing VIEs or VIE fault. Supply from A40 Manpacks
59da043e-b383-4dc6-a4ac-87ba7ed5bbc2 | section | IST Test
2f7675b3-426f-402d-86a9-143a169cbbef | checkpoint | IST Details
d1e76d0b-ce2a-5535-afe3-19b69270f4ee | textbox | Test Method - How can this be simulated? MEDGAS Ltd to confirm.
c6991baa-a9ff-5af0-aa29-afbe015ef373 | textbox | Area - A40
6a37e8a7-df5b-4f15-bf47-abbec04cba0b | section | First Test
1efa10a2-83a0-4521-a7eb-122ac311d942 | checkpoint | Mech - Control Room MGAP Alarm
69cc253e-09bf-488c-a309-2b51364f9a7f | checkpoint | BMS - BMS Alarm
6edd00a6-dc0a-4496-a9e4-7dd74580c0e2 | checkpoint | BMS - Email to ADHB Personnel
b5316568-6d2d-4dd2-8836-6e1cc633aa5c | checkpoint | Site supplied from A40 O2 Manpacks
628cdace-2909-4233-adba-a8bd5ef16104 | section | Second Test
6192a9a5-670c-40c7-b4f2-4e0756afd421 | checkpoint | Mech - Control Room MGAP Alarm
2aa97b0b-4ef6-4b27-a74e-7fec70717f7b | checkpoint | BMS - BMS Alarm
007c70f8-5924-4d9f-8f02-d69e3bca7f4d | checkpoint | BMS - Email to ADHB Personnel
4811fa2f-c6dd-4d6b-8ee4-42bd9405091c | checkpoint | Site supplied from A40 O2 Manpacks
460c6bb2-087d-4d81-abc9-92b9754908ef | checklist | MG10 - Nitrous oxide detector |  | MG10 - Nitrous oxide detector
50a8419b-58ec-4246-968c-cc2efa257621 | section | IST Test
fd218d42-fda7-40ba-b667-592897f6d3b9 | checkpoint | IST Details
2015774f-40bc-5445-bc80-620693373c91 | textbox | Test Method - Introduce N₂O test gas at sensor
62b4fe3c-1605-51d9-84e2-884c33e95967 | textbox | Area - A02
576af33f-7e00-41fc-af08-d86526a165d9 | section | First Test
89aee828-a758-4cbe-8435-7e7a284b29d6 | checkpoint | Mech - Plantroom MGAP Alarm
c7f684a0-4999-490a-a31f-ab6387d8d427 | checkpoint | Mech - Control Room MGAP Alarm
4c43c646-8a12-490c-b5b5-ef7e2cd3322b | checkpoint | BMS - BMS Alarm
5833e29d-9cac-4ab8-9f2a-ddf58693c210 | checkpoint | BMS - Email to ADHB Personnel
d7a7bbfb-493c-4a94-a889-7e7cbfed890b | checkpoint | BMS - Plantroom Vent Fan Boost Mode A02-01.3-EAF-001
4229fb36-03fe-4b0b-afa6-1ee2a8ffdaf8 | checkpoint | Nitrous Oxide Supply Solenoid Valve Shut Off
112a000c-992a-4047-9062-4d595b25dfaf | checkpoint | BMS - Room Gas Warning Light
a1e4fefd-051e-445d-990f-dad7ddf5edef | checkpoint | BMS - Room Gas Warning Sounder
d32d7d0b-cfe2-4205-bcb4-f9e28ac8a3f0 | section | Second Test
44d9eddc-9965-4340-94f9-e9c0ca7e4640 | checkpoint | Mech - Plantroom MGAP Alarm
40d5f28c-024d-4c93-b18e-701351913ab8 | checkpoint | Mech - Control Room MGAP Alarm
353cf9bb-23b6-48ad-bcdc-a3c57d19160b | checkpoint | BMS - BMS Alarm
d1b95f29-2fe8-4482-a92e-18581cecc221 | checkpoint | BMS - Email to ADHB Personnel
3a164a3d-8721-443b-a1e5-5c2a63e0bbe1 | checkpoint | BMS - Plantroom Vent Fan Boost Mode A02-01.3-EAF-001
a24fc29e-f7c8-4348-b70a-5c07ae35619f | checkpoint | Nitrous Oxide Supply Solenoid Valve Shut Off
c035330a-383c-4983-a726-793026cbd8d7 | checkpoint | BMS - Room Gas Warning Light
b02ccca5-5c8a-4335-b0ac-cb0a940333e7 | checkpoint | BMS - Room Gas Warning Sounder
494b3e0b-7cec-4b1c-b64d-7104cfead4a5 | checklist | MG11 - Loss of Power at MCC [A02-01.3-MCC-001] |  | MG11 - Loss of Power at MCC [A02-01.3-MCC-001]
6f06014f-05b8-4493-bd6f-89457de57336 | section | IST Test
18dbbc06-40a3-4011-8acd-214b9ac894d3 | checkpoint | IST Details
121100c8-b891-5ee4-9cb8-44fe87e7b96a | textbox | Test Method - Isolate N2O MGAP supply
73a862fe-0c0f-5a13-9e97-6af722668d0f | textbox | Area - A02
e3aae12a-75ab-4521-904d-97d67402f0d8 | section | First Test
2b6dfec7-1251-42df-b6da-285243970fbd | checkpoint | Mech - Plantroom MGAP Alarm
4e94b3e0-8a36-46ff-8aea-880acf900ee2 | checkpoint | Mech - Control Room MGAP Alarm
c030e84d-08bc-42a3-8dfe-f094a4c0cf11 | checkpoint | BMS - BMS Alarm
fe9892f2-d568-4e34-9e2d-96a2004249a6 | checkpoint | BMS - Email to ADHB Personnel
3ceb668a-8374-40ed-8307-7b6a53524b90 | checkpoint | Oxygen Supply Solenoid Valve Shut Off
e244d3d3-b024-43c7-ac49-0011021d543a | checkpoint | Nitrous Oxide Supply Solenoid Valve Shut Off
d7c5b00b-3650-4bf0-85e5-415a04d89d1b | checkpoint | Mech/E4M - O2 Supply Solenoid Valve Shut Off
3e8856fc-edf3-4290-947b-e4fa215911ff | checkpoint | Mech/E4M - MCC ATS Changeover Power Supply
2ce80233-db4b-4eb3-b391-eae50015cb7e | section | Second Test
2a222c6f-c5c8-46a8-bde5-4ab978d589dc | checkpoint | Mech - Plantroom MGAP Alarm
ca14dfe1-b6a9-49bc-8363-115d41583e3e | checkpoint | Mech - Control Room MGAP Alarm
b355f5d8-a105-443b-aaba-6520262c400d | checkpoint | BMS - BMS Alarm
8e60ddef-18ef-46b3-93d8-1ed9f3237939 | checkpoint | BMS - Email to ADHB Personnel
5a673522-4267-4ecc-b3c3-fd8e590da2da | checkpoint | Oxygen Supply Solenoid Valve Shut Off
16a7df59-0662-466e-9f0e-46fbf7db558a | checkpoint | Nitrous Oxide Supply Solenoid Valve Shut Off
148a2524-9fdf-4a58-ac54-46e7363a074e | checkpoint | Mech/E4M - O2 Supply Solenoid Valve Shut Off
992ba679-ebf6-4067-909e-68024f922b21 | checkpoint | Mech/E4M - MCC ATS Changeover Power Supply
26698814-c04b-46e0-921f-bf6312c541a8 | checklist | MG12 - Reinstate Power at MCC [A02-01.3-MCC-001] |  | MG12 - Reinstate Power at MCC [A02-01.3-MCC-001]
1fc41c91-58b8-4e1a-b9a1-553a97c1376e | section | IST Test
7590cdf6-1c91-4f50-9598-203eb3f5dc68 | checkpoint | IST Details
16be38cd-ffe1-5246-a4b5-24cfb844bf7a | textbox | Test Method - Reinstate N2O MGAP supply
b79c8919-d167-5c06-a162-905dfa9b8bf2 | textbox | Area -
9d82eaee-4c2b-40a3-9ae1-15b3acf302ad | section | First Test
5feaaaa0-bc5b-4690-b432-88e041599cf1 | checkpoint | Mech - Plantroom MGAP Alarm
85ec6cf3-a5d7-4a44-909f-8ddebc55e519 | checkpoint | Mech - Control Room MGAP Alarm
0a169bfa-7db9-430d-a75b-49d572f423ee | checkpoint | BMS - BMS Alarm
c765d790-9525-4215-9cae-a8cac733e4e8 | checkpoint | BMS - Email to ADHB Personnel
84c18c07-d723-4fe9-ba0b-6555176a13bf | section | Second Test
b4027c66-8115-4891-9fb3-b0719c5494b2 | checkpoint | Mech - Plantroom MGAP Alarm
1a458399-1a4d-40b4-95ff-acae8b78a3b5 | checkpoint | Mech - Control Room MGAP Alarm
8aad8cd5-a2b2-4e2c-a58a-7429eb4488dc | checkpoint | BMS - BMS Alarm
748b81ce-cc14-4763-a06e-282d35a2b281 | checkpoint | BMS - Email to ADHB Personnel
c133d57d-9bdc-401e-bfe4-43cdf9fa86ec | checklist | MG13 - Nitrous Oxide Duty Bank Empty, Standby Running |  | MG13 - Nitrous Oxide Duty Bank Empty, Standby Running
181c1207-4aa4-4515-bdac-8a464d430f6b | section | IST Test
5ba105ab-9117-43f9-97fa-c9145fea8a2b | checkpoint | IST Details
fa4b659f-b17b-51a7-a217-ef96e09e98f1 | textbox | Test Method - Isolate duty bottles and draw off some N2O
b5125be0-864f-54c6-a0b9-89bb68ecfb4b | textbox | Area - A02
c5421c14-fc8c-4d29-8e46-d66a47ba5aa0 | section | First Test
e10e64bb-be70-4292-94a9-6c8c0ebb1457 | checkpoint | Mech - Plantroom MGAP Alarm
d313fe92-fe22-4ee7-b068-a6ae98e3f1bc | checkpoint | Mech - Control Room MGAP Alarm
f853ce12-ae57-41cd-a591-54fb99881eb8 | checkpoint | BMS - BMS Alarm
ccc4c5dc-200d-4a64-b109-dbd5e3406fa4 | section | Second Test
0681915f-6c5d-4cd9-9aee-b141b43a868c | checkpoint | Mech - Plantroom MGAP Alarm
f200a880-86b6-4d31-933c-674e52fab2ed | checkpoint | Mech - Control Room MGAP Alarm
5ff43d82-72fb-4fea-ade0-55a35cfd8a11 | checkpoint | BMS - BMS Alarm
db1f96d4-3459-416f-857c-5b45087bcf93 | checklist | MG14 - Nitrous Oxide Standby bank below 10% capacity |  | MG14 - Nitrous Oxide Standby bank below 10% capacity
6ab98ddb-f8b7-40d6-a9c1-91544687c11a | section | IST Test
412f027a-3559-419e-86eb-cf354159e57b | checkpoint | IST Details
15c554f6-9239-5fdf-a21d-3d7b17f7796e | textbox | Test Method - How can this be simulated? MEDGAS Ltd to confirm.
c81bc627-c733-5833-8c70-9c530af30edf | textbox | Area - A02
e221b3f9-7f30-4fab-8797-bc0dae1bc6ce | section | First Test
8e29f7a0-9bd7-4e1b-856f-68737226c19a | checkpoint | Mech - Plantroom MGAP Alarm
8a1b85f5-bd3f-41cb-aec9-f6f4a0c02d01 | checkpoint | Mech - Control Room MGAP Alarm
b8a108e6-14b5-40f9-8093-cf298cff1ba7 | checkpoint | BMS - BMS Alarm
c46ec894-a2c7-406b-883b-2a2d48b9bbd4 | checkpoint | BMS - Email to ADHB Personnel
ebdf824f-e7b0-4c85-a1ec-dd41821ba05a | section | Second Test
ff6d0f1f-465a-49d8-ac12-989558c266aa | checkpoint | Mech - Plantroom MGAP Alarm
dd68743a-19ac-46d3-bbca-fef6599ab6be | checkpoint | Mech - Control Room MGAP Alarm
8d0c2ae9-a491-4116-8492-a32bed6376fe | checkpoint | BMS - BMS Alarm
a100b422-1b4a-412d-a738-537a1d26214a | checkpoint | BMS - Email to ADHB Personnel
a383391d-6885-4227-97c9-16551fbd7067 | checklist | MG15 - Nitrous Oxide pipe low/high pressure |  | MG15 - Nitrous Oxide pipe low/high pressure
d950c2af-e955-493c-9fa3-ec6ae9afed67 | section | IST Test
85f46b1f-3fd5-46be-b9da-29c90ca7a8e9 | checkpoint | IST Details
987d6ed0-d9c6-5ff6-ae57-8dc68d802485 | textbox | Test Method - How can this be simulated? MEDGAS Ltd to confirm.
de1fa919-e972-5887-91f8-6fbe4946181f | textbox | Area - A02
52515a8c-c8e7-471d-9a1f-763855f26dcc | section | First Test
ff3ae9a2-b0c3-44af-ac5f-f50abcdce122 | checkpoint | Mech - Plantroom MGAP Alarm
8cd6359a-35c0-49bf-b09d-70dc11213200 | checkpoint | Mech - Control Room MGAP Alarm
fb27b46e-32b9-4ce5-8742-b6937e8b2b1d | checkpoint | BMS - BMS Alarm
ce3f7f5d-a12b-4b22-87cf-bdca450213ed | checkpoint | BMS - Email to ADHB Personnel
a1989d2d-152e-4b39-8b25-87d613d74e9c | section | Second Test
12f75db5-943e-4214-ad4d-88d83172963e | checkpoint | Mech - Plantroom MGAP Alarm
bad699b0-2539-460d-9bb9-18e3877ea074 | checkpoint | Mech - Control Room MGAP Alarm
f1040895-3d5f-47bc-96e8-d9d806329e30 | checkpoint | BMS - BMS Alarm
78cc9284-ec70-4d5f-b5c9-4627d793f14b | checkpoint | BMS - Email to ADHB Personnel
6b88f95d-c8da-4fee-b005-216da209fe3b | checklist | MG16 - Low delivery pressure at A32 bottles |  | MG16 - Low delivery pressure at A32 bottles
bf6311e9-0687-45a2-a0f3-ec488d446ec9 | section | IST Test
80d8757b-51c4-405b-a3bb-0d8593c65e9e | checkpoint | IST Details
e26b5aa0-4413-5243-9ff2-fe827ad14a52 | textbox | Test Method -
a0651311-ac99-5eee-a1d0-5f473a1b42f3 | textbox | Area - A02
b5df1972-659f-4816-95ce-0e146c3ac7d6 | section | First Test
1acefff2-5836-473c-a72e-40d322ec53a9 | checkpoint | Mech - Control Room MGAP Alarm
1ba10eff-3ebf-4b8b-b76f-c096a34afce1 | checkpoint | BMS - BMS Alarm
de9cffd4-a75f-4104-8140-7f341de088a0 | checkpoint | BMS - Email to ADHB Personnel
060a20db-d387-4b9f-bffb-fa0999ff5cab | checkpoint | Automatic Manifold Operational
aaf4bf08-ac9b-4289-8458-c0ac60ecffab | section | Second Test
1584757e-ad11-460d-982f-86b4b898d96f | checkpoint | Mech - Control Room MGAP Alarm
21e8fd5a-6047-4f18-b83d-e9234975c722 | checkpoint | BMS - BMS Alarm
9b3f0b88-0076-4c9e-99d1-856f84bea67d | checkpoint | BMS - Email to ADHB Personnel
95350f06-dc5a-4600-a6fe-51ca4ee55ffb | checkpoint | Automatic Manifold Operational
0cf58f17-93ff-4af3-b134-82b4ea6c50df | checklist | MG17 - Tunnel Zone 1 Oxygen Level exceeds Recommended level (xx ppm) |  | MG17 - Tunnel Zone 1 Oxygen Level exceeds Recommended level (xx ppm)
fa94d100-6261-4e1b-bfde-317a00500ad4 | section | IST Test
4305cbe3-3219-4304-949b-07c730901462 | checkpoint | IST Details
999f83be-8ecf-592f-b3e5-af88c68465f8 | textbox | Test Method - Introduce O2 test gas at Tunnel Zone 1 O2 Detector
c822a03d-ce63-5cf7-9bc7-3a206b7b0b5c | textbox | Area - Tunnel Zone 1
6e64f567-ef09-4fd2-aa56-f1c8e954020f | section | First Test
bed68815-b623-4dc2-b888-c8e4d4bd295b | checkpoint | BMS - BMS Alarm
07de2703-454b-4e8b-b214-a854dc8460e6 | section | Second Test
8dbe1c85-66ba-410d-a4ff-49da68cb91f4 | checkpoint | BMS - BMS Alarm
4283f236-5e4c-4114-96f2-83a847e61580 | checklist | MG18 - Tunnel Zone 1 Oxygen Levels Exceed Safe level (xx ppm) |  | MG18 - Tunnel Zone 1 Oxygen Levels Exceed Safe level (xx ppm)
2c6387b0-0964-41ce-929a-987862cc6668 | section | IST Test
5f9e6293-a164-4808-ac01-3bdd5e089213 | checkpoint | IST Details
342bedc7-4821-5d62-86e1-7857af8f46c9 | textbox | Test Method - Introduce O2 test gas at Tunnel Zone 1 O2 Detector
34994830-bb51-5e72-a5b1-8beea81517e1 | textbox | Area - Tunnel Zone 1
ffffbd57-9771-49d7-ba0d-414d48efeae7 | section | First Test
fd0eadff-e7ac-4419-a1a2-d42dd3e30f4a | checkpoint | BMS - Tunnel Ventilation Fans go to Boost Mode
82351c8f-074d-41a3-8c28-db5e161b2501 | checkpoint | BMS - Zone 1 Oxygen Solenoid Valves (x2) Close
7b4a8b80-6008-4382-99d1-408d4bcf6c86 | checkpoint | BMS - Gas Visual Alarm Panel Activates - A40 entrance to Zone 1
4c803c0c-11f8-4734-abd8-169a608d1dc6 | checkpoint | BMS - Gas Visual Alarm Panel Activates - Zone 2 entrance to Zone 1
5075397b-e74e-490a-843e-dcaca2785c8e | checkpoint | BMS - Zone 1 sounders activate
9c8b14d1-c0ec-4715-9f44-178cef0f0bad | checkpoint | BMS - BMS Alarm
fa841f25-7702-4e6f-bcf7-e0f99ca126f3 | checkpoint | BMS - Email to ADHB Personnel
1427691e-9df0-419c-94fc-b1d7cd0cd502 | section | Second Test
d58ea66d-3272-46c2-893b-48c36a855f4e | checkpoint | BMS - Tunnel Ventilation Fans go to Boost Mode
f929337c-2763-4a8a-a4d8-738a566f9fc8 | checkpoint | BMS - Zone 1 Oxygen Solenoid Valves (x2) Close
408b1b11-d512-4252-acc6-6044a2f61d55 | checkpoint | BMS - Gas Visual Alarm Panel Activates - A40 entrance to Zone 1
e13012d5-ac6c-42db-93d9-f29410d4c240 | checkpoint | BMS - Gas Visual Alarm Panel Activates - Zone 2 entrance to Zone 1
94b90cd7-0b4c-4d39-acfb-78913d7a3e4d | checkpoint | BMS - Zone 1 sounders activate
1c00090d-58e5-418a-9213-4916b947a7b3 | checkpoint | BMS - BMS Alarm
2c5eee59-1864-4976-96b0-3594489bc7a6 | checkpoint | BMS - Email to ADHB Personnel
08702e36-f672-4665-98fc-0857b64d0836 | checklist | MG19 - Tunnel Zone 2 Oxygen Level exceeds Recommended level (xx ppm) |  | MG19 - Tunnel Zone 2 Oxygen Level exceeds Recommended level (xx ppm)
d59e3236-f19e-4097-8353-55f23864baf5 | section | IST Test
4ec08389-e50d-43ca-8ae9-4a36d5333cee | checkpoint | IST Details
c7b204fa-5a65-53ed-a7ee-f5bf10fbb3e8 | textbox | Test Method - Introduce O2 test gas at Tunnel Zone 2 O2 Detector
5c0d1d6c-44ab-59a8-9716-8cd3aa8122e9 | textbox | Area - Tunnel Zone 2
5185eea0-5636-4c8a-830c-72359dc55e67 | section | First Test
d6435174-c488-4fc6-8d53-5e00ff88673e | checkpoint | BMS - BMS Alarm
14dd5617-7944-449c-8160-33876eb15fad | section | Second Test
80443dd2-eeca-44ca-abd4-337fa0a3e89a | checkpoint | BMS - BMS Alarm
45a25c35-1429-44c6-8ee6-ad4341eada0e | checklist | MG20 - Tunnel Zone 2 Oxygen Levels Exceed Safe level (xx ppm) |  | MG20 - Tunnel Zone 2 Oxygen Levels Exceed Safe level (xx ppm)
6de5a672-2935-4d69-94f6-e54329e11eec | section | IST Test
14f16dfe-cf6b-4428-af05-2774730fb927 | checkpoint | IST Details
44c92c96-b282-5f83-bd26-fbbe9717fec9 | textbox | Test Method - Introduce O2 test gas at Tunnel Zone 2 O2 Detector
f3ba47d7-2550-547d-8c6a-b488c5d0cff6 | textbox | Area - Tunnel Zone 2
315d1367-29fd-4182-8be8-d1394d10e222 | section | First Test
3d50b68c-25dc-4335-bcef-7c3e93db0346 | checkpoint | BMS - Tunnel Ventilation Fans go to Boost Mode
a7ebb797-0f06-43b8-aed6-a7620f3e52f9 | checkpoint | BMS - Zone 2 Oxygen Solenoid Valves (x2) Close
c74162b9-340b-4d81-8709-949c0befbe15 | checkpoint | BMS - Gas Visual Alarm Panel Activates - Zone1 entrance to Zone 2
23f56255-fccd-41f0-8234-379da32fea57 | checkpoint | BMS - Gas Visual Alarm Panel Activates - Zone 3 entrance to Zone 2
ca5506ee-ecd3-46f5-87da-61331ded15b5 | checkpoint | BMS - Zone 2 sounders activate
86c76015-c763-4818-84eb-48bb62d05592 | checkpoint | BMS - BMS Alarm
a9a8442c-d0d0-42b0-936c-c3cc49425c45 | checkpoint | BMS - Email to ADHB Personnel
5e10ff55-d20f-4478-8e2a-1c3b4144eebe | section | Second Test
0d027a8d-0be1-44e2-acdd-8003504d9eb3 | checkpoint | BMS - Tunnel Ventilation Fans go to Boost Mode
c1f3cc51-0365-4f0c-9f7e-94f77ed89720 | checkpoint | BMS - Zone 2 Oxygen Solenoid Valves (x2) Close
d7dbba84-215f-41ef-b7ab-37394109dd06 | checkpoint | BMS - Gas Visual Alarm Panel Activates - Zone1 entrance to Zone 2
9441f380-a876-4d45-9858-0aa4c14466ce | checkpoint | BMS - Gas Visual Alarm Panel Activates - Zone 3 entrance to Zone 2
d0afda51-59e1-4466-b62e-6fe7b864ff15 | checkpoint | BMS - Zone 2 sounders activate
4aad91c6-f899-4d38-a49d-1bd5e62b2b0f | checkpoint | BMS - BMS Alarm
42c597ca-8462-4691-a069-7defef268670 | checkpoint | BMS - Email to ADHB Personnel
98a46b56-2ce5-4e9d-a5b9-f5dbf050ce84 | checklist | MG21 - Tunnel Zone 3 Oxygen Level exceeds Recommended level (xx ppm) |  | MG21 - Tunnel Zone 3 Oxygen Level exceeds Recommended level (xx ppm)
d2285c39-bd90-4fe6-81bc-ccebfb84a172 | section | IST Test
52cc9200-a3f0-4fb8-81f3-becef65bdba9 | checkpoint | IST Details
90e200e2-167b-56ea-8ed0-4367744d02cb | textbox | Test Method - Introduce O2 test gas at Tunnel Zone 3 O2 Detector
67b74e43-7a99-5294-8c65-4bc9eea29822 | textbox | Area - Tunnel Zone 3
921356f2-49e3-427b-b335-491b61690b52 | section | First Test
d797e0e6-7c75-4026-ad3f-39712c66e9e9 | checkpoint | BMS - BMS Alarm
639beb39-eb16-4ec6-a81a-0569a2dd2832 | section | Second Test
11bb903c-0e91-4deb-98d4-7c3ae017afd0 | checkpoint | BMS - BMS Alarm
38a38b08-9fd1-4392-b975-1305512d469d | checklist | MG22 - Tunnel Zone 3 Oxygen Levels Exceed Safe level (xx ppm) |  | MG22 - Tunnel Zone 3 Oxygen Levels Exceed Safe level (xx ppm)
1b60ace7-ecbc-41e3-a4ba-9d4bce44a526 | section | IST Test
2dc5363a-18db-4dd8-a882-293251ef7a49 | checkpoint | IST Details
7ecc73ee-39de-5864-bee5-8cfdafeea973 | textbox | Test Method - Introduce O2 test gas at Tunnel Zone 3 O2 Detector
e4cfa4f3-ea8e-533a-a3ec-c1771a79215c | textbox | Area - Tunnel Zone 3
ec989253-6f12-4224-8b01-8d5ed0a7ba42 | section | First Test
effc3699-ba5d-4a7d-8524-a42c65358320 | checkpoint | BMS - Tunnel Ventilation Fans go to Boost Mode
2a3c7b29-41f5-4bd9-992a-93f4aaf8e956 | checkpoint | BMS - Zone 3 Oxygen Solenoid Valves (x2) Close
f2b73c25-1b2b-4c98-9205-577fefca4d54 | checkpoint | BMS - Gas Visual Alarm Panel Activates - Zonev2 entrance to Zone 3
7ee6a10d-c2de-4ae7-9b7c-c4a48eac3e8d | checkpoint | BMS - Gas Visual Alarm Panel Activates - A01 entrance to Zone 3
e74db791-f011-46de-8993-aa3880bea9d7 | checkpoint | BMS - Zone 3 sounders activate
ca9b3f9c-fcf3-4569-a938-1ca462de9cb6 | checkpoint | BMS - BMS Alarm
5fdc9759-465f-46ea-8c05-2a48b442641c | checkpoint | BMS - Email to ADHB Personnel
d53ea76f-cbb0-43a5-99ee-3e668b5b620e | section | Second Test
9853aaa8-71ed-4c2d-8535-9669846a68ac | checkpoint | BMS - Tunnel Ventilation Fans go to Boost Mode
0e8fefcb-9a83-478b-b2a2-62e9bab90b6c | checkpoint | BMS - Zone 3 Oxygen Solenoid Valves (x2) Close
89fcb6c8-e020-4c6c-9c38-e1587e4fa6d9 | checkpoint | BMS - Gas Visual Alarm Panel Activates - Zonev2 entrance to Zone 3
93d037ba-16a1-4dea-b84f-504008bb78e3 | checkpoint | BMS - Gas Visual Alarm Panel Activates - A01 entrance to Zone 3
65afb9f0-1f54-4b07-a361-a3b91d50f32f | checkpoint | BMS - Zone 3 sounders activate
378abfa7-4963-4908-8c66-2f734dedddfe | checkpoint | BMS - BMS Alarm
963adca2-789a-446c-ae09-8c0e605a4667 | checkpoint | BMS - Email to ADHB Personnel
46172d4a-916d-48af-a8ba-c8337690cc5e | checklist | MG23 - Tunnel Zone 1 N2O Level exceeds Recommended level (xx ppm) |  | MG23 - Tunnel Zone 1 N2O Level exceeds Recommended level (xx ppm)
76ff4059-d95c-4755-ab66-b055febae34f | section | IST Test
dd2212dd-2afa-43e3-8c90-0653ffd2b2e4 | checkpoint | IST Details
4d134971-2a39-5754-8243-06e2d8dcb070 | textbox | Test Method - Introduce N2O test gas at Tunnel Zone 1 N2O Detector
f949e20f-a615-506e-ac94-356d44a3d23b | textbox | Area - Tunnel Zone 1
2d93788d-cc12-43e4-8573-816bfd72fbf9 | section | First Test
98845f58-3e39-4a4f-ab67-3c74bdb490ce | checkpoint | BMS - BMS Alarm
61e9843c-c9b6-48ad-8139-70ccc4ac9da1 | section | Second Test
4356d251-8e53-4b09-8dde-26e21a5a601c | checkpoint | BMS - BMS Alarm
d7fc6d5e-d23e-4a17-a9f8-37e0eb147cb4 | checklist | MG24 - Tunnel Zone 1 N2O Levels Exceed Safe level (xx ppm) |  | MG24 - Tunnel Zone 1 N2O Levels Exceed Safe level (xx ppm)
a9008815-cec4-4747-9823-09b047ff3899 | section | IST Test
6ce31251-5033-4c84-81c7-4dd2de105321 | checkpoint | IST Details
3db47a66-4534-51fa-a7c8-6474a7cc5cd9 | textbox | Test Method - Introduce N2O test gas at Tunnel Zone 1 N2O Detector
e59297b9-64d1-56ef-bbc5-7371146f147b | textbox | Area - Tunnel Zone 1
26e61f16-0e23-404f-a161-5862e3a9d0fb | section | First Test
94413b70-3dfc-48a2-8e02-198f49bb954f | checkpoint | BMS - Tunnel Ventilation Fans go to Boost Mode
676db6e1-4eba-4ea0-a571-a99a84a3e9e5 | checkpoint | BMS - Zone 1 N2O Solenoid Valves (x2) Close
026d674c-6d29-4c74-833a-6921860b0939 | checkpoint | BMS - Gas Visual Alarm Panel Activates - A40 entrance to Zone 1
879228ee-eb57-4e62-8711-369d255ecc16 | checkpoint | BMS - Gas Visual Alarm Panel Activates - Zone 2 entrance to Zone 1
364bae7b-de71-4b65-8950-687c232af61b | checkpoint | BMS - Zone 1 sounders activate
9538a645-0d8e-4d1d-8c3b-88aebd2b5833 | checkpoint | BMS - BMS Alarm
75dee055-ec1e-47e9-9b40-bb4fc6c43a87 | checkpoint | BMS - Email to ADHB Personnel
3dbe45a9-4fce-4b0d-8c52-2cbada31d591 | section | Second Test
cc24e497-d09c-4eb6-a1f9-99f35746fb39 | checkpoint | BMS - Tunnel Ventilation Fans go to Boost Mode
451904c3-592d-49ee-bf0c-043d771952f6 | checkpoint | BMS - Zone 1 N2O Solenoid Valves (x2) Close
c652d19c-c871-452c-b8d6-ec7c77798c50 | checkpoint | BMS - Gas Visual Alarm Panel Activates - A40 entrance to Zone 1
9555bc34-7dfe-4391-be8f-0c75e7965763 | checkpoint | BMS - Gas Visual Alarm Panel Activates - Zone 2 entrance to Zone 1
9da1b693-eee6-4535-9562-bd29cb6e3dc6 | checkpoint | BMS - Zone 1 sounders activate
f78d5901-6a82-4ce3-8e82-0488b325c5b3 | checkpoint | BMS - BMS Alarm
32dafbe2-9d4a-40e2-b831-9f9e8a6985e9 | checkpoint | BMS - Email to ADHB Personnel
632ae71b-2f15-4ba9-8410-e21194d6b2ac | checklist | MG25 - Tunnel Zone 2 N2O Level exceeds Recommended level (xx ppm) |  | MG25 - Tunnel Zone 2 N2O Level exceeds Recommended level (xx ppm)
8521c385-9301-4c2d-8167-89d4298d9787 | section | IST Test
77dd6390-8624-430c-82ca-cc0d3451ca20 | checkpoint | IST Details
4bfe0d18-2ba1-5122-8b12-c5b0fbdd91b0 | textbox | Test Method - Introduce N2O test gas at Tunnel Zone 2 N2O Detector
979e7119-b543-5d79-a81b-5a4e91ca64d6 | textbox | Area - Tunnel Zone 2
2a2bbfbe-5f96-41cf-ba01-ca699296a127 | section | First Test
38a9ee72-222b-498c-b350-784a317d1f6c | checkpoint | BMS - BMS Alarm
8a11b87e-0633-4ce1-8adc-68486b01d6e4 | section | Second Test
6ad517e8-ef63-40d3-be30-a3152d4d0faa | checkpoint | BMS - BMS Alarm
31da907b-c25b-481c-8958-54498d68541f | checklist | MG26 - Tunnel Zone 2 N2O Levels Exceed Safe level (xx ppm) |  | MG26 - Tunnel Zone 2 N2O Levels Exceed Safe level (xx ppm)
674b7593-20f9-4d27-9434-d1745a168ee8 | section | IST Test
75204604-36a7-4a69-9799-c8821766dd00 | checkpoint | IST Details
417c93d4-9761-5d79-a31b-14da26228bf8 | textbox | Test Method - Introduce N2O test gas at Tunnel Zone 2 N2O Detector
bf751bb8-05ee-596b-9873-09ee6fa5b7a9 | textbox | Area - Tunnel Zone 2
ae67d02e-4a1e-41a0-be4b-066f68982d4e | section | First Test
351c4301-613a-4cc7-82a4-00b824db7622 | checkpoint | BMS - Tunnel Ventilation Fans go to Boost Mode
028e701a-f1c4-402d-8fe6-d32045e544ce | checkpoint | BMS - Zone 2 N2O Solenoid Valves (x2) Close
02d71586-2716-49a9-bd7c-e508c1922d65 | checkpoint | BMS - Gas Visual Alarm Panel Activates - Zone1 entrance to Zone 2
c00afd13-c0ed-42b3-b216-c077619f4a5c | checkpoint | BMS - Gas Visual Alarm Panel Activates - Zone 3 entrance to Zone 2
e89d07da-c1dd-413b-92c5-88e372fa4d8f | checkpoint | BMS - Zone 2 sounders activate
ef4fedb0-acf0-4dbc-8737-d1470a52cc63 | checkpoint | BMS - BMS Alarm
dab6d386-1320-4de5-89ac-00b9eaa790d7 | checkpoint | BMS - Email to ADHB Personnel
79c1a305-5183-4a15-a6e8-6d21b1faa1b6 | section | Second Test
cad58643-ee89-4a5d-a99c-8cd2f6ea40b1 | checkpoint | BMS - Tunnel Ventilation Fans go to Boost Mode
2c2fd249-f95b-4bcd-acc3-6f463b57cc95 | checkpoint | BMS - Zone 2 N2O Solenoid Valves (x2) Close
581a9549-7b40-41a8-8edb-820db374d37d | checkpoint | BMS - Gas Visual Alarm Panel Activates - Zone1 entrance to Zone 2
2417cf06-3e5c-45d2-8b71-f2d88ff7fc60 | checkpoint | BMS - Gas Visual Alarm Panel Activates - Zone 3 entrance to Zone 2
26c095d1-0efa-4966-bd15-0d2c8186dd9d | checkpoint | BMS - Zone 2 sounders activate
8f5d34f0-5fa8-4558-ab4c-1511410fb46e | checkpoint | BMS - BMS Alarm
0549b8e7-d8e0-45dc-b356-debbe4a6fd85 | checkpoint | BMS - Email to ADHB Personnel
707b48e5-6d48-4647-a681-bef1e34dd7d1 | checklist | MG27 - Tunnel Zone 3 N2O Level exceeds Recommended level (xx ppm) |  | MG27 - Tunnel Zone 3 N2O Level exceeds Recommended level (xx ppm)
f3b3bb6a-8773-463b-be87-516989abb39b | section | IST Test
2e1c9950-96b0-4486-b4f4-fb9d891fba8d | checkpoint | IST Details
56f1d797-6ca0-5237-8a6f-ab744da0c83f | textbox | Test Method - Introduce N2O test gas at Tunnel Zone 3 N2O Detector
7f86c7d7-b52f-5738-8347-076fcd311b0f | textbox | Area - Tunnel Zone 3
422659af-5498-4220-b3f9-75e72e062e45 | section | First Test
306f6972-cf9e-401e-8854-ab588c9dcc5b | checkpoint | BMS - BMS Alarm
3102cf6b-4348-45c7-81e4-e20239c62156 | section | Second Test
8bb901e8-b3d4-4036-b77c-681c9423f049 | checkpoint | BMS - BMS Alarm
33627538-2605-4840-9174-2669e5948a66 | checklist | MG28 - Tunnel Zone 3 N2O Levels Exceed Safe level (xx ppm) |  | MG28 - Tunnel Zone 3 N2O Levels Exceed Safe level (xx ppm)
aacb41ee-8b1d-4853-a070-031bc9739953 | section | IST Test
88185ea7-4be6-459c-9a2b-9f0210b1d191 | checkpoint | IST Details
1276cf6d-a7de-5baf-b4f8-6ee497c4cbd0 | textbox | Test Method - Introduce N2O test gas at Tunnel Zone 3 N2O Detector
d2e9bf07-c7e7-5943-ab69-2e04aa9b9154 | textbox | Area - Tunnel Zone 3
015230b8-9e27-453d-9d92-b11ce143f2a8 | section | First Test
6e2f2869-abd3-4c36-ab5a-a634b8ed6b4d | checkpoint | BMS - Tunnel Ventilation Fans go to Boost Mode
3d3fbbab-a074-432a-bad2-c8f0c1318d88 | checkpoint | BMS - Zone 3 N2O Solenoid Valves (x2) Close
d16250bf-741a-4062-aeb8-68ee50cf097d | checkpoint | BMS - Gas Visual Alarm Panel Activates - Zonev2 entrance to Zone 3
2b190164-4536-42c7-85a2-590b579aeb2e | checkpoint | BMS - Gas Visual Alarm Panel Activates - A01 entrance to Zone 3
f06fd36d-edbc-4bd6-abac-24a57e3deb19 | checkpoint | BMS - Zone 3 sounders activate
55b3823a-02dc-43fc-b50a-a994e3e0b0df | checkpoint | BMS - BMS Alarm
4fcd7aca-3b8b-4f38-9336-86389ea4380e | checkpoint | BMS - Email to ADHB Personnel
3511934c-fc90-489e-85ee-20003515fc8f | section | Second Test
512229da-6d18-423f-8a73-446a85dda77c | checkpoint | BMS - Tunnel Ventilation Fans go to Boost Mode
d28e1cc1-40f4-46b0-bd0c-1e1035738546 | checkpoint | BMS - Zone 3 N2O Solenoid Valves (x2) Close
fc903400-fe0b-4a55-9334-dd9cf9bdb6ab | checkpoint | BMS - Gas Visual Alarm Panel Activates - Zonev2 entrance to Zone 3
4f2955d2-6156-4c46-98c3-4b62d8c81ddc | checkpoint | BMS - Gas Visual Alarm Panel Activates - A01 entrance to Zone 3
6e7b84ba-a0fc-4f11-b04a-8daf6ca4caab | checkpoint | BMS - Zone 3 sounders activate
4d37973f-0af2-4726-a54c-6e7ac80d2c5e | checkpoint | BMS - BMS Alarm
dc0608a8-5a4e-41fa-8868-2ad6657e2459 | checkpoint | BMS - Email to ADHB Personnel
aee85248-f11d-48d5-ad0e-6cd6f4496a1a | checklist | MG29 - Tunnel O2 pipework Leak |  | MG29 - Tunnel O2 pipework Leak
61ded0f3-5051-424c-9791-d2e946695ac0 | section | IST Test
ea2def54-9f7f-429f-9d78-e479db4014fa | checkpoint | IST Details
78248579-844a-5681-8e1d-af3bb584a3bb | textbox | Test Method - Vent O2 from line until line pressure reaches xxkPa
2d6341ff-d1f7-57b6-9e77-0385201caba4 | textbox | Area - Tunnels
0bef8fb8-431f-4693-bf6e-1a4277f7f12e | section | First Test
d097cdbb-12f6-4e60-87b3-f89559487f1a | checkpoint | BMS - Zone 1,2,3 O2 Solenoid Valves CLOSE
97a36c1d-324e-43a5-b8e7-269fca8058d2 | checkpoint | BMS - BMS Alarm
fce16b47-6487-4782-9780-36253898fb48 | checkpoint | BMS - Email to ADHB Personnel
8ff6c29d-907a-49d4-9aea-55ed4f2a43b7 | section | Second Test
49531e9c-6b0d-47ca-85c2-a8d0b8c468a7 | checkpoint | BMS - Zone 1,2,3 O2 Solenoid Valves CLOSE
bb430a86-084a-4eb2-93fa-0f325a0e061b | checkpoint | BMS - BMS Alarm
8842b402-a1ca-44ca-9908-dc68494823c4 | checkpoint | BMS - Email to ADHB Personnel
6823122b-b399-49e7-8e03-7fa943ef657e | checklist | MG30 - Tunnel N2O pipework Leak |  | MG30 - Tunnel N2O pipework Leak
ae990428-166a-492c-b76f-9bf3dd55046d | section | IST Test
b2501a94-4598-4e6a-a9f1-00c21c2f027c | checkpoint | IST Details
04f22cdd-96e0-51f2-b0e6-66a931525636 | textbox | Test Method - Vent N2O from line until line pressure reaches xxkPa
2d4d4929-5330-5378-bd19-2795af7839b9 | textbox | Area - Tunnels
c596e8f6-0b53-40bf-86cf-a7e516df4a78 | section | First Test
bb357fbc-d404-4873-8622-fbc69ad18894 | checkpoint | BMS - Zone 1,2,3 N2O Solenoid Valves CLOSE
9bed649f-7661-47a9-ad89-82d58773e2ce | checkpoint | BMS - BMS Alarm
19ba49d0-342c-4e96-b884-27ed3ae3e862 | checkpoint | BMS - Email to ADHB Personnel
238015f7-2d5c-49d8-b5b4-35bc0ddebdba | section | Second Test
b043ba86-19c8-4be5-b8d7-1e6e0479c9ea | checkpoint | BMS - Zone 1,2,3 N2O Solenoid Valves CLOSE
0a1febaf-2750-48e9-8219-f32ef934da46 | checkpoint | BMS - BMS Alarm
75c1e431-2387-4f0d-936a-dc9257299899 | checkpoint | BMS - Email to ADHB Personnel
29163749-caf9-4122-af78-b4e2927c258e | checklist | MG31 - Tunnel MA pipework Leak |  | MG31 - Tunnel MA pipework Leak
db5b6bfc-4039-4dba-97f3-bc944906ed7f | section | IST Test
a12445b4-bd96-4b5c-a1ca-446660de0fda | checkpoint | IST Details
5935f88b-f92f-5944-901b-1ce94f94fc2b | textbox | Test Method - Vent MA from line until line pressure reaches xxkPa
294028fd-1cb0-5539-83bf-1ebe9de083cc | textbox | Area - Tunnels
21765f30-dea8-4ce3-bb54-7e6b5b9b5c41 | section | First Test
5015884e-b89f-4732-b198-5ea41a706412 | checkpoint | BMS - Zone 1,2,3 MA Solenoid Valves CLOSE
b28dc99e-4402-49ad-b6d9-abdbeb35535f | checkpoint | BMS - BMS Alarm
380cd07b-d5c8-4f39-99a5-b27044e5d2d7 | checkpoint | BMS - Email to ADHB Personnel
65c72c17-ad4e-478f-a83d-dcda6317552a | section | Second Test
7521192a-49c9-4574-a785-897e4ed95f44 | checkpoint | BMS - Zone 1,2,3 MA Solenoid Valves CLOSE
471da5f8-7ce4-4883-8ff9-bc2784c3017d | checkpoint | BMS - BMS Alarm
340a3a57-46f1-4371-90c6-a61b1901d00c | checkpoint | BMS - Email to ADHB Personnel
6c5c701a-5d00-4f44-859b-c72fd61355ae | checklist | Neutral Earthing Resistor |  | Equipment -
050c1e60-109f-4fc4-8846-8111da261b22 | section | Factory Acceptance Testing
5af474b1-96c1-4ac6-a6b0-0907c4e3e274 | checkpoint | Factory Acceptance Test Report
6a36f024-683e-4dac-8992-94427a07e3c9 | section | Pre-Commissioning
fce7f0a0-bacd-47ab-be5b-65fb07ead637 | checkpoint | Pre-Commissioning Test Report
4d150b66-9e7b-41ff-a71b-9dd11b4a8979 | checkpoint-no-value | Mcconnell Dowell
73b04745-aa73-4214-9f6e-46a5eb131cfd | signoff | Request McConnell Dowell Signoff
561a3f9b-c173-45d6-8874-7efdc648515e | checkpoint-no-value | Beca
e7969c61-05a5-4d77-b7d9-33542bdf5e38 | signoff | Request Beca Signoff
55e54c13-6c93-4260-8333-5f310ed1414b | checkpoint-no-value | FIRP Signoff
2afc4135-b685-47fb-b0bd-c94d107dec53 | signoff | Record of Witnessing
e5e0a731-84e8-4fab-af1a-95bda944f901 | section | Commissioning
07109636-a9b4-4edb-8c8f-644d32569ed1 | checkpoint | Neutral Earthing Resistor Commissioning report
0aca99a9-0181-4a67-a34e-7912ef079858 | checkpoint-no-value | Mcconnell Dowell
c5fbe927-c7cd-42ac-ae55-a73471f4b02d | signoff | Request McConnell Dowell Signoff
58f8a757-47f6-4c21-aec3-fe0393d3aaa2 | checkpoint-no-value | Beca
bb6618c0-c9fe-4766-8289-287e8b3a61e7 | signoff | Request Beca Signoff
61ac4b2f-c079-4f46-a9e0-5af5b37e8c89 | checkpoint | Completion and Certification documents
65450c39-6fd3-4bc8-ac2a-10f9265d0868 | checkpoint-no-value | FIRP Signoff
fed85fba-bf7b-4be9-b6f6-53fd2d2910d8 | signoff | Record of Witnessing
df7ee2f3-b1fb-4590-bfa8-72e5846389e9 | checklist | Non Potable Water Tank |  | Equipment -
a6ebedcf-c45e-439a-a45c-5b4bc9a47667 | section | Pre-Commissioning
8f7ab699-69ca-47ff-a0bc-d2879816c643 | checkpoint | Tank Check Sheet
3a12a704-6e6f-4866-9ac5-2c912f3aed95 | checkpoint-no-value | Mcconnell Dowell
576b1aa6-e7a9-48c5-9335-4c2595d2cd71 | signoff | Request McConnell Dowell Signoff
c9b5ba2d-5f00-47cf-833a-baa593a6b161 | checkpoint-no-value | Beca
345bceb1-bfff-46e2-8780-ad01974d4115 | signoff | Request Beca Signoff
03e6f865-1921-4bf8-8ab2-6804d5cc5c00 | checkpoint-no-value | FIRP Signoff
af3fa137-0c41-4638-83bb-c4646efdb95f | signoff | Record of Witnessing
a2d9a313-3af7-4a63-a154-203e0e6e7477 | section | Commissioning
048ed9f1-babd-4f19-8e6b-7813ecd4571d | checkpoint | Tank ready for use
5dbdc040-431d-42f6-ba58-05b1fae5306e | checkpoint-no-value | Mcconnell Dowell
a90fc79c-60ac-4f00-945d-be271ffab196 | signoff | Request McConnell Dowell Signoff
0f348dbc-031d-4672-aa3f-5b71b231e45a | checkpoint-no-value | Beca
b9b7973a-54c1-4a7c-abe4-350ab2622b74 | signoff | Request Beca Signoff
69133cfd-401b-4da7-ba0b-43a4d8cefbb4 | checkpoint | Completion and Certification documents
3fd373a2-5eda-46a2-b406-1d9251ed3ecb | checkpoint-no-value | FIRP Signoff
ebd8d598-42e1-4170-8478-142a9b74ad6f | signoff | Record of Witnessing
0844ac77-712e-4580-8f14-e88a72201bad | checklist | PCMS |  | Equipment -
f2a4486c-7184-4799-8c12-abbbb725bde9 | section | Factory Acceptance Testing
8d7debca-c590-40f5-ba4d-c7fe59fc40b2 | checkpoint | Factory Acceptance Test Report
e5ad7eb0-db84-4323-bf55-8873e07fa1d7 | section | Pre-Commissioning
e19c50b4-7eae-4480-86d5-edc8db77c80b | checkpoint | PCMS Point to Point Testing Report
580821be-f113-4a6f-9224-8e4983526f65 | section | Commissioning
7d0d2166-624d-4552-aad6-7a9a881217ee | checkpoint | PCMS Commissioning report
b5bba6bf-aca8-461e-a651-742a91ad1601 | checkpoint-no-value | Mcconnell Dowell
9e10e930-714f-4632-a2ba-f0663e6ab814 | signoff | Request McConnell Dowell Signoff
f98bd5f5-a562-4c3c-9266-ecbcc6659066 | checkpoint-no-value | Beca
f22d7317-2ad2-4e18-8b70-7ac934ebf565 | signoff | Request Beca Signoff
ba85d337-3bea-4b7d-81d4-be4128cd99e4 | checkpoint-no-value | FIRP Signoff
f6e477b1-a65f-4d80-ac06-554f1378462d | signoff | Record of Witnessing
9b4177e7-d2f6-4e51-ad5b-b518008e33b9 | checklist | Pipework |  | Equipment -
929e1162-751d-4a57-8ce5-2c849af90c93 | section | Pre-Commissioning
0599ac44-2728-4247-b934-6f74eb837d15 | checkpoint | Pipework pressure test QA
c2db73eb-fd3d-45cd-b972-a98ea088bc7a | checkpoint | Flood Test
78491141-952d-4913-83f5-0de2eec181f8 | checkpoint-no-value | Mcconnell Dowell
3c6f084c-77d0-4ae2-b93b-bde50ca4c0f6 | signoff | Request McConnell Dowell Signoff
d3c8f5a4-39f4-47ba-9404-b627ac22aacc | checkpoint-no-value | Beca
23d74c3f-5d29-425e-a52d-ffbe5dd2c9bd | signoff | Request Beca Signoff
8bb34d2a-4770-44af-b38b-7d3e10f8bf3b | checkpoint-no-value | FIRP Signoff
60c16151-0823-49c8-b8ab-d33e504a97e7 | signoff | Record of Witnessing
5326ae65-cd60-4e40-a208-0360ae2b0058 | checklist | Pre action Valve set |  | Equipment -
aa9af901-e6b1-425f-9e37-fc9099cfc477 | section | Pre-Commissioning
5d4e943b-c7f8-4abf-a237-c4e308a4dab7 | checkpoint | Testing of Dry and Pre-Action Systems Form
57547a78-0777-4976-8f70-b658db9b09f2 | checkpoint-no-value | Mcconnell Dowell
a1684591-e756-449f-b1ce-ed262382b150 | signoff | Request McConnell Dowell Signoff
98442431-fa35-4d4a-bee4-16dbb11e8140 | section | Commissioning
eda19d3d-d3cd-40ac-92b6-939531fdab9c | checkpoint | Pre Action valve set functional test report
afee54db-321a-4d9f-82f4-944264294721 | checkpoint-no-value | Mcconnell Dowell
4f5facf0-13a8-4c05-8109-16ebf59ce6b7 | signoff | Request McConnell Dowell Signoff
597a4251-83d2-4d2f-a98e-a900cfea6249 | checkpoint-no-value | Beca
7209405c-96b9-450a-8a2f-7b5335f5d67e | signoff | Request Beca Signoff
b39e830a-1524-4ef8-87ad-80e0784bea2b | checkpoint-no-value | FIRP Signoff
8c12c654-ad29-41df-a089-e5c81350adb9 | signoff | Record of Witnessing
e724b6ec-a895-49fa-90af-f10d2ff01e38 | checklist | Pump |  | Equipment -
99caef22-e4c1-4f04-885f-3bd0b4a040e1 | section | Factory Acceptance Testing
2736e37b-59f4-4d12-a4eb-c197ced489a8 | checkpoint | Factory Acceptance Test Report
1496584a-7b6a-4cb0-bb24-f3294dc3d1cd | section | Pre-Commissioning
0ff9b96b-41b6-4fa8-98d3-b17bb96fb8e1 | checkpoint | Model Number
252d57a8-be98-5086-a96d-5d4c8de478b9 | textbox | Model Number
901ab030-7194-4921-bbbd-ac5cae7c50d2 | checkpoint | Visual inspection, no apparent damage
46eaa4b3-9d77-4203-a8bf-a84c7adedbd9 | checkpoint | Pump mounted on base and housing ok - no leaks
ccb063a1-1c67-4634-9f5e-17f7f35f159d | checkpoint | Alignment checked
fe8300a1-31f2-41f6-b6eb-8bd26f316668 | checkpoint | Coupling guard in place
7666ab23-a1f0-4c7c-9dc1-8add5e5f212d | checkpoint | Vibration mounts not bridged out or fully compressed
f9f331c8-a061-4c1d-aa83-a59b815b6d6f | checkpoint | Impeller rotates freely
0022b3fa-def2-44f5-8c85-779aaf93aa5a | checkpoint | Correct piping connections and pipework adequately supported
da8d5a2a-5f9f-4208-bfdc-c6947b9a4336 | checkpoint | Isolating valves installed in the suction and discharge lines
36573912-1248-4f55-95a5-16416771400d | checkpoint | Non-return valve installed in the discharge line
9c95f7d8-ac1e-4eb5-bf2f-fa92433a34f9 | checkpoint | Strainer installed and cleaned (c/w test port each side of strainer)
823dda74-d552-4a7e-9ae0-5f58c7a0bbe9 | checkpoint | Test points installed across the pump
901a806a-35fe-42be-9958-1996522192e6 | checkpoint | All isolating valves installed set in the operational position
f94148c2-063e-4eed-bdc5-a24351428101 | checkpoint | Drain with hose union installed
3188e6ba-0ba8-4449-b5cb-873c8e5555b2 | checkpoint | Pressure gauge installed across the suction and discharge lines
0d5ccfb9-6289-43ee-b6a2-84521cc8a49b | checkpoint | Flexible pipe installed at pump connections
593da8e7-4c6c-4b6b-9753-d0f822fb10c2 | checkpoint | Pipework flushing, venting and chemical treatment complete
6d06e7a7-6a16-4709-8173-4e2e0dc87b0a | checkpoint | Local isolator installed in accessible position
3c349cdd-f460-44f0-b3af-315300ffad1f | checkpoint | All power and control wiring correctly installed as per schematic
c9bae09c-b993-467b-9269-0c7c2ed71dcb | checkpoint | All connections tight
f08d68e1-0a98-41f2-b663-802c6929bf57 | checkpoint | Motor rotation checked
db78a333-e494-4f6d-8a5e-cb830a96d506 | checkpoint | VSD programmed and integrated with BMS
f40f09f3-39ce-4ffc-b7a6-f8fa1c0144d9 | checkpoint | Controls point to point checks completed
4532c6c2-1c9f-4180-804e-f4f21ccebbe1 | checkpoint-no-value | Mcconnell Dowell
f22c1764-406d-4b5c-843f-a318d7c5d3f7 | signoff | Request McConnell Dowell Signoff
39d8bfa8-4423-48bf-bfcd-602c81f7d17c | section | Commissioning
7b596b6c-3d76-4bf9-ad89-7404e1b3917f | checkpoint | Pump Commissioning report
c0ffd4c3-777d-48a4-b0cb-4970347bcdaf | checkpoint-no-value | Mcconnell Dowell
59fedd45-d204-4836-948c-6bf470f80f72 | signoff | Request McConnell Dowell Signoff
8ad1ec12-88ab-4137-8a89-c394bc956a76 | checkpoint-no-value | Beca
4eb9d127-552a-4656-8214-e1d87ae0fd1a | signoff | Request Beca Signoff
8cd780eb-1c9f-4428-999d-6e69e39fa6d6 | checkpoint-no-value | FIRP Signoff
9b9fbea1-59b1-4126-ab14-eb49c8fcf390 | signoff | Record of Witnessing
9776620f-b9e1-476a-843b-0fa739243383 | checklist | Room Release |  | Room #
90717708-0c91-440e-be70-6cc1585f5af3 | section | Room Location
df0d4da1-78fd-42df-b9c4-c0c91ed92c98 | checkpoint-no-value | Room Location
bccf7624-0d57-4f24-9c02-c69794ca24ed | section | First Fix
15fcb341-c644-4152-bc1c-8afc191449a2 | checkpoint | AQUAHEAT - Pipework
4b20b239-6237-486f-ab34-52639562b606 | checkpoint | AQUAHEAT - Ductwork
ff6974f1-c2e9-48f6-845e-9d415eabc9cd | checkpoint | AQUAHEAT - Electrical For Mechanical
1296e46e-1f02-49fd-9402-a95e382d1c1c | checkpoint | AQUAHEAT - Medical Gas
671355e1-c092-4a3c-9538-37884dcdfaea | checkpoint | AQUAHEAT - VRF
e42aae16-df9a-4796-9310-23c4cf3fbb4c | checkpoint | AQUAHEAT - Diesel
7b30cbb7-b8b3-42a4-90ce-c37d14bee424 | checkpoint | AXIS - Modframe
a69e2717-ef8d-4a7f-b46c-6b41afff770e | checkpoint | CLE - Containment
e5f85041-8d09-4723-9ccd-64de1282fae5 | checkpoint | CLE - Power & lighting
be0e0047-1129-4dd5-871c-e7e9b478de86 | checkpoint | CLE - Switchboards
0822518e-ee7d-442d-a14c-cd8f151f8db7 | checkpoint | CLE - HV
9906f0a0-fa54-4ebb-b5a3-bf190b96a9a4 | checkpoint | DL GOOD
a9939768-c488-4157-906d-4a5028a67c8e | checkpoint | TRIANGLE FIRE - Sprinklers
2e578279-0f75-48a1-8754-beac72b35d27 | checkpoint | TRIANGLE FIRE - Alarms
81a7e7b8-cf1b-44e0-9e60-d0bf0148a056 | checkpoint | SACO
c1c1b098-8bba-4bfb-8e93-f47ce905adcb | checkpoint | AOTEA
0ce9901a-efef-4955-9201-54c77f18f21d | checkpoint | FILTEC
a54700e8-27c7-46f6-aa79-f3726dd3d183 | section | Second Fix
57f72853-7f01-4b10-a65e-aec2d51d08bf | checkpoint | AQUAHEAT - Pipework
d75f90ca-67db-4a2d-ad17-cef21d9e42e7 | checkpoint | AQUAHEAT - Ductwork
d5de08ed-96f9-4209-9e1a-1f26e7e6b612 | checkpoint | AQUAHEAT - Electrical For Mechanical
e0851de3-3abf-4a89-bfe4-6aeeac28378e | checkpoint | AQUAHEAT - Medical Gas
422f8c9d-c6d7-4341-8264-95872d66b9e9 | checkpoint | AQUAHEAT - VRF
9ea8e262-72e1-4d75-8de5-a21734447cea | checkpoint | AQUAHEAT - Diesel
aa6c1f57-efab-4100-ac33-839220830036 | checkpoint | CLE - Power & lighting
67c75f66-94cd-4d39-9e81-ba73a1ef4b0e | checkpoint | CLE - Switchboards
c50bdc1b-aef9-47b2-8629-3c3d733b7ed7 | checkpoint | CLE - HV
40b615c0-a2a2-4d98-ab59-0415368299a7 | checkpoint | DL GOOD
93633da5-b85c-4d0c-92d7-3b24cfa25392 | checkpoint | TRIANGLE FIRE - Sprinklers
ae6bc71d-d9c0-4ecf-93d9-2d8cf895a580 | checkpoint | TRIANGLE FIRE - Alarms
7a8877a7-f04b-4a92-8025-53e6e3ea0e8b | checkpoint | SACO
d6ef81b3-5aa3-43b2-93ce-80de0b9b6550 | checkpoint | AOTEA
f57bd478-31a4-46a1-b290-a1c62ab8d775 | checkpoint | FILTEC
d567b5f2-feb0-43b1-9af5-69512c814243 | checkpoint | GLOBAL FIRE
2387e4b9-f7a3-4110-9b7b-62b68b604a3b | checkpoint | CONTRACT COATINGS
ef24f18a-be26-4091-aa91-cc54debf948c | checklist | S01 - Corridor access controlled doors release on fire alarm activation |  | S01 - Corridor access controlled doors release on fire alarm activation
3133e379-48b3-412b-9b6e-7b04c1676ea4 | section | IST Test
6a20630e-afca-4d3f-915e-5d2acd684445 | checkpoint | IST Details
7988083f-d100-564e-b55b-7b9418137908 | textbox | Test Method - Activate A40 MCP
521a041c-c580-5d4a-a893-46f6e481ac99 | textbox | Area - A40
c8ab9bdd-0b33-4f83-be81-519a35e049a9 | section | First Test
43be6436-5a0a-483f-9792-9cf6a2e4d16c | checkpoint | Fire - D.00.056A
6640e2a9-8cb3-4b64-bc71-77b9d7f620d3 | checkpoint | D.00.057A
a0595e51-83fc-4bd5-910c-b6c93c2baad6 | checkpoint | D.00.027A
0cf68291-bdff-4da8-b3ec-1f7f1cda8840 | checkpoint | D.10.056A
c836631f-4c08-46bf-ad0e-2c6f7f4bb056 | checkpoint | D.20.056A
1c71d5bd-5b4a-4c8a-9e6c-bf390b7ba0b6 | checkpoint | D.20.027A
e0a83020-dc43-41d6-83d1-0bc5a9cbb668 | checkpoint | D.30.056A
95080478-e77d-4817-99c0-1f0fe976dbf7 | checkpoint | D.30.041A
781039a3-3389-4d16-b28b-da18562023a0 | checkpoint | D.40.056A
8f8ce98d-a2c0-4afb-905b-7f65d83fe721 | checkpoint | D.40.041A
7688ac10-a337-4ac5-9061-ad6832e3a305 | checkpoint | D.50.056A
5d5fd795-5c10-46c8-a244-0634842cfd12 | section | Second Test
6d2f20dc-2957-4c30-aa7c-c7ce24b95a66 | checkpoint | Fire - D.00.056A
892fc401-7b0a-46b5-956c-f869b8637c50 | checkpoint | D.00.057A
dd2ec6e1-83fb-4136-be05-69b7a4bebe37 | checkpoint | D.00.027A
1bf38599-a524-4ff6-b210-528107859172 | checkpoint | D.10.056A
2ea0cc1b-43b7-48d6-a4ab-57c641cabc30 | checkpoint | D.20.056A
c5a25a5a-8021-420f-b6e1-3949aa818a99 | checkpoint | D.20.027A
74a1fec2-af33-4305-a71a-5e22f871d769 | checkpoint | D.30.056A
5c18bade-f03f-40b7-a3c9-5e5a5972e348 | checkpoint | D.30.041A
a07176c2-d82b-40bf-8b8a-4b21a3999605 | checkpoint | D.40.056A
521e5110-df47-43b9-a943-19eaafd04598 | checkpoint | D.40.041A
903c2759-c921-4732-bfa3-9436820d6468 | checkpoint | D.50.056A
45f8f4a8-521a-43e3-a0f4-ff235ce963f0 | checklist | S02 - Level 0 Comms Room (A40.00.032) Door releases on Pre-Action Stage 2 activation (smoke detector + Sprinkler) |  | S02 - Level 0 Comms Room (A40.00.032) Door releases on Pre-Action Stage 2 activation (smoke detector + Sprinkler)
4f0d5560-fdaa-4852-b1d8-22893204d1c2 | section | IST Test
94fd2960-b4df-454d-bc63-f761885ddba5 | checkpoint | IST Details
ba5cd3b2-34da-5df3-b4ca-d5f9aa55e752 | textbox | Test Method - How will this be simulated?
57b3c8e6-8edd-56cc-b8a7-6bcd78391721 | textbox | Area - A40
486efc7a-8a87-4140-9ae2-11c2eb82538b | section | First Test
d3076a1c-56d4-49fa-9a16-113c7da4fbe2 | checkpoint | Fire - (A40.00.032) Door releases
8c65dc55-d3bd-4ba8-85b0-5294bdcbdaa1 | section | Second Test
a85bbc02-8976-42e5-a258-8b4bc12faef8 | checkpoint | Fire - (A40.00.032) Door releases
07574cc9-4135-4fc1-be83-97607f71e6ef | checklist | S03 - Level 3 Comms Room (A40.30.034) Door releases on Pre-Action Stage 2 activation (smoke detector + Sprinkler) |  | S03 - Level 3 Comms Room (A40.30.034) Door releases on Pre-Action Stage 2 activation (smoke detector + Sprinkler)
35ed0aa8-50a1-434f-86e9-cc4cb18932f0 | section | IST Test
e3769e02-45c3-4836-903c-587547cbd166 | checkpoint | IST Details
360e0d18-c819-5cba-982f-2a3b992448aa | textbox | Test Method - How will this be simulated?
ac98a0f9-7ea4-5859-9347-cf41150b6ec3 | textbox | Area - A40
3a493422-4c6e-4a63-bf8a-e544a4765f7c | section | First Test
7416a529-773c-4f90-a252-55db46364650 | checkpoint | Fire - (A40.30.034) Door releases
a14db1de-ce1a-4f5e-8edd-54989c704198 | section | Second Test
c6aa3722-0711-493b-bfa8-0cf632de1733 | checkpoint | Fire - (A40.30.034) Door releases
d1dc188d-b9c7-4eab-b918-e60cff5d3caf | checklist | S04 - Fire Intercom operation under tunnel fire condition |  | S04 - Fire Intercom operation under tunnel fire condition
dc34e7b2-2050-424b-bad4-309fb0219871 | section | IST Test
4996c4bb-ce89-4681-9bc3-da580d426d13 | checkpoint | IST Details
21bb0b27-d76b-5978-82ee-e2e6bbba628f | textbox | Test Method - Activate tunnel MCP
2f2e9fd9-d233-563f-b9d7-f6fd653f6bcf | textbox | Area - Tunnel
a9f9997b-56bf-4d90-b4d7-203ae6c26c1b | section | First Test
6f2117a0-3576-4334-9ebc-41cddab3f488 | checkpoint | Fire - Verify fire intercom operation and inter-unit communication per the Fire Intercom commissioning and testing procedure.
8f9a8b8b-e3d1-40fc-a658-de49bbbfa846 | section | Second Test
c96a42d0-c7bc-41d6-be42-82809df14fe6 | checkpoint | Fire - Verify fire intercom operation and inter-unit communication per the Fire Intercom commissioning and testing procedure.
731c2336-cbf9-4dcb-9b1b-8db2e44b1e4c | checklist | SCADA |  | Equipment -
8e5f7dc3-fe5a-4754-a15d-1294b80a9101 | section | Pre-Commissioning
52c29634-5d92-45ae-bf20-ec2b20977c8c | checkpoint | SCADA Point to Point Testing Report
6551585e-282d-42d4-8722-5d1842977c25 | section | Commissioning
609b95b1-12a6-410e-87e7-58783bb93224 | checkpoint | SCADA Commissioning report
033712df-7a91-4c64-83cc-8102bb9ed9c0 | checkpoint-no-value | Mcconnell Dowell
fd2f5c05-283d-42af-b989-d8f8bd94efbd | signoff | Request McConnell Dowell Signoff
e6dfb371-1738-405a-9561-d821651f0bfc | checkpoint-no-value | Beca
8e8979bb-7685-4907-afb2-04815785634d | signoff | Request Beca Signoff
515be0ab-8fb4-45a1-b8ac-6e7edea6a7a6 | checkpoint-no-value | FIRP Signoff
3be551d1-9a7b-4daf-bd1b-e51238e7c2b7 | signoff | Record of Witnessing
68532888-81fb-4532-b849-f814ab1a25aa | checklist | Security Panel |  | Equipment -
2a5d670d-5bdd-47d3-ba93-669fe247928a | section | Pre-Commissioning
ff664719-7084-40e6-9e7c-88c85f117f77 | checkpoint | Precommissioning report
486c27d2-a8fc-45b7-b9fb-eb184d65ee8d | section | Commissioning
2c972915-e699-485b-ac96-42411dc20ffd | checkpoint | Commissioning report
ce93e520-8802-4698-acc7-31f58c04b16f | checkpoint-no-value | Mcconnell Dowell
6465b589-a28b-4233-9fd9-51130318242d | signoff | Request McConnell Dowell Signoff
bbb24bbd-de28-4f8c-8eba-c6f49e4cf947 | checkpoint-no-value | Beca
cb82e6a1-e889-4aaf-b071-4066e17f4442 | signoff | Request Beca Signoff
7add7b00-1d51-414f-adb4-345826db2dca | checkpoint-no-value | FIRP Signoff
ed52933f-3361-4697-8452-50d9ad41cb82 | signoff | Record of Witnessing
1c5579ba-9de2-49db-a5ee-4116a175e24a | checklist | Service/Passenger Lift |  | Equipment -
5b6784a6-6ade-4c0c-b60d-1ffab46f9414 | section | Pre-Commissioning
16b51148-3dc1-4b87-b575-eb89b8dfe41d | checkpoint | Pre-Commissioning Test Report
ca70b1bb-96ef-47fa-9c04-3861bf0fb471 | section | Commissioning
2fbd2169-bb62-4b34-933b-698c9196b440 | checkpoint | Commissioning report
f3527716-8634-4680-87fb-168fb10a9148 | checkpoint-no-value | Mcconnell Dowell
0dfa4192-5927-4bf7-8d03-49fe5a3dd468 | signoff | Request McConnell Dowell Signoff
cf18c80b-2e4c-42a7-ae24-fe3516bfc2b4 | checkpoint-no-value | Beca
8adabcb1-2228-4046-8b70-37ca30ae91b4 | signoff | Request Beca Signoff
729e4ada-b0b4-4f05-809b-99a666062098 | checkpoint-no-value | FIRP Signoff
fbe679ed-15c7-4b5f-af0e-a95e2442d649 | signoff | Record of Witnessing
36418cf4-0438-47b7-8443-321e4dfd287d | checklist | Split System |  | Equipment -
5f352b55-0643-43b6-ab8a-400e72a18199 | section | Pre-Commissioning
2b5e854d-fdfc-4188-bc57-65d8e4967768 | checkpoint | Electrical Testing
e2a37628-8ae5-4649-ac8a-dfdd11278a67 | section | Commissioning
fe995d14-7a44-4b00-80f9-204281bdfa6b | checkpoint | Test Sheet
c11333e3-1bf2-4c0e-9ef2-d45958c381b3 | checkpoint-no-value | Mcconnell Dowell
e6691a9b-a818-49d5-9ba1-2d938ffe376d | signoff | Request McConnell Dowell Signoff
1a0b4186-0c9c-473a-a812-01616b679eb8 | checkpoint-no-value | Beca
c6287d47-4a71-4cca-b8c0-0a926361f1f6 | signoff | Request Beca Signoff
80cfe088-5b41-4841-b366-6f24f810b2f6 | checkpoint-no-value | FIRP Signoff
55ebea29-19e1-4073-994a-e0c32fd005f2 | signoff | Record of Witnessing
cd3f9ae5-69ad-4c04-b186-3b34f760be2c | checklist | Sprinkler Pipework |  | Equipment -
47f64d8a-d358-426d-b2d2-cef79e32035c | section | Pre-Commissioning
1b69a209-090c-419e-b2ab-eee7070ee782 | checkpoint | Monitor Valve Check Sheet
02a902ba-aa86-4c81-9acf-e79718c483f3 | checkpoint | Testing of Dry and Pre-Action Systems Form
f9c72591-34d3-4b7a-80d5-500c4260bee6 | checkpoint | Sprinkler Flow Switch
2e59a072-8ecd-4f82-ae35-0f6441e358dd | checkpoint | Flow switch test form
6da52bdc-cc06-40f4-8288-ceb4b41ed956 | checkpoint | Hydrostatic Test Sheet
2b0159e8-af39-4deb-960d-cde095620e36 | section | Commissioning
bed7baf3-4f86-45a4-b447-bdf38e9f1217 | checkpoint | Sprinkler System Commissioning form
c82fa50f-4c15-4c5f-aeb7-b344de48f129 | checkpoint | Sprinkler Commissioning report
37ef07d6-9bd9-4528-99dd-bc0294020291 | checkpoint-no-value | Mcconnell Dowell
2a373563-44f4-44a5-8873-77e2a8102a16 | signoff | Request McConnell Dowell Signoff
577bead5-94c1-45ee-b2b8-3bd181b6d3bd | checkpoint-no-value | Beca
cfd9cb1c-ef0f-447d-a722-d2c27374389b | signoff | Request Beca Signoff
127f217d-9fa4-4ead-8899-52f53522716c | checkpoint | Completion and Certification documents
52d43c2f-0d51-4c99-bcb4-c695f54499e0 | checkpoint-no-value | FIRP Signoff
1fa1fe96-2eea-48e8-99af-d0c001b857c0 | signoff | Record of Witnessing
cd974274-7630-4dd8-b494-a10b5ee8e68b | checklist | Stormwater Drainage |  | Equipment -
14181843-a7a5-4e7f-a517-e7fe2e5ceed6 | section | Pre-Commissioning
8c71d3d5-d393-4ed3-a429-216ae71ed733 | checkpoint | Flood Test
8d592c13-626b-4b8b-acff-e28c7c051c6c | checkpoint-no-value | Mcconnell Dowell
e54692e2-b148-47a8-b854-ed7e2c52be70 | signoff | Request McConnell Dowell Signoff
586bb621-ae4b-4c24-90ec-d0cd8e1dfed9 | checkpoint-no-value | Beca
88b560f3-b342-4255-b2cc-838980c0a9ae | signoff | Request Beca Signoff
31b34e9c-fed9-4109-8996-0f44779aee00 | checkpoint-no-value | FIRP Signoff
c62b9c90-b896-4a2f-8739-923e2225cf7a | signoff | Record of Witnessing
68680755-c452-4800-9ad2-4e1ec3349b69 | checklist | Transformer |  | Equipment -
fda970c3-8f35-4df5-adee-28fcdab71b6f | section | Factory Acceptance Testing
5cd95884-9642-4210-ab8f-072e74bc37e4 | checkpoint | Factory Acceptance Test Report
f12bc9cd-9642-4675-832b-32cd1161060b | section | Pre-Commissioning
aa91f803-f4e0-4bf0-bbb7-3932e771a54c | checkpoint | Pre-Commissioning Test Report
97eff089-65da-4b13-a548-5713d8dee0be | checkpoint-no-value | Mcconnell Dowell
3acbf60a-abd6-4a1f-b82f-8d83c35513aa | signoff | Request McConnell Dowell Signoff
fe9bd417-b784-4cc2-9dd0-16437880bcd7 | checkpoint-no-value | Beca
c8309c13-1dfd-45df-8cb3-ac750bb7de72 | signoff | Request Beca Signoff
3bacc7bf-a57d-4ba9-a9e2-a6c0fee57463 | checkpoint-no-value | FIRP Signoff
da84f56a-88a6-4ee0-8312-1cc8d10b1021 | signoff | Record of Witnessing
84f425d8-6f0a-4981-8379-60873dc941d3 | section | Commissioning
a61f220e-a404-4eb1-a21a-c5490ad8cb82 | checkpoint | Transformer Commissioning report
6f54868a-ca88-4928-942c-3e655a5df976 | checkpoint-no-value | Mcconnell Dowell
8c628096-330b-4549-8ab3-ae48589744f3 | signoff | Request McConnell Dowell Signoff
5c1aba8b-54fb-4f61-bbff-cecd0c809b48 | checkpoint-no-value | Beca
6950a85d-5118-4a60-adb2-9ce1464e1ecd | signoff | Request Beca Signoff
af380d74-5e59-49be-900d-433c34f1fa89 | checkpoint | Completion and Certification documents
c364a7de-73c3-4b2a-a83c-09b262f6ad4d | checkpoint-no-value | FIRP Signoff
72ac390a-1aa6-4647-b483-c1d23ef26fc8 | signoff | Record of Witnessing
07e0898d-b236-4692-9d07-554099ef2346 | checklist | Tunnel Occupant Counter |  | Equipment -
a9116d8c-f006-4533-94fd-650d45b2a464 | section | Pre-Commissioning
0d9526c8-778c-4ca1-bb4e-a71b980c6347 | checkpoint | Precommissioning report
1f04d0ee-2213-40e5-a542-e205f7d63517 | section | Commissioning
e0945759-bd66-4047-bdb7-510bdf82cace | checkpoint | Commissioning report
c38e86ec-cd13-4554-9010-dcb316144a19 | checkpoint-no-value | Mcconnell Dowell
b998db28-4abc-406b-95f8-471d1b307fb8 | signoff | Request McConnell Dowell Signoff
f7e60dd2-5800-43dc-9f73-289ba48661da | checkpoint-no-value | Beca
f4ec4a42-0f1f-42b4-bbf3-6813b5edbf1a | signoff | Request Beca Signoff
f47d757a-bf33-4678-9cf1-6eae9c9b3138 | checkpoint-no-value | FIRP Signoff
268aaa5c-857e-41d1-8cbf-b77074c5cff9 | signoff | Record of Witnessing
d32c82e8-0c63-458c-aa14-3de61f9af0da | checklist | Vesda |  | Equipment -
eb83546b-8365-42c4-b9f9-8e4007c3bd46 | section | Pre-Commissioning
1a8c06ff-5c1d-4a21-91db-c87d8fefe60e | checkpoint | Pre-Commissioning Test Report
98108ff5-0287-47f4-b100-820d6d890db2 | checkpoint-no-value | Mcconnell Dowell
9abfedb8-7f85-4709-a056-4d221a8abc09 | signoff | Request McConnell Dowell Signoff
9357dd92-f4fc-43dc-a7aa-d6cebaa691ba | section | Commissioning
e7dea31a-4b2f-46fd-ba41-1537e0bddc6e | checkpoint | Vesda Commissioning form
40cb80b5-a962-4563-b6a6-ccc4a2bbb73f | checkpoint | VESDA Plus Detector Commissioning Form
1681fef9-749c-4528-8b79-76e4df2a2982 | checkpoint | Vesda Commissioning Forms for Stage 1 and Stage 2 activation
a1dbffd1-ccf4-47bd-b850-0cdbbf0cfce4 | checkpoint | Display/Relay Configuration
65cf97b0-fdd2-4677-8df3-c45df939442d | checkpoint | VESDA Plus Relay Configuration
4b1a0ae1-6ee3-40ef-8649-bd8fc63a425a | checkpoint | VESDAnet Interface Card (plug-in)
1a872b6c-a37f-4ae4-94d1-eaf1a0e68818 | checkpoint | Ancillary Devices
35497025-9ccf-466b-8830-ceb2c351431a | checkpoint | ASPIRE2 Data
0f6747f6-9b0a-4f5f-b5a8-5224a0f8dbd2 | checkpoint | Air Sampling Test Results
e0e936dc-0f73-4c43-ac74-10d653deb765 | checkpoint | VESDA Commissioning report
bcc75cfd-bc04-4423-9fa8-fca3d6362af6 | checkpoint-no-value | Mcconnell Dowell
f65f8d34-db28-4009-960c-1f4704553f35 | signoff | Request McConnell Dowell Signoff
ab469604-2c25-429b-9923-615fcf566a8c | checkpoint-no-value | Beca
bd139975-b485-4314-91f0-f4564bc1661c | signoff | Request Beca Signoff
1935f688-9da7-41ac-b8ef-3fa296302778 | checkpoint | Completion and Certification documents
ee6fa2fc-0004-4e39-beff-97f95bf1f548 | checkpoint-no-value | FIRP Signoff
11221dd6-60eb-414f-a816-f826938fa6c7 | signoff | Record of Witnessing
de8c643c-b5df-44a5-be8d-8feb216a7aa6 | checklist | VRF IDU |  | Equipment -
3c147249-88f6-4bbf-8a19-049fbd1c053e | section | Pre-Commissioning
cc709bcd-d30e-4996-87aa-92a8bd3823a6 | checkpoint | Electrical Testing
0764be38-c723-44fe-a604-902116601d28 | section | Commissioning
79240054-c42d-4e12-b0b5-235be923ceda | checkpoint | Electrical Testing
0e054c46-693b-419c-8932-166eec87d472 | checkpoint | Airflow test
9a5524a8-c154-4d67-ab41-f9d1b70729ee | checkpoint-no-value | Mcconnell Dowell
4a8278ed-c080-44c9-a69e-f750d1bbbbe5 | signoff | Request McConnell Dowell Signoff
7f3ec269-f879-4645-bf28-3c29ca52d552 | checkpoint-no-value | Beca
4f9a218a-dc4b-4b33-aa45-cebf077cbeb7 | signoff | Request Beca Signoff
688ee07a-46b5-4217-8488-d05010f98451 | checkpoint-no-value | FIRP Signoff
0bc7dcd1-f1a7-48af-bfa7-ed3b0582e1bb | signoff | Record of Witnessing
97db41ae-337a-4671-b714-2d970a0964ef | checklist | VRF ODU |  | Equipment -
0d3f3b95-db16-48a1-b30d-184a78128eea | section | Pre-Commissioning
6a6c9b92-3728-4d04-9852-eea27ffb8e23 | checkpoint | Precommissioning report
b34c2d4d-cb4d-4e45-8ae0-3c21f7fb6641 | checkpoint-no-value | Mcconnell Dowell
cf568b29-4944-4d1d-b8c3-83b76b959d7c | signoff | Request McConnell Dowell Signoff
08669cef-0f30-41d8-9eb6-662019616743 | section | Commissioning
e6b11f03-26b0-45ad-878f-b57bee87ca66 | checkpoint | Commissioning report
f76fd57d-e3f2-4bcd-b188-e76e444d1736 | checkpoint-no-value | Mcconnell Dowell
ddd8dcdd-2f4b-425b-91ac-67467412b3ef | signoff | Request McConnell Dowell Signoff
ebe46f2d-6985-48c4-be90-50cf7137b75c | checkpoint-no-value | Beca
1b1b1570-17c5-4d1d-8883-4a232acd95d0 | signoff | Request Beca Signoff
6ce56abf-e0fb-465a-939f-0dcbf0e0bc31 | checkpoint-no-value | FIRP Signoff
a63d85aa-492d-4903-a9ea-af2edc72bbf6 | signoff | Record of Witnessing
52f2bb90-3b86-4030-b9ba-a294da6b5266 | checklist | VT01 - Building Wide Fire Alarm |  | VT01 - Building Wide Fire Alarm
158320db-fe06-45af-a038-d882f3199031 | section | IST Test
354becfb-3ce2-4fd4-9eb0-ef8ed510005c | checkpoint | IST Details
9af2bb43-b6ec-5c91-9d8f-edbfe0c7d668 | textbox | Test Method - Activate MCP
49c00b05-864e-551f-a13d-f36b30a5d92b | textbox | Area - A40
cbd81a54-a9df-4e4f-86eb-56c53c9f11ad | section | First Test
1d5aa84f-3152-4e04-8283-8901d89daee9 | checkpoint | Fire - Lifts return to Ground Floor
b3ccc9b2-b004-4f1c-b1bf-312adf78a575 | checkpoint | Fireman Lift recalls operates
efce6718-55f9-4e5a-b1e6-925720b6a466 | section | Second Test
731d470d-67c5-41ed-a17e-acef7bf8c68d | checkpoint | Fire - Lifts return to Ground Floor
3a5393e3-ace7-412a-9e09-04298e05df1c | checkpoint | Fireman Lift recalls operates
a3de8e12-e314-4da1-8633-52dd44348fbd | checklist | VT02 - Fire Alarm level 0 Lift lobby |  | VT02 - Fire Alarm level 0 Lift lobby
cfbe716e-43bc-4871-a37e-0463f4edec35 | section | IST Test
fa104709-112a-4466-a3e0-3e4ae276a450 | checkpoint | IST Details
579e2b08-426a-5062-99b9-747998276618 | textbox | Test Method - Trigger Smoke Detector in L0 lift Lobby
281e3357-58a4-5b38-b4e3-c13cd7c59e17 | textbox | Area - A40
2265c229-3df8-415c-a869-2da8b3f63a25 | section | First Test
bc1c3ee5-ed20-4198-81c7-0c0f0fa5408e | checkpoint | Fire - Lift returns to Level 2
8540beda-51e3-43e2-abbf-b19118b394e1 | checkpoint | Fireman recalls operates
7586c1de-3708-4acf-89d3-ebf8dcafd3c9 | section | Second Test
eca1020d-e910-4aaf-82a4-a056185d1f74 | checkpoint | Fire - Lift returns to Level 2
bbcffcca-3cb2-42fc-977a-2cb90cee4d9a | checkpoint | Fireman recalls operates
ec50cb04-2010-4550-8053-4a9047542f4d | checklist | VT03 - Authorised Lift Access |  | VT03 - Authorised Lift Access
b915c85b-fd9b-4a39-a0ac-21bc8d387719 | section | IST Test
d4dc1d03-5cf4-426a-9048-cc0ed98c71df | checkpoint | IST Details
45e2c657-d8c3-5c70-b429-8ba054e9fac0 | textbox | Test Method - Access lift and floors using authorised access control card
1d80f92d-8550-5c21-a1cd-564e73375653 | textbox | Area - A40
060b8c50-dcff-465e-9a75-785414f9c931 | section | First Test
27824e86-5c6f-48c2-857b-dfcf40e36a54 | checkpoint | Security - Access to lift and floors
29a4be9a-2845-4387-a637-2e66dbef8715 | section | Second Test
301ae85d-f2c4-483a-a84e-3fe2af03ea62 | checkpoint | Security - Access to lift and floors
ddb2c535-605e-44fc-8e6c-ed0b3abb1187 | checklist | VT04 - Unauthorised Lift Access |  | VT04 - Unauthorised Lift Access
e28e9cb2-26b0-4c95-99ca-564982adaf4f | section | IST Test
9c5baeee-a0ca-49c3-b2b7-f09bd1447baa | checkpoint | IST Details
a4d89c56-ed4d-5088-95e3-aa70e9b516a7 | textbox | Test Method - Access lift and floors using un-authorised access control card
9f3d3ed1-1b9e-547a-b6ce-749cf0b52cfb | textbox | Area - A40
ebdc9362-91aa-4994-8995-45384df253fa | section | First Test
f8c0e9a6-0142-498d-9512-98e9cf45e6a3 | checkpoint | Security - Access to lift and floors Denied
be6a6c68-1865-4186-b620-941b65c162a6 | section | Second Test
85592171-98c3-447e-9415-6d0757d5daaa | checkpoint | Security - Access to lift and floors Denied
de956b46-e5c0-47f6-9876-323e3811a18c | checklist | VT05 - Passenger Lift Alarm |  | VT05 - Passenger Lift Alarm
d2b953b1-b924-44c1-a607-8567446b0ba2 | section | IST Test
36c99e30-ff39-4459-9406-0a81fffac102 | checkpoint | IST Details
a34965de-6fd6-5daa-8615-56290385101b | textbox | Test Method - Trigger Lift alarm A40-05.0-P-001
266bee4a-321e-5faf-a0bc-0d6c7ad4fee6 | textbox | Area - A40
407d3f5e-60c4-4c9d-8820-957f183282bf | section | First Test
65510348-b878-412a-960f-8c722563f9fc | checkpoint | BMS - Passenger Lift Alarms Indication at BMS
f5e359ff-74d6-4efc-8af8-6fbe47e861e7 | section | Second Test
40fd2c0b-4bfd-4a32-8b24-59f7aaaeb104 | checkpoint | BMS - Passenger Lift Alarms Indication at BMS
28570121-73a4-48ec-addd-47a9a523af94 | checklist | VT06 - Goods Lift Alarm |  | VT06 - Goods Lift Alarm
ba30e7c3-e8f3-46e8-8b08-812907ef0ee9 | section | IST Test
b110dff7-0349-4be4-9da3-412379957c27 | checkpoint | IST Details
78cfcca8-3c64-56ed-a417-45ceb0a7b755 | textbox | Test Method - Trigger Lift alarm A40-05.0-U-001
b20130df-31db-545e-ba50-3dcf60a58c18 | textbox | Area - A40
f9fd184a-3df3-4a39-aff7-4a792b3c5d17 | section | First Test
01b9177e-1af4-431e-9f91-f136ec192058 | checkpoint | BMS - Goods Lift Alarms Indication at BMS
925c04b8-0ab1-4a43-b6f6-2659c67d68a7 | section | Second Test
bc6beca5-1385-48e6-b240-0a36b5804af8 | checkpoint | BMS - Goods Lift Alarms Indication at BMS
0bee9d95-438a-40ad-ad3c-21415169dfdb | checklist | VT07 - Emergency Lifts |  | VT07 - Emergency Lifts
5f6e917b-edc8-48e9-bea1-8d9cc7a20fba | section | IST Test
ab6e921d-9fe8-4a60-b9c6-fa300986e522 | checkpoint | IST Details
9fc56711-d8fd-5865-8544-5cdf1c59c56d | textbox | Test Method - How can this be simulated?
53d4ef0c-f6f8-5b92-91b3-4c3ae8c03980 | textbox | Area - A40
6a7654b3-02eb-4be5-9ee4-80904c4c5e71 | section | First Test
7eed7e79-5c1e-4a51-8c7d-69b9af7348c8 | checkpoint | Monitored by site wide emergency lighting system
706e6d3d-4f60-4056-8fdf-37c68bad7fb7 | section | Second Test
3fb0ecc5-ca70-41b1-afa8-55d16ee2fba8 | checkpoint | Monitored by site wide emergency lighting system
482673ae-d239-4e52-b6c7-7298b36468fa | checklist | VT08 - Data link to lift car |  | VT08 - Data link to lift car
487e6b06-614f-4b29-a792-06d89b14bef6 | section | IST Test
ff92328f-7a4b-48cc-8975-465f79d00350 | checkpoint | IST Details
705da47c-d573-59b7-b205-a6f2c6e44c45 | textbox | Test Method - Remove data connection from lift cart?
99050e1b-284a-5464-b94e-2903b629ec0a | textbox | Area - A40
3250beed-64ff-4c2d-956c-4e5c34a85f0d | section | First Test
7f0f0488-6963-4f32-b1eb-09d02286a0f7 | checkpoint | Data - Performance of combined data link
754bbd71-633e-48f0-89d2-5c684ac629fc | section | Second Test
e9fc9e46-29de-45e0-bc04-2964bbb29e13 | checkpoint | Data - Performance of combined data link
7406d78f-b0c1-48eb-ae4c-48a920086328 | checklist | VT09 - Check sequential starting of lifts on return to mains |  | VT09 - Check sequential starting of lifts on return to mains
2f83c7be-dec2-461d-bd98-195331621007 | section | IST Test
bf05739d-9768-49e7-a94a-14184284295b | checkpoint | IST Details
de4c8666-b503-5cd3-8c6f-0e0f7fd2a9d6 | textbox | Test Method - Remove power test generator and switch back to see seqeuncial starts
7a5d1e89-7f2b-5ccf-9fd5-c4c06439d6c3 | textbox | Area - A40
25af9e68-6985-4d0e-bb07-959de2076c72 | section | First Test
a65689c3-8969-4c5b-ab99-2591cd83773a | checkpoint | Elec - Sequential starting of the lifts on return to mains
644946a7-9a17-4dc6-a40a-784f2691f9f5 | section | Second Test
6a2d3a2c-9876-4444-aa5a-c5cb93ac6e6f | checkpoint | Elec - Sequential starting of the lifts on return to mains
96bb6ea3-cc17-4648-9ff1-188eda566a29 | checklist | Water Treatment Pipework |  | Equipment -
64e71039-05e8-4a66-a99a-c9dbe2483a86 | section | Pre-Commissioning
d35a6a45-46ce-420b-a76f-b591c87fcd1c | checkpoint | Pipework pressure test QA
afdbcdb0-0251-461e-a1fd-19e029f325a5 | checkpoint | Disinfection QA
b5264268-611a-4ae4-86d1-26cd1107ccce | checkpoint-no-value | Mcconnell Dowell
db82a5b0-8ce7-4a95-80ae-b38f235ceff1 | signoff | Request McConnell Dowell Signoff
b1feaec1-e5bd-40c3-a028-d79d9b339e92 | checkpoint-no-value | Beca
bcaffac4-240a-4b20-afb0-2d6130dd356c | signoff | Request Beca Signoff
e8d24966-ff4b-47b1-89f4-b9646c0e5028 | checkpoint-no-value | FIRP Signoff
bdbd2f49-e8e4-481a-aafc-dc5811098c2d | signoff | Record of Witnessing
5dede9ad-376f-441c-a8ce-c97bc9d41e28 | checklist | Water Treatment Plant |  | Equipment -
5fe8a23d-5f37-4962-b8d2-9447df888a7a | section | Pre-Commissioning
253089f6-27b5-47f3-a945-3031ed851dc8 | checkpoint | Piping check sheet
84db6cba-3384-4d26-ba22-1f01aed55f36 | checkpoint | Manual Valve Check sheet
630f59f5-00ac-4cd5-8dbd-6d8403b1370e | checkpoint | Automated valve Check sheet
7b7b41a0-d421-43bd-beb1-3665939ee7ba | checkpoint-no-value | Mcconnell Dowell
6b6e3fe6-2f8f-4d09-9370-6011c32b18ba | signoff | Request McConnell Dowell Signoff
13c9a103-a263-4e32-a6e4-09defa058212 | section | Commissioning
25ec5899-896e-43ed-8d63-70cd06f2da8b | checkpoint | Instruments- Switches Check Sheet
66e39839-41b3-4f96-847e-2956d1bb0c9e | checkpoint | Instruments - Sensors, Transmitters and Analyzers Check Sheet
ca8e4fbd-2ace-40ac-99a6-ddbfd07a9732 | checkpoint | Others
7f33ec86-afce-4089-b88e-59307f71dfc1 | checkpoint-no-value | Mcconnell Dowell
cc758aa5-18f2-4ab8-a942-3dfd00324dd0 | signoff | Request McConnell Dowell Signoff
a6646ed3-8cef-4d9b-853a-ea64f9164e87 | checkpoint-no-value | Beca
eeac9eb0-9782-4711-b437-b3c00ab19367 | signoff | Request Beca Signoff
114a20d5-84f1-4bea-9bf7-c8f8422de222 | checkpoint | Completion and Certification documents
b1e384e4-b3dd-4aa3-8cf6-b0ac47138edf | checkpoint-no-value | FIRP Signoff
6b9d3715-8369-4b3a-b933-abc42ca90b0b | signoff | Record of Witnessing
631113d7-35b7-4436-a71c-c30dbc1ac0df | checklist | Water treatment pump |  | Equipment -
0632fabb-45ed-45a1-a1a8-b2578bf6629c | section | Factory Acceptance Testing
3930b3f7-06df-4716-ab19-c14397692e39 | checkpoint | Factory Acceptance Test Report
c385b4bb-82b3-499f-be18-606891782ef0 | section | Pre-Commissioning
fa1ba829-b3e5-4eef-a0de-8ccdc0f13f55 | checkpoint | Pump Check Sheet
0308170c-a039-4749-a8ef-9e20e9ad9f15 | checkpoint-no-value | Mcconnell Dowell
016948f7-2b8b-4672-8caa-c09375c376f7 | signoff | Request McConnell Dowell Signoff
9b45b626-4e5b-4184-ae1e-eccc185df30c | section | Commissioning
7854f986-5174-4727-a71c-17b4619eca9b | checkpoint | Pump Check Sheet
b759805c-c88d-4ee0-8f3b-b9da0d96430e | checkpoint-no-value | Mcconnell Dowell
e57988dc-c582-484a-aa16-35bd638f45e6 | signoff | Request McConnell Dowell Signoff
87b96d3a-8511-4861-876a-d236bd5848d9 | checkpoint-no-value | Beca
df05effa-ca8a-455f-ad3a-4c0bd79af9cd | signoff | Request Beca Signoff
3b461057-42ae-49f8-b992-4e821c1f60ac | checkpoint | Completion and Certification documents
a20bc1fe-9714-4397-a118-317e34f3259f | checkpoint-no-value | FIRP Signoff
27c72850-7a4e-409b-889b-296f99fa89ab | signoff | Record of Witnessing
e88818b8-ff8b-4bc2-899b-761e885ddf8f | checklist | WTP01 - Raw water turbidity high |  | WTP01 - Raw water turbidity high
e4633e39-ea9e-4ea0-9d81-85b8576d97f0 | section | IST Test
f2cadc1c-57cc-4137-a430-5b2a22173018 | checkpoint | IST Details
594e1e3a-6f4f-5c1d-9bb7-396e58debfb4 | textbox | Test Method - Filtec to simulate via Turbidty analyser
d75daf7d-2724-5c03-84d5-f8f648b76e41 | textbox | Area - A40
ce847385-1256-43b3-af4f-a5610723e1dd | section | First Test
b6e739b4-898f-41f6-9a71-41828d38ba04 | checkpoint | BMS - WTP status NOT READY indication
ccee9208-31d5-435c-bb57-3b2b2c0503f5 | checkpoint | BMS - STOP raw water pumps
a2b7f52d-9ba2-4a82-b089-da711f1bf654 | checkpoint | BMS - STOP bore pump
f499da33-52a0-4f5c-9f54-c55275fbb2d5 | checkpoint | BMS - WTP alarm status on BMS
5cdde1a6-3499-4ed1-9294-6d06575a3dc8 | checkpoint | Tank fill on Mains
be6c37e2-ef8d-4f85-bee8-e6c811576df8 | checkpoint | BMS - Turbidity value on BMS
81356e76-0f4d-4441-9cb7-2af859b70d77 | section | Second Test
556b87ef-fc9f-4de6-ad9d-7a3051941083 | checkpoint | BMS - WTP status NOT READY indication
37cf5ec7-3a52-413d-b0b1-b980c8c2ace4 | checkpoint | BMS - STOP raw water pumps
b6a6c291-8290-4a6f-a9ac-8378ac781b4e | checkpoint | BMS - STOP bore pump
3604cedc-4381-4b57-b23d-39ae9212859c | checkpoint | BMS - WTP alarm status on BMS
f65b4e74-e53d-4ce9-908e-0fb26821d551 | checkpoint | Tank fill on Mains
72a2ab4a-c123-482d-bcd8-40cefde3b49e | checkpoint | BMS - Turbidity value on BMS
3b24103e-ddb9-4293-bd50-159b162b73d7 | checklist | WTP02 - Treated water turbidity high |  | WTP02 - Treated water turbidity high
8f5436a0-2fbb-441e-8b05-a1036f4de29c | section | IST Test
cd4beaaa-8d25-4f11-9936-e11b463d9052 | checkpoint | IST Details
6bff62a7-6e4a-5bd9-a5de-c50ac8a68abb | textbox | Test Method - Filtec to simulate via Turbidty analyser
106c8baa-abb5-5049-b4ef-de492ef998b3 | textbox | Area - A40
ebb59c51-7e65-4e49-b31b-dba40f9c752f | section | First Test
b239cd30-f84a-49cc-a4ff-fabb78ac61c6 | checkpoint | BMS - WTP status NOT READY indication
418fbffb-fb16-4f78-9fde-eecc9e454e75 | checkpoint | BMS - STOP raw water pumps
a2f52ad7-198a-423e-8488-51337f62e701 | checkpoint | BMS - WTP alarm status on BMS mimic
0808d3b9-21d4-46e5-87c4-1e1a8a6ca316 | checkpoint | BMS - Tank fill on Mains
74c62dfc-1e88-4eab-9559-852ba015ae5d | checkpoint | BMS - Turbidity value on BMS
3e99470e-cc0b-4c66-a17c-a7d29f5ca52d | section | Second Test
a42c7ff6-bab5-4dde-a748-16336e4254a9 | checkpoint | BMS - WTP status NOT READY indication
7ced91b7-52c6-4ed7-b52b-438849782870 | checkpoint | BMS - STOP raw water pumps
3a7fd71f-7a7d-400b-954b-dc35b7570be8 | checkpoint | BMS - WTP alarm status on BMS mimic
e5646370-ff65-4470-af34-ef18c6afcf61 | checkpoint | BMS - Tank fill on Mains
b9718e7b-80e2-4bae-a62e-672e79c59c19 | checkpoint | BMS - Turbidity value on BMS
cb01765f-a919-4f7e-8416-58d2b984c7a5 | checklist | WTP03 - Treated water pH out of spec |  | WTP03 - Treated water pH out of spec
f70e14c8-fdc6-4f2b-9c92-337e3a0b53db | section | IST Test
aa87837f-9e32-4b7f-a11c-206a7c66215d | checkpoint | IST Details
c34d2347-d43b-5468-bfa7-7d943a560a19 | textbox | Test Method - Filtec to simulate via pH analyser
dceaade9-46ef-55c5-98bc-f46e33f38d98 | textbox | Area - A40
a094bda6-7250-4ad7-9296-9823de8cd674 | section | First Test
63a6a617-d42a-4415-9b3b-2605a12c0e8c | checkpoint | BMS - WTP status NOT READY indication
e6601b07-3b97-4f79-bc9c-9f7a47ea6db7 | checkpoint | BMS - STOP raw water pumps
4ec043f2-f2fc-4d88-973e-9b6cdb8dc4ef | checkpoint | BMS - WTP alarm status on BMS mimic
fd2d0aa8-b2f5-4a55-bc6e-a4ee7f7f23af | checkpoint | BMS - Tank fill on Mains
6c1147e9-2531-420a-8ea2-e21a923fd0b8 | checkpoint | BMS - pH value on BMS
c674523e-078c-4529-8ed1-47ec57192237 | section | Second Test
0b98f7bf-7e56-4ecd-9c62-531bc825adeb | checkpoint | BMS - WTP status NOT READY indication
a8a145da-b9af-4ebb-a0c7-0f2beb6a7a2e | checkpoint | BMS - STOP raw water pumps
b9d2023b-7b6c-44d8-80ac-78fd63de8d6a | checkpoint | BMS - WTP alarm status on BMS mimic
897c90ed-3f17-4554-8bb0-6bc97018e070 | checkpoint | BMS - Tank fill on Mains
3ae0ef25-6a30-4366-9366-a2cecc882aee | checkpoint | BMS - pH value on BMS
48f1ff07-1edf-4fc2-a991-a53a0b61f30a | checklist | WTP04 - Treated water Flouride out of spec |  | WTP04 - Treated water Flouride out of spec
24a89c08-942a-42e9-86a7-3fc755e8f468 | section | IST Test
e857253e-fe83-473f-ba3e-2d4b87a7bee5 | checkpoint | IST Details
713f5a38-c1b2-5156-bba2-8b9b4a97ffbc | textbox | Test Method - Filtec to simulate via Flouride analyser
b9967f83-48b7-5c78-88fd-47d2f07c141a | textbox | Area - A40
b1be6a6d-0d3e-4fea-9b57-28d5870b970b | section | First Test
dfb93621-e642-4b05-9ae9-ebf72354f856 | checkpoint | BMS - WTP status NOT READY indication
4d2c4c16-7a5a-4524-8275-7b0001a26668 | checkpoint | BMS - STOP raw water pumps
ec8524b1-9890-43b1-92ad-ca86dcab8ac2 | checkpoint | BMS - WTP alarm status on BMS mimic
da4bc56e-40c7-42a8-ae24-83e34adf5da8 | checkpoint | BMS - Tank fill on Mains
28d054cc-2621-4334-ac17-8e07f6162052 | checkpoint | BMS - Flouride value on BMS
8cb76dfa-4a5c-42c8-8b04-a200a7c95e27 | section | Second Test
14f93283-f0e3-460e-a498-3dc88ddd943f | checkpoint | BMS - WTP status NOT READY indication
4ddf6b43-bed0-405d-afc4-1e3f935d88c3 | checkpoint | BMS - STOP raw water pumps
c7e70a37-033e-4076-a7ff-10cc91736bc5 | checkpoint | BMS - WTP alarm status on BMS mimic
5c73aa0a-25c0-4a55-bc0c-f9e57eab4503 | checkpoint | BMS - Tank fill on Mains
698acbc0-4e0d-436d-ad51-224c17a57f39 | checkpoint | BMS - Flouride value on BMS
6b8929cd-2db4-40a9-972c-4e4797878a4f | checklist | WTP05 - Treated water chlorination out of spec |  | WTP05 - Treated water chlorination out of spec
6493ccb0-e48e-4c30-8a62-0b7576fb39a6 | section | IST Test
e698da23-0f2d-46d5-b9c9-3356c9b180f9 | checkpoint | IST Details
e765dcc0-f467-5c55-9e42-9aa150ff2e17 | textbox | Test Method - Filtec to simulate via chlorine analyser
9f10d272-c4f0-5f79-8351-5088bc619af9 | textbox | Area - A40
e6580e43-42e6-4deb-95e9-052867af51a5 | section | First Test
5f41e889-d36a-485b-82b4-e7558fd5b2f5 | checkpoint | BMS - WTP status NOT READY indication
f100d09e-885a-4631-b488-11e34af91967 | checkpoint | BMS - STOP raw water pumps
05ee068e-bb98-46b2-ad1b-e36e9dc4cf1b | checkpoint | BMS - WTP alarm status on BMS mimic
8dda2d98-25e6-4195-bed4-dbf32679a53a | checkpoint | BMS - Tank fill on Mains
5443f6f2-7514-4ab0-943b-fee30ea42224 | checkpoint | BMS - Chlorine value on BMS
68efa0e8-a3a3-483a-a7d0-afd872707679 | section | Second Test
948eb9fd-cefb-4b19-a1c1-0dd19869aa34 | checkpoint | BMS - WTP status NOT READY indication
d3cc6376-aeee-45ec-9a3f-fdf63158a744 | checkpoint | BMS - STOP raw water pumps
02ddebea-af20-407f-b690-a6e240e651c7 | checkpoint | BMS - WTP alarm status on BMS mimic
3b8fcb8b-046f-42c0-aa19-c650ca69bdac | checkpoint | BMS - Tank fill on Mains
ba8f42f0-4280-4326-9d2b-397404186beb | checkpoint | BMS - Chlorine value on BMS
a19b0882-7ee3-45cf-a1f1-e6083e2fc9e4 | checklist | WTP06 - Filter inlet pressure high |  | WTP06 - Filter inlet pressure high
b3b8007b-37d7-4d29-8e99-7eb4784c1c83 | section | IST Test
b17baaea-17cc-4d7d-9c9b-60f7b1ddac78 | checkpoint | IST Details
768407eb-0842-5474-9540-b9f7997d496d | textbox | Test Method - Potters/Filtec to confirm how this can be simulated/tested
091af2ce-c503-532c-b9f6-cb670bb803e3 | textbox | Area - A40
e2688031-0a4b-470a-9986-a82f6f72b667 | section | First Test
b160a145-46cd-4e2b-b077-3de899451359 | checkpoint | BMS - Switch duty treatment train
c7a1e50c-8f45-41d5-9d35-fa3eded48f78 | checkpoint | BMS - Treatment train in service indication #1, #2, both
a49a473c-86cf-4914-855b-5c3e7008c0f5 | checkpoint | BMS - Inlet pressure on BMS
d140020d-2557-4c82-8dce-d4035f4d17cb | checkpoint | BMS - BMS Alarm
2298b7e1-6e8c-451b-969d-8bbe033f5203 | section | Second Test
8ec7ae63-e61f-48b9-b26b-c706edad48f3 | checkpoint | BMS - Switch duty treatment train
3e55b092-20e5-498b-872b-aac0ceb8e277 | checkpoint | BMS - Treatment train in service indication #1, #2, both
6bdc251f-63fd-4a09-8718-64cba30fea0f | checkpoint | BMS - Inlet pressure on BMS
e7227c1b-86a0-4541-928d-d307a59cab69 | checkpoint | BMS - BMS Alarm
9f6d8c10-9a9c-4d0f-9bde-107b3dcc45b3 | checklist | WTP07 - Raw water pH LL/HL alarm |  | WTP07 - Raw water pH LL/HL alarm
5a0e2d6f-9572-452a-bab6-0149a38a4043 | section | IST Test
5e349795-5437-4f0e-82b7-627a985d9a26 | checkpoint | IST Details
6d561e72-d198-5ad2-90be-d50719449fc2 | textbox | Test Method - How can this be simulated?
5b205661-e806-5923-a65d-6596da600d85 | textbox | Area - A40
284ee285-8b7f-4f4d-bdce-f9d0cb4ac5c0 | section | First Test
ff5a4d15-0a04-4c0f-9fa7-563b4e4eea31 | checkpoint | Indication on local HMI panel
c16376b7-2304-43dc-9dd3-e3cf3b65b03f | checkpoint | BMS - Analog/digital value on BMS Mimic
f1da8bc1-1d43-480d-a6c4-ed3c3361a015 | section | Second Test
91109ad3-e41b-4caa-9cb8-46321734bfd3 | checkpoint | Indication on local HMI panel
5f68720b-770e-4636-8702-a03fa3b3a433 | checkpoint | BMS - Analog/digital value on BMS Mimic
73859eed-1d77-4e04-aa02-c40bee2b71a7 | checklist | WTP08 - Nitrate analyser high |  | WTP08 - Nitrate analyser high
b4ab4c74-c655-4dfb-8fe1-368051eb9f18 | section | IST Test
1e4d298e-baaa-4253-ad78-c99fd8cf8497 | checkpoint | IST Details
72266162-4055-5705-a4aa-1e9cae93c80d | textbox | Test Method - How can this be simulated?
ba9ae571-e3c6-5b95-b459-2e84f0ab537d | textbox | Area - A40
cf9a4cd2-a211-4d5d-8d8f-21b5c9d7b59f | section | First Test
6fd3db26-dff6-4db4-8e35-763a7d964d4a | checkpoint | Switch duty treatment train (local auto action)
f6434769-d4fc-4d5e-ab6e-a0d6ac62b39d | checkpoint | Indication on local HMI panel
f39478b6-72dc-4b06-be46-657c715b2f44 | checkpoint | Regenerate IEX column (local auto action)
2f3400d8-d22b-4f7f-97d6-007a87f4a867 | checkpoint | EX regeneration status #1, #2, READY
a329d4d4-0b92-49f6-a311-ad01a7c5dda9 | checkpoint | Treatment train in service indication #1, #2, both
0bc9766d-e9a3-40a4-8af0-0c1d1aaacf76 | checkpoint | BMS - Analog/digital value on BMS Mimic
0ec7a25a-44f8-49a0-98a1-7699442265c8 | section | Second Test
1cafd182-8faf-4dae-9774-455471fa613a | checkpoint | Switch duty treatment train (local auto action)
e3b5ca55-1c02-40c5-b1fe-4752b49576fb | checkpoint | Indication on local HMI panel
52a6dda4-ff87-43e7-b878-f1ab3d469389 | checkpoint | Regenerate IEX column (local auto action)
7cc81e48-534d-4857-8200-6c298906f916 | checkpoint | EX regeneration status #1, #2, READY
d880292b-84af-4d53-bd1b-69b939bdd611 | checkpoint | Treatment train in service indication #1, #2, both
966b2f69-aa24-432a-b97e-57eaddbba4cf | checkpoint | BMS - Analog/digital value on BMS Mimic
23a08850-44ec-4f15-bbb9-9131685d8325 | checklist | WTP09 - Low Level hypochlorite solution tank |  | WTP09 - Low Level hypochlorite solution tank
9447c391-95f5-4fd8-bc0b-fb7c8b24d8e1 | section | IST Test
82c32567-2d22-4a4c-9ddb-a03dbe1712aa | checkpoint | IST Details
49e53e62-f197-5c04-9d89-853af723e093 | textbox | Test Method - How can this be simulated?
0c81c99a-27df-52ba-b87f-8277205a7224 | textbox | Area - A40
4470c9ee-cdb9-408e-be01-e41e15d9339f | section | First Test
aaf6f08a-5537-44a6-a25c-f8b2dfa1d99c | checkpoint | Plant status NOT AVAILABLE
e6b2e96f-f711-4551-b26b-7733686f74db | checkpoint | Chemical dosing pumps status STOP
f11958d1-f63b-4a3e-bc1a-751b73ed0ba7 | checkpoint | Indication on local HMI panel
0e9bf82d-ba1a-468a-9332-470311fbfc56 | checkpoint | Refill chemical tanks (Local manual action)
8f7bf6fc-106d-4f47-8bcb-c6b0c5e6de0a | checkpoint | WTP status NOT READY indication
1df3c978-cf64-4b8c-acce-3938c53880ca | checkpoint | STOP raw water pumps
96777539-3ee3-4efc-8727-2087ac6e686e | checkpoint | BMS - WTP alarm status on BMS mimic
3e9d047c-35ef-4bf8-ba1d-3855c14d32f2 | section | Second Test
773dfbee-af35-4637-8fb1-ca6688759c1f | checkpoint | Plant status NOT AVAILABLE
383edd7b-e5c0-4c6b-bd34-a1cfc31b4f3d | checkpoint | Chemical dosing pumps status STOP
ece0010b-bb36-4ac4-822f-88b2f8667c63 | checkpoint | Indication on local HMI panel
fc3504f3-c4ce-44a9-93d9-ef1f04122ea4 | checkpoint | Refill chemical tanks (Local manual action)
a1d62276-d1b0-48a1-9e56-f17c79a8a5d4 | checkpoint | WTP status NOT READY indication
ac35fa01-aa72-4adb-a809-af3aa5e8467e | checkpoint | STOP raw water pumps
b946f174-4adc-4dbc-9910-6521ce6442f7 | checkpoint | BMS - WTP alarm status on BMS mimic
88e321b2-b046-409e-adb0-4f10b86d85fd | checklist | WTP10 - Low Level fluoride solution tank |  | WTP10 - Low Level fluoride solution tank
e3dec838-7d94-4bce-86be-be8819b3ab9a | section | IST Test
f59fa359-8d7e-4df9-9d9e-691832e0ebbe | checkpoint | IST Details
9d3aaadf-4e7e-5c29-860f-63f2b1805846 | textbox | Test Method - How can this be simulated?
60d61500-150f-5acb-b158-6b4a788866df | textbox | Area - A40
b3ab1e62-3901-4309-b33f-55e5d13392c9 | section | First Test
0bb6e601-aef8-4c37-b2b8-e4509fe42f64 | checkpoint | Plant status NOT AVAILABLE
ce57758e-b3c7-4b26-80ee-f4a170a2212e | checkpoint | Chemical dosing pumps status STOP
218fc11b-33be-49ff-aa40-f38aedbc5b34 | checkpoint | Indication on local HMI panel
fa8afd79-a99c-448f-9207-f3f9730391b9 | checkpoint | Refill chemical tanks (Local manual action)
e86e3143-2b9d-4286-9373-cdb3fb7de62b | checkpoint | WTP status NOT READY indication
7c8fada3-55d1-4666-88e5-9fb0349595fb | checkpoint | STOP raw water pumps
6f006401-367f-4e4a-9605-c66dcfe3cd5a | checkpoint | BMS - WTP alarm status on BMS mimic
4ff86da7-152a-491b-92d6-0d515aceb2da | section | Second Test
5522946b-7555-42e3-968c-5fd84108a9f2 | checkpoint | Plant status NOT AVAILABLE
ee970445-da2b-4b47-9c7f-38ea443b09c3 | checkpoint | Chemical dosing pumps status STOP
25b1bf09-06ae-4a78-8d41-72b1e706e3e8 | checkpoint | Indication on local HMI panel
c0bfa33d-255b-4289-8ac7-b7421e42f101 | checkpoint | Refill chemical tanks (Local manual action)
7dbe3c58-efce-4616-80ac-7cecda2d3343 | checkpoint | WTP status NOT READY indication
4739f1a7-b794-4b8d-a401-996dcd2f66fb | checkpoint | STOP raw water pumps
aa0aeb52-ee1e-4b1e-a6cc-0525cc23b20a | checkpoint | BMS - WTP alarm status on BMS mimic
6d1bd09a-ebd9-47b9-9ee9-0ed723ce7dbf | checklist | WTP11 - Raw Water flow <200m3/d |  | WTP11 - Raw Water flow <200m3/d
f05f10b7-0a4c-4f73-a694-e8a239416a6f | section | IST Test
0401ebfc-3cd0-4b8a-bdda-7e7ffcec034b | checkpoint | IST Details
c0e3f6d8-2fa7-503e-9cf5-a6e74b805ceb | textbox | Test Method - Decrease raw water flow
e049148e-0eda-5d0b-bceb-25ea417a6d3c | textbox | Area - A40
1fb9661e-aa0c-40f5-b988-a1b99339558d | section | First Test
5eae7946-e730-4689-a990-797b8bc6607d | checkpoint | Switch duty treatment train (local auto action)
a9ee7125-8433-4278-8983-a2e329030b7b | checkpoint | Indication on local HMI pane
88266664-09ee-4a36-b38c-6417d2171cb5 | checkpoint | Treatment train in service indication #1, #2, both
1f8b53f5-c793-46e6-9a8b-2e514c742ee2 | checkpoint | BMS - WTP alarm status on BMS mimic
6e0e2be1-3d58-4622-8cca-664188383fa6 | checkpoint | BMS - Analog/digital value on BMS Mimic
eea0320e-96bd-4219-98f3-6109206cb7f3 | section | Second Test
8e57f2fe-58ad-4206-b7c3-2fbe8e81ade6 | checkpoint | Switch duty treatment train (local auto action)
7e6c1876-7825-4947-9dc2-45e4078fb678 | checkpoint | Indication on local HMI pane
c5c9b2d4-fb05-42be-9b0b-0174a12033c1 | checkpoint | Treatment train in service indication #1, #2, both
83b7ad69-0a84-4ed0-8031-575fe24b1a78 | checkpoint | BMS - WTP alarm status on BMS mimic
d30b3fcd-c4f3-48c8-9f0d-a0360f66330e | checkpoint | BMS - Analog/digital value on BMS Mimic
3cfb522d-4f91-4e45-b009-3331274382b8 | checklist | WTP12 - Fluoride dose pump fault |  | WTP12 - Fluoride dose pump fault
de848e27-ac36-45f8-918e-2b4d75e6e406 | section | IST Test
2433eec8-7d2b-417e-b880-a0788a898137 | checkpoint | IST Details
58f4358c-f78e-5ae2-a7d4-c90868e559b7 | textbox | Test Method - How can this be simulated?
9e0eb09c-0dbe-58dc-a566-8045c1ec2805 | textbox | Area - A40
471b71a8-dcad-483a-9368-dcaf83a23b74 | section | First Test
86e9f85b-6a3f-4cb4-ad70-42b867a12e57 | checkpoint | Plant status NOT AVAILABLE
fce50ba2-0eff-4c9e-b407-c56de688cee4 | checkpoint | Chemical dosing pumps status STOP
5e8a3710-dfe8-4b1b-b048-2e4910641732 | checkpoint | Fluoride dose fault Pump OFF
99b4b57b-5e01-4f14-9150-4ccc7508702e | checkpoint | WTP status NOT READY indication
7d027f35-ecd2-44cc-9308-8ec6fdb9311f | checkpoint | STOP raw water pumps
3f5d6255-30af-4801-9309-160a5415d216 | checkpoint | BMS - WTP alarm status on BMS mimic
fafcead6-59cd-4281-b6fa-473a10f298b2 | section | Second Test
496a7bf0-fab1-4f08-91fb-69ea57fd09b6 | checkpoint | Plant status NOT AVAILABLE
40e66bd0-d7b4-4f7a-8a35-88915a1d2332 | checkpoint | Chemical dosing pumps status STOP
b4b45ebc-e2af-418a-8e66-bcd8ffdaa63a | checkpoint | Fluoride dose fault Pump OFF
3d6a484b-afbb-49b7-9af9-65b2ea569903 | checkpoint | WTP status NOT READY indication
bcd7d1db-69f1-4983-a5a1-70b5f4723d7a | checkpoint | STOP raw water pumps
5f0073ca-aa16-4e85-a5a8-3f21fbfaf0c0 | checkpoint | BMS - WTP alarm status on BMS mimic
c4c7c94a-b11a-49c6-83d9-6e9e15dfbe46 | checklist | WTP13 - Chlorination dose pump fault |  | WTP13 - Chlorination dose pump fault
6fb818ea-4526-46c8-bbfa-30d38e2e4835 | section | IST Test
e6ad102b-7080-425f-aedf-1a20a8e40b50 | checkpoint | IST Details
fdcfa419-4fe8-5ef6-9fea-e1d0a795aadd | textbox | Test Method - Simulate fault condition
374c083e-363b-5fae-a131-949f5c58a551 | textbox | Area - A40
30f82374-de35-482d-b499-47a433f0f038 | section | First Test
af4bbee5-3050-40c7-893c-175abe79cfbb | checkpoint | Plant status NOT AVAILABLE
e5c30fa0-4609-4097-b0e4-cad61c464d00 | checkpoint | Chemical dosing pumps status STOP
f71592e6-95bf-4d47-afc3-cf8140538ea1 | checkpoint | Chlorine dose fault Pump OFF
7677aef3-2392-47fd-bae9-d65b684e44f5 | checkpoint | WTP status NOT READY indication
6314b403-dda4-442b-86e6-64f03ce9f2be | checkpoint | STOP raw water pumps
49b37730-1d5d-4f62-ac1c-c05ad9ac75a8 | checkpoint | BMS - WTP alarm status on BMS mimic
461300e2-cd89-4dbb-bf15-bda09a6539f6 | section | Second Test
94bc7a99-5a03-4dc4-8e0c-82662154e9ac | checkpoint | Plant status NOT AVAILABLE
50a4948f-8e87-41a7-8ccc-7210cac71546 | checkpoint | Chemical dosing pumps status STOP
b42464b9-3fa4-4409-bd51-bffdecaa8127 | checkpoint | Chlorine dose fault Pump OFF
cff7f890-943f-4c57-912a-0b1fe71913da | checkpoint | WTP status NOT READY indication
6ab44579-8f98-464e-8a76-184075c40555 | checkpoint | STOP raw water pumps
4062d4d2-489a-41c9-9904-66824ac6631d | checkpoint | BMS - WTP alarm status on BMS mimic
1fcad240-9a1a-4ca8-a516-fa20f99fa1ea | checklist | WTP14 - Brine tank Low Level |  | WTP14 - Brine tank Low Level
4c62e14f-6355-4a57-859b-9aeef042db59 | section | IST Test
c1354dbf-e747-4a03-99e2-3c70fb80394b | checkpoint | IST Details
af54d35f-6945-5e86-ae67-3d3f9e061be7 | textbox | Test Method - Trigger level Sensor
f18b6974-889a-5e1f-b0b3-8e46b835e804 | textbox | Area - A40
2ae2d689-0887-42c4-90ab-ec905a871cd9 | section | First Test
68a73b3c-3fc7-4cde-bed3-4d4e4e147bf9 | checkpoint | Indication on local HMI pane
adb2012f-b543-4b08-ba4b-37c8e6393c4b | checkpoint | Regenerate IEX column (local auto action)
9be500e4-0e77-4b58-b401-198cb197c50c | checkpoint | Refill chemical tanks (Local manual action)
a2226c61-9cbc-43ec-b29c-089ca992b088 | checkpoint | IEX regeneration status #1, #2, READY
64e227a9-90fa-4121-a05a-c3a51febc18c | checkpoint | Treatment train in service indication #1, #2, both
1c55b9fe-ff2f-4de5-852a-7935194d50b9 | checkpoint | BMS - WTP alarm status on BMS mimic
67c3b13a-63e8-4a21-9443-6f25c13900ec | section | Second Test
d9397a3a-fba1-46e0-bad8-b36a56e773e1 | checkpoint | Indication on local HMI pane
a2e908e0-d02a-4756-beba-2b8ac702ed1f | checkpoint | Regenerate IEX column (local auto action)
30e42c63-0dc0-4646-94ef-53cf8ddb7faa | checkpoint | Refill chemical tanks (Local manual action)
2eee103f-862f-4d40-8abf-c32257e0c06c | checkpoint | IEX regeneration status #1, #2, READY
e70d41fd-54b0-4f7a-b683-900c37c2d65d | checkpoint | Treatment train in service indication #1, #2, both
e2ca5b65-c95b-4d38-a819-14e106ec13d1 | checkpoint | BMS - WTP alarm status on BMS mimic
cbc6a78b-f459-452c-97b1-ec0e7febeba9 | checklist | WTP15 - IEX Regen sequence fault |  | WTP15 - IEX Regen sequence fault
a9b54547-bde7-4f0e-af62-5537fe4e773f | section | IST Test
bb3c4e3a-fa17-473b-98bb-9dbad05d1e1a | checkpoint | IST Details
f767f8e8-e685-5db7-970a-cffbe7d9e1b0 | textbox | Test Method - How can this be simulated?
604a42d0-3406-5319-acd9-df8e275776a6 | textbox | Area - A40
1fce5765-7361-4d16-b50c-c36a1b057b38 | section | First Test
6deeb9ed-dc6e-4c43-a20b-a827c0b1e269 | checkpoint | Switch duty treatment train (local auto action)
6eaafa99-dca0-457a-bff9-a6607984d4bb | checkpoint | Indication on local HMI pane
0e51dd00-fd3b-46f0-ae6a-c8d15fb506aa | checkpoint | Regenerate IEX column (local auto action)
9c6c979b-ff3a-4f51-8214-595e625ba00e | checkpoint | IEX column bypass OPEN
f52ca385-1c76-4cfa-a992-a92f91915013 | checkpoint | IEX regeneration status #1, #2, READY
8356965d-36d5-49cd-bb02-5896ed8b5139 | checkpoint | Treatment train in service indication #1, #2, both
a55be1c3-c9d4-4e58-b5e6-614fec847606 | checkpoint | BMS - WTP alarm status on BMS mimic
b7697bc6-ee47-43cf-a8d8-2fd2a45e8a38 | section | Second Test
b9ef1bf5-fd21-4c93-afe6-d0778646010b | checkpoint | Switch duty treatment train (local auto action)
2d59daaa-dfae-420b-a4ba-19f9f535bffe | checkpoint | Indication on local HMI pane
22066428-5ae4-4b5d-839d-4d2b88391d7c | checkpoint | Regenerate IEX column (local auto action)
23b937e3-d0cb-4661-8fef-4fe77ad6e699 | checkpoint | IEX column bypass OPEN
eeb3ad45-8691-4551-8d76-1c8db445a581 | checkpoint | IEX regeneration status #1, #2, READY
ddf5f8e3-7ba0-4e50-8601-56f95792ae2f | checkpoint | Treatment train in service indication #1, #2, both
27598248-f4b8-4625-ab0d-ceb7c84d7dd4 | checkpoint | BMS - WTP alarm status on BMS mimic
7ec60f61-a3c0-4c4d-8d11-235092d81dc0 | checklist | WTP16 - UV Bank #1 fault |  | WTP16 - UV Bank #1 fault
b79317d0-7a1a-4f15-a4a2-6ea11574bf45 | section | IST Test
baad5ed4-4d5f-4e06-845a-d7a343af0517 | checkpoint | IST Details
48874a06-9ed5-5f22-9fc4-67a16187fc04 | textbox | Test Method - Simulate fault condition
7f68d90f-3351-5772-862d-1ecc67918110 | textbox | Area - A40
4b00fae5-7c9c-4d64-906a-635c48c39f9d | section | First Test
0fdfe3af-7267-4c44-8810-17f3cbc373e0 | checkpoint | Switch duty treatment train (local auto action)
46fa1011-0e5e-4e39-8507-c02655d10a0b | checkpoint | Indication on local HMI pane
9205293c-f5dc-4ad6-a252-5122444c6a99 | checkpoint | UV bank duty switch (Local auto action)
45920c14-7066-45b3-8511-a349df22353f | checkpoint | UV bank status #1, #2
b8288b5e-f6a8-4bd8-9fb8-0f849425d1b5 | checkpoint | Treatment train in service indication #1, #2, both
a39e2587-bfac-4c35-85a8-7365b88f2935 | checkpoint | BMS - WTP alarm status on BMS mimic
177ee5c6-001e-451d-b211-13c787dbe969 | section | Second Test
0644758d-8b5f-4cda-b659-fba0b5dbd1d5 | checkpoint | Switch duty treatment train (local auto action)
eae6c79b-e742-4edb-aa2f-aa7c4b4ff94a | checkpoint | Indication on local HMI pane
fbf6f517-6ac8-4bf4-a62b-cc81b4d52578 | checkpoint | UV bank duty switch (Local auto action)
9583a0b5-d659-46f0-85bb-c1e18fde9509 | checkpoint | UV bank status #1, #2
3cbcb771-0a74-4243-9e77-522b7c7e5f14 | checkpoint | Treatment train in service indication #1, #2, both
fb91d9a0-b46a-4e4f-b8f0-6ea6cd3f19d3 | checkpoint | BMS - WTP alarm status on BMS mimic
ef42afb6-143d-45e9-b9fc-a9db6aa0fdcc | checklist | WTP17 - UV Bank #1 fault |  | WTP17 - UV Bank #1 fault
73bd3493-81ff-474e-8c87-59d0c3380489 | section | IST Test
c6c0f410-d3fd-45dc-82d0-b4cae156ac7b | checkpoint | IST Details
0209e71f-5f72-5709-82a2-4a701da42214 | textbox | Test Method - Simulate fault condition
96759d23-579a-5473-8efc-29c006766aab | textbox | Area - A40
398b6e4b-5ffc-4b8f-b66c-d6d7c398bc85 | section | First Test
bc3105ac-f52e-42fe-b417-0a3f68925862 | checkpoint | Switch duty treatment train (local auto action)
361df3b7-5097-4d08-bf44-be6ac8ba2bbe | checkpoint | Indication on local HMI pane
870d57be-c414-4b61-9e9b-3cf8a8078bc8 | checkpoint | UV bank duty switch (Local auto action)
4ce99178-5fdc-46f9-8069-b69140883ce4 | checkpoint | UV bank status #1, #2
316a24e1-d25a-4a7f-aee2-47ad92bab868 | checkpoint | Treatment train in service indication #1, #2, both
f3abddd6-0cdc-4efe-a287-7b1f0537eecd | checkpoint | BMS - WTP alarm status on BMS mimic
9ce573a6-d982-4c2a-9c92-9bcd40d16879 | section | Second Test
45b6981e-25f4-458d-a945-1207ef447196 | checkpoint | Switch duty treatment train (local auto action)
6d679dfa-f414-4301-b311-34b4fe0f4c76 | checkpoint | Indication on local HMI pane
19e38776-0c6c-4138-8396-b22265e40040 | checkpoint | UV bank duty switch (Local auto action)
6d9a6af3-5a83-494d-b316-dc5bd6a097a5 | checkpoint | UV bank status #1, #2
fc61d642-3fcd-477b-a65e-0a9a6e3280a5 | checkpoint | Treatment train in service indication #1, #2, both
2fa04d57-ff79-4381-8c08-46850fdadb54 | checkpoint | BMS - WTP alarm status on BMS mimic
17eb71f3-a643-41d9-85ca-3de43fe4e319 | checklist | WTP18 - Non-potable water tank NPST01 High Level (1) |  | WTP18 - Non-potable water tank NPST01 High Level (1)
a2281067-ce48-48b7-904b-3726c8fa9e9e | section | IST Test
113173b3-be85-4994-b077-7817fde59f6c | checkpoint | IST Details
7683353d-3353-5f3b-a3fe-1e8577fa9982 | textbox | Test Method - Manipulate level sensor?
ee65e123-4af8-51f0-aebd-f4aa3430bb0e | textbox | Area - A40
1f6ec762-74e6-4856-97bb-c9a8b0fa763a | section | First Test
0e17cde9-abcc-4f5d-b2b3-190f1e3cb2f2 | checkpoint | STOP bore pump
7e15ac9f-4cef-4110-9b0b-c11d396d5f88 | checkpoint | BMS - WTP alarm status on BMS mimic
ee92289a-1c7a-44a0-a509-646969668cf9 | checkpoint | BMS - Analog/digital value on BMS Mimic
980ca16a-9958-4aa7-91b3-8b514c7a42c6 | section | Second Test
2feaac53-e60d-4ab3-b15c-5c55c02e6dae | checkpoint | STOP bore pump
c44d9610-0c6b-4780-a408-9eec780ed28d | checkpoint | BMS - WTP alarm status on BMS mimic
14a735f3-e4e8-400e-a538-44ce0a0a9bd1 | checkpoint | BMS - Analog/digital value on BMS Mimic
4e0f668b-4a75-47d2-a24a-d19d0db75107 | checklist | WTP19 - Non-potable water tank NPST02 High Level (1) |  | WTP19 - Non-potable water tank NPST02 High Level (1)
854bfa03-2317-45e5-ba0e-fe9e77566096 | section | IST Test
f9106e87-53f3-41ce-bc1a-fad6a8597c76 | checkpoint | IST Details
2a9b8892-2b3b-549a-98b0-48e22cd95467 | textbox | Test Method - Manipulate level sensor?
cbc43738-6004-5893-91dc-be17def1cfae | textbox | Area - A40
f820b25b-da08-40ad-ae48-ba0999daf835 | section | First Test
8e78503e-f181-434f-8c8f-90adbf069853 | checkpoint | STOP bore pump
04ec4fb0-57a5-4ae2-b18c-be6a00eac365 | checkpoint | BMS - WTP alarm status on BMS mimic
8a588a0b-00c7-41cf-a1bf-df685f1e963b | checkpoint | BMS - Analog/digital value on BMS Mimic
033042bd-7fb9-4249-82b4-010ae7295726 | section | Second Test
782442e6-efea-44b6-9916-d569c0b4ec59 | checkpoint | STOP bore pump
f9470d31-79c1-4ca5-9926-8b752e25c6c5 | checkpoint | BMS - WTP alarm status on BMS mimic
b1ca3192-b8db-46f5-b248-a6b055e6fcc8 | checkpoint | BMS - Analog/digital value on BMS Mimic
483f648d-beea-40aa-8757-ab7d1a202f09 | checklist | WTP20 - Potable water tank PST-01 Level (6) Emergency mode 1000m3/d |  | WTP20 - Potable water tank PST-01 Level (6) Emergency mode 1000m3/d
7cbc6392-5940-4fe0-bf73-867bd8a13164 | section | IST Test
f822b942-82db-446c-9184-594c64b27e3c | checkpoint | IST Details
cfec6041-28d3-57be-82b0-c6ecc78622e7 | textbox | Test Method - Manipulate level sensor?
e58ea957-e406-5a4f-8dfa-014180538985 | textbox | Area - A40
16ee2799-a70f-431b-95cc-b74e8733a29b | section | First Test
176cd600-1b1d-4305-bffd-1a5a097294a0 | checkpoint | Switch duty treatment train (local auto action)
0ebd46fd-ca43-4ed2-bc21-cd7e68b10396 | checkpoint | Indication on local HMI pane
39451892-8884-4914-b914-eb0b0c34e06c | checkpoint | IEX column bypass OPEN
c19fde84-908e-4c20-90d7-a89d68176219 | checkpoint | Treatment train in service indication #1, #2, both
c24cfa4b-9a81-4ea8-a39b-3466ad77c7bf | checkpoint | BMS - WTP alarm status on BMS mimic
f0f2c7fb-a1f2-45bd-b753-14dd7ba2ccf2 | checkpoint | BMS - Analog/digital value on BMS Mimic
1bde0e4b-a9aa-4339-816d-930b500ba526 | section | Second Test
bb55652f-b880-42d0-a557-97e9417ef032 | checkpoint | Switch duty treatment train (local auto action)
c44a0c6e-cac7-44ee-a6a6-688fff1ead71 | checkpoint | Indication on local HMI pane
ba35f81d-31c8-4cb8-af59-7f77dc21c40a | checkpoint | IEX column bypass OPEN
873afba1-0a20-41d5-8218-94d2bae9d898 | checkpoint | Treatment train in service indication #1, #2, both
f190b7cd-5c72-4310-8d33-110bad59adf0 | checkpoint | BMS - WTP alarm status on BMS mimic
e7b1e278-1ed6-4f15-801a-e9c6ab4a1ce0 | checkpoint | BMS - Analog/digital value on BMS Mimic
b2f67754-460d-4ad4-a2b9-42797d60651f | checklist | WTP21 - Potable water tank PST-02 Level (6) Emergency mode 1000m3/d |  | WTP21 - Potable water tank PST-02 Level (6) Emergency mode 1000m3/d
63da980d-258a-41eb-a972-1aed9a509e6a | section | IST Test
84859881-dba5-49fe-a9d7-e1da48b8d015 | checkpoint | IST Details
b36b9e57-5b31-56de-babb-802805785c62 | textbox | Test Method - Manipulate level sensor?
e4e6929c-0948-52e4-8200-d243f4e86940 | textbox | Area - A40
d1847dba-d8a1-4e92-83be-bd70e49a6cb2 | section | First Test
110fa705-9cc0-438b-b670-1ad6cda2aa08 | checkpoint | Switch duty treatment train (local auto action)
bd26f2aa-13f3-496a-bb86-3e4ff66847ac | checkpoint | Indication on local HMI pane
0177ee10-d92f-426a-9b2a-c44602829d13 | checkpoint | IEX column bypass OPEN
fc871985-3ec5-420f-a108-ec12b084b89a | checkpoint | Treatment train in service indication #1, #2, both
a1f332d9-0168-4186-a98b-05cb251431ed | checkpoint | BMS - WTP alarm status on BMS mimic
b45e23eb-cd3a-4d26-b152-78c82cde8761 | checkpoint | BMS - Analog/digital value on BMS Mimic
c2d09812-5af3-470c-bdda-2ee9321a3546 | section | Second Test
5bb84ae2-a96b-48dc-8c01-2be5b615f65c | checkpoint | Switch duty treatment train (local auto action)
b8b5899f-5efd-4bf5-a67e-c259ad7bcc80 | checkpoint | Indication on local HMI pane
7b1728b4-79cc-4f57-b2c2-33b052c3c20c | checkpoint | IEX column bypass OPEN
18d01e47-ad3c-4137-9c60-503ed89ff439 | checkpoint | Treatment train in service indication #1, #2, both
ef94217b-10be-4b5a-a5d1-bb9172ea0cbf | checkpoint | BMS - WTP alarm status on BMS mimic
6870629f-934f-4c78-a8c8-4ad0222d010c | checkpoint | BMS - Analog/digital value on BMS Mimic
5c6fdbc1-6ed0-435b-921e-df43e6b90a8d | checklist | WTP22 - Potable water tank PST-01 Level (7) Minimum contact volume |  | WTP22 - Potable water tank PST-01 Level (7) Minimum contact volume
91ee1ce4-3760-40de-8816-a14e6ebd83cb | section | IST Test
7038f7a3-421d-4924-ad20-24ff6ffc4135 | checkpoint | IST Details
431069a1-987d-5abf-affd-43b42f8f6087 | textbox | Test Method - Manipulate level sensor?
e89d3cb2-e719-5557-b8ad-355b2c9c548f | textbox | Area - A40
d5372daf-994e-4889-8508-d341929e9906 | section | First Test
1952fa10-a919-457e-a12d-69de87ea2fc8 | checkpoint | Plant status NOT AVAILABLE
6bcdf021-53e4-4b1c-9e69-7110997445f9 | checkpoint | WTP status NOT READY indication
539dd77b-0db2-4017-a50f-ccafbf0dc3b8 | checkpoint | STOP raw water pumps
f234bb2d-7af2-4050-a5bf-0c8b046e2471 | checkpoint | BMS - WTP alarm status on BMS mimic
4135b54d-16b7-45ae-a63a-ac43bfb56516 | checkpoint | BMS - Analog/digital value on BMS Mimic
2cb35a1f-0a4f-4af2-b853-d58582e18265 | section | Second Test
fa82a7a4-d874-4dd1-9a0e-6bd616aaf205 | checkpoint | Plant status NOT AVAILABLE
5b6ca0b3-912b-440b-a5e4-93e46299b3db | checkpoint | WTP status NOT READY indication
0c78d49e-fad4-49e5-a883-c61db4f2ca3f | checkpoint | STOP raw water pumps
acac948a-82e5-4770-8d4d-6f09c0f2a3bd | checkpoint | BMS - WTP alarm status on BMS mimic
a8f58cf1-1c43-4805-ba7d-ea754cdf581b | checkpoint | BMS - Analog/digital value on BMS Mimic
60cd2634-a34d-4a25-97ff-71f5349cc8ef | checklist | WTP24 - Potable water tank PST-01 Level (1) Tank full |  | WTP24 - Potable water tank PST-01 Level (1) Tank full
2ca7d5f7-f175-4af8-aa0a-1c623def7a3a | section | IST Test
05f74980-35a5-4f4a-9c1c-7d36bfa6dcf1 | checkpoint | IST Details
25d4b436-38ff-5be7-9893-fda12a0cc404 | textbox | Test Method - Manipulate level sensor?
902a879a-e275-5637-83cc-4789f491dc7b | textbox | Area - A40
c24dca6e-08d7-4297-b751-52f2985d774c | section | First Test
8cfc5ed8-11c0-46c2-9ff6-86592c495e6a | checkpoint | STOP raw water pumps
c754fcb3-83e7-417b-9fee-cff74a78b6c2 | checkpoint | BMS - Analog/digital value on BMS Mimic
d7b5ecff-f4ad-47ac-8f41-5b01094faff7 | section | Second Test
b47d845c-4a12-4323-b3e2-6a2d4df11998 | checkpoint | STOP raw water pumps
22fbb441-b581-402a-80b7-c3035230b4cf | checkpoint | BMS - Analog/digital value on BMS Mimic
8fc71ef4-9dac-46b0-a1e0-9ac7efe3ad2a | checklist | WTP25 - Potable water tank PST-02 Level (1) Tank Full |  | WTP25 - Potable water tank PST-02 Level (1) Tank Full
b2c64774-1d66-4e90-a346-1071dfc9d671 | section | IST Test
e4806b87-e3c6-48b2-a216-6917f49cb937 | checkpoint | IST Details
bfa69301-067f-5f08-a6bf-97831913dcd0 | textbox | Test Method - Manipulate level sensor?
7c2389fe-0d70-554b-a4a9-7d1cd05757c0 | textbox | Area - A40
6e83aa3e-5aa9-47cf-9d9a-6fe1acad62ae | section | First Test
76165c20-dc5f-4487-aecb-50633e4d2a17 | checkpoint | STOP raw water pumps
4da9577a-2985-483b-a50e-a9ba25f3d2c3 | checkpoint | BMS - Analog/digital value on BMS Mimic
c0b79a01-0b87-44b4-a90c-ff42dd13e627 | section | Second Test
206da1f9-584f-4f7d-9d4b-271b0b8fc7cd | checkpoint | STOP raw water pumps
200bc60a-d1eb-464b-890d-781164e96a0f | checkpoint | BMS - Analog/digital value on BMS Mimic
676f0a0b-0fed-4c5a-8b59-391bb51d173c | checklist | WTP26 - WTP feed pump(s) fault |  | WTP26 - WTP feed pump(s) fault
9aac6838-948d-4750-8123-1a07deecfe3a | section | IST Test
12f46165-513a-4584-89b1-c96da343530c | checkpoint | IST Details
ac46d20e-54a1-537d-9bb9-d4bb07d17be8 | textbox | Test Method - Simulate fault condition
ede9d16c-f5dc-5859-bf17-f93d1b9b2b82 | textbox | Area - A40
f35497fd-f176-4af1-a162-7cce68b8945c | section | First Test
5cc360f7-ed20-4450-b1ca-2fa880953d4c | checkpoint | Plant status NOT AVAILABLE
e02cd9fa-9431-4901-96dc-b53a57c75c6f | checkpoint | Chemical dosing pumps status STOP
eb069ad0-6b37-4289-b77f-a9c067ba5568 | checkpoint | Indication on local HMI panel
df9289dd-174c-45ed-b85d-a896788e2713 | checkpoint | WTP status NOT READY indication
a2d5280f-4aa7-40cc-8490-7d3205aba6cf | checkpoint | STOP raw water pumps
b2eb5151-d727-4ddf-acac-16e46fc1d69f | checkpoint | BMS - WTP alarm status on BMS mimic
a80acfe1-6d33-44e0-a6d6-9e6101afb2b3 | section | Second Test
ce32b136-026a-473d-9603-b0ec08be03fa | checkpoint | Plant status NOT AVAILABLE
d6a36d23-006d-43ef-8357-8ead1c669709 | checkpoint | Chemical dosing pumps status STOP
fb04f943-98b4-4ffa-8a7c-7bfd42f12a88 | checkpoint | Indication on local HMI panel
d764da6c-6abe-4c45-9679-e8007c40634b | checkpoint | WTP status NOT READY indication
94c648f5-4bb7-4962-a1f7-f677a08079e9 | checkpoint | STOP raw water pumps
26c06807-8833-46c0-9735-6ad8fe5beb62 | checkpoint | BMS - WTP alarm status on BMS mimic
7f995197-4482-49f5-a521-6f053c6c2371 | checklist | WTP27 - Mains supply to NPST >3hrs |  | WTP27 - Mains supply to NPST >3hrs
d854c9ce-0b05-4e3e-a046-566502c0f76c | section | IST Test
36ccab7d-bd47-4a33-b24e-790a13be9c3c | checkpoint | IST Details
02cd81ae-56a4-5fc4-bd83-64c12ce03107 | textbox | Test Method - How can this be simulated?
9ffa3b92-d523-5c98-a16f-a0ee6fee1f34 | textbox | Area - A40
4eb18d06-60ce-4b05-a2df-43bf2913a326 | section | First Test
720fe0dc-efdc-4774-92df-3bb31a3652ea | checkpoint | Plant status NOT AVAILABLE
65bf3ea7-a447-437e-9e29-eb62a5beb978 | checkpoint | Chemical dosing pumps status STOP
1cee24ee-8857-467f-b5bd-11c63867c7c2 | checkpoint | Indication on local HMI panel
56de3d94-8ed9-4eac-9f5c-df6ba6bca24f | checkpoint | STOP raw water pumps
df3b1d66-9b88-40bc-9867-b9c5bdd78c63 | checkpoint | BMS - WTP alarm status on BMS mimic
21ea2ee3-ff8f-42ce-b265-b55422848bca | section | Second Test
5c86df18-7f07-4e29-8191-0669c78ecc62 | checkpoint | Plant status NOT AVAILABLE
f21d331e-3a1e-4672-83b6-9ad5e285dff1 | checkpoint | Chemical dosing pumps status STOP
512e7447-1249-44c7-be4a-e36d2b8d6e01 | checkpoint | Indication on local HMI panel
872d504f-2644-40b1-a9a7-8651ad82b35f | checkpoint | STOP raw water pumps
c2f8251e-a012-462e-9dfb-7e2b1c5d32cc | checkpoint | BMS - WTP alarm status on BMS mimic

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
327a495b-3fc2-441a-af36-32b53e59931e | checklist | MG01 |  | MG01 - Oxygen Leak - Simulate an oxygen plant leak within the Gas Bottle Storage Room
7331e2ad-759e-46f8-be7a-37c7f1303d29 | section | IST Test
b6a34b4c-edc1-4041-ad8c-f1173daa1c38 | checkpoint-no-value | Test Method
1f311031-332b-517d-addc-79a6eeac39d3 | textbox | Test Method - Release O2 gas near sensor until alarm level reached
7ab310fa-d055-530d-953c-797cc13bd560 | textbox | Area - A40
3bd0b4c0-4e0a-48f4-b0a8-1b1741975c20 | checkpoint | Plantroom MGAP Alarm
aaba9739-b224-4766-9135-625c6c5b69fa | checkpoint | Control Room MGAP Alarm
aadf74b7-1f85-46e6-82b0-c97156f387bb | checkpoint | BMS Alarm - O2 Leak
545fa995-0627-42c9-9a11-db2072df54c5 | checkpoint | Email to ADHB Personnel
db44fa20-fbbc-4c9b-91d6-0effc8105089 | checkpoint | Plantroom Vent Fan Boost Mode
57d2a5b8-368d-4ba1-bb87-2a7404f35667 | checkpoint | O2 Solenoid Valve Shut Off
dc38858d-3e8c-4717-844a-1fe01fed255d | checkpoint | Room Gas Warning Light
9b50a591-649b-470c-8e1a-a95e8d3c655d | checkpoint | Room Gas Warning Sounder