## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | GAJV-ITP-00028_8.0 - Twin Rising Mains Installation | itp |  |  |  |  | GAJV-ITP-00028_8.0 - Twin Rising Mains Installation
section | 1.0 - Preliminaries
checkpoint | 1.1 - Design Drawings
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Ensure the latest IFC drawings are used and available onsite
label | CONFORMANCE CRITERIA - Sighting of drawings
label | METHOD - Retain Drawings
label | FREQUENCY/PROCESS HELD - Before project execution
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - DWG register with the drawing revision used
holdpoint | HOLD POINT
checkpoint | 1.2 - Check - CEP, SWMS, TMP and ESCP in place and signed off by personnel
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Ensure the latest IFC Plans are used and available onsite
label | CONFORMANCE CRITERIA - Sighting of plans
label | METHOD - Retain Plans
label | FREQUENCY/PROCESS HELD - Before project execution
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Plan register with the revision used
holdpoint | HOLD POINT
section | 2.0 - Materials (approval)
checkpoint | 2.1 - Pipe delivery inspection
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Watercare Standard Specification 203.7 , 203.12, 225.9, AS2033, AS 4130, AS 4131
label | CONFORMANCE CRITERIA - Free from defects and meet the requirements of Tables in specification 225.9
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Within 2 working days of delivery
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - This ITP signed, delivery dockets, pipe inspection check sheet
label | ○ GAJV inspection release certificate required.
holdpoint | HOLD POINT
checkpoint | 2.2 - Flange Connections
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Watercare Standard Specification 225.8.1
label | CONFORMANCE CRITERIA - Flanged connections to conform to BS EN 1092 PN16 with any necessary modifications to suit the polyethylene pipe and any connections to adjoining pipework
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Before project execution
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Pipe inspection check sheet, Material Certs
checkpoint | 2.3 - PE Stub Flanges
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Watercare Standard Specification 225.8.1
label | CONFORMANCE CRITERIA - Conform to Table 3 of the latest revision of ISO 9624
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Before project execution
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Pipe inspection check sheet, Material Certs
checkpoint | 2.4 - Backing ring
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Watercare Standard Specification 225.8.1
label | CONFORMANCE CRITERIA - Mild steel or stainless-steel backing flanges shall be used on all flanged joint. Stainless steel backing flanges, bolts, nuts, and washers made from 316 stainless steel shall be utilised.
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Before project execution
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material Certs
holdpoint | HOLD POINT
checkpoint | 2.5 - Bolts and Nuts and Washers
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Watercare Material Supply Standard
label | CONFORMANCE CRITERIA - Bolts and nuts for large flanges shall be manufactured to AS/NZS1251 316 stainless steel class 80
label | ○ Washers shall be manufactured from 316 stainless steel
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - All mechanical joints
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material Certs
checkpoint | 2.6 - M/4 AP40 Base
label | RESPONSIBILITY - GA-JV
label | REQUIREMENTS / REFERENCE - CI-CIVIL 2013350.219
label | CONFORMANCE CRITERIA - Minimum sampling rate: Sand Equivalent: >= 40 Clay Index: =< 3 Plasticity Index: <= 5, Broken face content: >= 70%
label | – – – – – – – – – – –
label | Particle size distribution for AP40
label | Test Sieve Aperture ¦¦ Maximum and minimum allowable percentage weight passing AP40 (Max size 40mm)
label | – – – – – – – – – – –
label | 37.5mm ¦¦ 100
label | 19mm ¦¦ 66-81
label | 9.5mm ¦¦ 43-57
label | 4.75mm ¦¦ 28-43
label | 2.36mm ¦¦ 19-33
label | 1.18mm ¦¦ 12-25
label | 600um ¦¦ 7-19
label | 300um ¦¦ 3-15
label | 150um ¦¦ 0-10
label | 75um ¦¦ 0-7
label | – – – – – – – – – – –
label | – – – – – – – – – – –
label | Particle Size distribution shape control:
label | Fractions ¦¦ Maximum and minimum allowable percentage weight of material within the given fraction AP40 (Max size 40mm)
label | – – – – – – – – – – –
label | 19mm – 4.75mm ¦¦ 28 - 48
label | 9.5mm – 2.36mm ¦¦ 14 – 34
label | 4.47mm – 1.18mm ¦¦ 7 – 27
label | 2.36mm – 600um ¦¦ 6 – 22
label | 1.18mm – 300um ¦¦ 5 – 19
label | 600um – 150um ¦¦ 2 - 14
label | – – – – – – – – – – –
label | METHOD - Test sand equivalent with sand equivalent test.
label | ○ Test Clay Index or Plasticity Index with either clay index test or plasticity index test.
label | ○ Test Broken Face Content with broken face test.
label | ○ Test Particle size distribution with wet sieving test.
label | ○ If any test fails, go back to production of new aggregate and repeat tests.
label | FREQUENCY/PROCESS HELD - Before project execution
label | TYPE - H
label | ATTENDANCE REQUIRED - Watercare
label | RECORDS OR CHECKLISTS - Materials Data Record Sheet, Delivery Dockets
holdpoint | HOLD POINT
checkpoint | 2.7 - AC14 M10
label | RESPONSIBILITY - GA-JV
label | REQUIREMENTS / REFERENCE - CI-CIVIL 2013350.219 (Temporary works), however the asphalt is permanent
label | CONFORMANCE CRITERIA - Mix Design Requirements: Dense Graded Asphalt:
label | – – – – – – – – – – –
label | Sieve Size (mm) ¦¦ Nix Designation AC14 Percentage Passing Sieve Size (By Mass)
label | – – – – – – – – – – –
label | 37.5 ¦¦ –
label | 26.5 ¦¦ –
label | 19.0 ¦¦ 100
label | 13.2 ¦¦ 90 – 100
label | 9.5 ¦¦ 72 – 83
label | 6.7 ¦¦ 54 – 71
label | 4.75 ¦¦ 43 – 61
label | 2.36 ¦¦ 28 – 45
label | 1.18 ¦¦ 22 – 40
label | 0.600 ¦¦ 13 – 27
label | 0.300 ¦¦ 9 – 20
label | 0.150 ¦¦ 6 – 13
label | 0.075 ¦¦ 4 – 7
label | Minimum Layer Thickness (mm) ¦¦ 55
label | Binder Content (% by mass) ¦¦ 4.0 – 6.0
label | – – – – – – – – – – –
label | METHOD - Asphalt mixes shall be designed with a target combined aggregate particle size distribution (including filler) and binder content complying with the relevant limits given. The following tests performed:
label | ○ The particle size distribution,
label | ○ The total binder content,
label | ○ The RAP content (if used),
label | ○ The maximum specific gravity and density of the compact mix,
label | ○ The air voids at laboratory design compaction level.
label | FREQUENCY/PROCESS HELD - Before project execution
label | TYPE - H
label | ATTENDANCE REQUIRED - Watercare
label | RECORDS OR CHECKLISTS - Materials Data Record Sheet
holdpoint | HOLD POINT
checkpoint | 2.8 - Bedding Material
label | RESPONSIBILITY - GA-JV
label | REQUIREMENTS / REFERENCE - 2012034.055 WSL 225,WSL 225P CG-P
label | CONFORMANCE CRITERIA - Bedding shall be DM 7/3.
label | METHOD - Material Approval
label | FREQUENCY/PROCESS HELD - Before project execution
label | TYPE - H
label | ATTENDANCE REQUIRED - WSL
label | RECORDS OR CHECKLISTS - Materials Data Record Sheet
holdpoint | HOLD POINT
checkpoint | 2.9 - Lightweight Sand
label | RESPONSIBILITY - GA-JV
label | REQUIREMENTS / REFERENCE - 2012034.113
label | CONFORMANCE CRITERIA - Lightweight sand to be installed between Ch 557 to 663
label | ○ Lightweight sand to be used in lieu of cement stabilized sand
label | METHOD - Material Approval
label | FREQUENCY/PROCESS HELD - Before project execution
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Materials Data Record Sheet
holdpoint | HOLD POINT
checkpoint | 2.10 - F2 Sand
label | RESPONSIBILITY - GA-JV
label | REQUIREMENTS / REFERENCE - 2012034.113
label | CONFORMANCE CRITERIA - F2 sand to be installed between Ch 557 to 663
label | METHOD - Material Approval
label | FREQUENCY/PROCESS HELD - Before project execution
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Materials Data Record Sheet
holdpoint | HOLD POINT
section | 3.0 - Construction
checkpoint | 3.1 - Survey and Set out
label | RESPONSIBILITY - GA-JV
label | REQUIREMENTS / REFERENCE - Drawings
label | CONFORMANCE CRITERIA - Survey and set out to be as per drawings.
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - As required
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - N/A
checkpoint | 3.2 - Undercut procedure and design
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - Drawings
label | CONFORMANCE CRITERIA - If 12kpa to 50kpa use 2012034.054 IF 50kpa plus use 2012034.055
label | ○ If less than 12kpa, excavation to be undercut up to 1750mm below pipe invert or until 12kpa strength is found. This is to be backfilled with DM 7/3.
label | METHOD - Shear Vane
label | FREQUENCY/PROCESS HELD - Every 4m after CH412 (each trench shield installation).
label | TYPE - W
label | ATTENDANCE REQUIRED - Watercare
label | RECORDS OR CHECKLISTS - Scala or shear vane records.
checkpoint | 3.3 - Trench Bedding
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - WSL 225.22, drawings WSL 225.22P
label | CONFORMANCE CRITERIA - Bedding shall be DM 7/3. Minimum bedding depth shall be 400mm below pipe invert, max 1750mm (depending on ground conditions), 200mm cover, and 350mm surround.
label | ○ Bedding to be installed to correct gradient as per drawings. Gradient changes across various chainages across the pipeline.
label | ○ Bedding to be 90% in vegetation Bedding to be 95% in road works
label | METHOD - NDM test
label | FREQUENCY/PROCESS HELD - 1 test per 2 layers per 100 linear meters of the pipeline
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - IANZ NDM Results
holdpoint | HOLD POINT
checkpoint | 3.4 - Trench Backfill
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - Watercare Standard Specification 225.23 And 225.23P Drawings CG-P
label | CONFORMANCE CRITERIA - As per DWGs in 2012034 Set
label | ○ Backfill in vegetation to be as per drawing compacted to 90%
label | ○ Backfilling of trench through trafficable areas within the Mangere Wastewater Treatment Plant shall be shall compacted in layers to achieve 95%MDD (industry Standard) Clegg calibration.
label | ○ Lightweight Sand to be 95% compacted F2 Sand to be 95% compacted
label | METHOD - NDM test
label | FREQUENCY/PROCESS HELD - 1 test per 2 layers per 100 linear meters of the pipeline
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - IANZ NDM Results
checkpoint | 3.5 - Geogrid and Geotextile install
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - 2012034 Set Manufactures instruction
label | CONFORMANCE CRITERIA - A29 bidim filtration class 4 and strength class C to be included showing minimum 500mm overlap.
label | ○ Geo grid to either have bodkin installed or cable tied
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Trench length
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Install Checklist
checkpoint | 3.6 - Backfilling around existing services
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - WSL CG C3.1.5, C3.1.6, C3.1.7
label | CONFORMANCE CRITERIA - Minimum vertical and horizontal separation as per Watercare design standards, and utility specific requirements.
label | ○ Refer to CG -3.1.5 and CG -3.1.6 for minimum clearances
label | METHOD - Compaction Test
label | FREQUENCY/PROCESS HELD - Each service crossing trench
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Clegg sheet or NDM. (for polystyrene install visual inspection required )
checkpoint | 3.7 - Trace wire and warning tape installation
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - WSL CG C3.1.7 and Drawings
label | CONFORMANCE CRITERIA - Install tracer wire at trench extremities as per drawings
label | ○ Warning tape to be cream coloured 100mm width and installed 450mm above top of pipe
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Trench length
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Install Checklist
checkpoint | 3.8 - Flanged Joints
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - Watercare Standard Specification 225.11.2
label | CONFORMANCE CRITERIA - Nuts shall be oiled before tightening. The Contractor shall detail flange tightening procedure and torque values in their WMS. Stainless steel backing plates shall be used on all flanged joints unless specified otherwise in the Particular clauses.
label | METHOD - Torque wrench
label | FREQUENCY/PROCESS HELD - Each mechanical Joint
label | TYPE - W
label | ATTENDANCE REQUIRED - Watercare
label | RECORDS OR CHECKLISTS - Checklist signed
checkpoint | 3.9 - Compaction of AP40
label | RESPONSIBILITY - GA-JV
label | REQUIREMENTS / REFERENCE - CI-CIVIL 2013350.219
label | CONFORMANCE CRITERIA - MDD = 95%
label | METHOD - Nuclear Densometer
label | FREQUENCY/PROCESS HELD - 5 tests every 1000m2
label | TYPE - W
label | ATTENDANCE REQUIRED - Watercare
label | RECORDS OR CHECKLISTS - Nuclear Densometer Test Results
checkpoint | 3.10 - Compaction of AC14
label | RESPONSIBILITY - GA-JV
label | REQUIREMENTS / REFERENCE - Auckland Transport Code of Practice 2013
label | CONFORMANCE CRITERIA - MDD >= 98%
label | METHOD - Core sample
label | FREQUENCY/PROCESS HELD - Each new batch
label | TYPE - W
label | ATTENDANCE REQUIRED - Watercare
label | RECORDS OR CHECKLISTS - Core Sample Test Results
checkpoint | 3.11 - Beam test
label | RESPONSIBILITY - GA-JV
label | REQUIREMENTS / REFERENCE - Auckland Transport Code of Practice 2013
label | CONFORMANCE CRITERIA - Not more than 5% of the deflections exceed 1mm. None to exceed 1.5mm
label | METHOD - Benkelman Beam test
label | FREQUENCY/PROCESS HELD - 10m staggered intervals
label | TYPE - W
label | ATTENDANCE REQUIRED - Watercare
label | RECORDS OR CHECKLISTS - Benkleman Beam Test
section | 4.0 - Construction (Testing to be done after final install)
checkpoint | 4.1 - CCTV Inspection PRE
label | REQUIREMENTS / REFERENCE - Watercare Standard Specification 225.11.3 and 225.11.4
label | CONFORMANCE CRITERIA - A CCTV inspection shall be carried out of any welded pipe string. The video record shall be delivered to the Engineer for inspection and approval prior to the in-ground installation
label | METHOD - CCTV Camera
label | FREQUENCY/PROCESS HELD - Prior to backfilling pipe/sections of pipe
label | TYPE - W
label | ATTENDANCE REQUIRED - Watercare
label | RECORDS OR CHECKLISTS - Video Record
checkpoint | 4.2 - CCTV Inspection Post
label | REQUIREMENTS / REFERENCE - Watercare Standard Specification 225.11.5 and 225.11.6
label | ○ Watercare Standard Specification 225.12 And 225.12P
label | ○ Watercare Standard Specification 225.18 And 225.18P
label | CONFORMANCE CRITERIA - Following the in-ground installation of the pipeline, it shall be CCTV inspected prior to water pressure testing. The video record shall be delivered to the Engineer for inspection and approval prior to final testing.
label | The video data shall be in colour, be presented in an approved format and be recorded on DVD medial. The video of each inspection record shall clearly identify the pipe string and running chainage by means of a digital overlay on the video image. It shall also include the following information:
label | a) The day, date and time of the inspection;
label | b) Camera orientation;
label | c) Inclinometer reading; and
label | d) Appropriate references to related surveys. The quality of the video picture shall be such that the condition of the pipe surface is readily apparent and any defects or obstructions are clearly visible. The CCTV camera shall proceed at a height corresponding to the centreline of the pipeline ± 10% of the pipes internal diameter. The speed of the camera shall not exceed 0.2 m/sec. The camera shall be a pan and tilt type with w zoom capability. The camera shall be set to record immediately before entering the pipe and shall be kept running until the end of the inspection.
label | METHOD - CCTV Camera
label | FREQUENCY/PROCESS HELD - Prior to final testing
label | TYPE - H
label | ATTENDANCE REQUIRED - Watercare
label | RECORDS OR CHECKLISTS - Video Record
holdpoint | HOLD POINT
checkpoint | 4.3 - Pressure pipelines Final Testing – exceeding 400m and greater than 315mm
label | CONFORMANCE CRITERIA - The pipeline shall be filled with water 24 hours before commencement of the test. The main shall be pressurised to 1.25 times the MAOP. Loading Time (tL) shall not be less than 50 minutes. The Contractor shall record pressures in the main throughout the test by means of a data-logger. The data-logger shall have a current certificate of calibration, and shall be capable of recoding pressures in increments of 5 kPa or less. A calibrated test gauge shall also be installed to monitor mains pressures and to check the data-log results. Where the test is abandoned for any reason, the main shall to be left to recover at static pressure before re-pressurising
label | METHOD - Hydrostatic test, Visual Inspection
label | FREQUENCY/PROCESS HELD - Entire pipeline
label | TYPE - H
label | ATTENDANCE REQUIRED - Watercare
label | RECORDS OR CHECKLISTS - This ITP signed, Record Sheet. Procedure
holdpoint | HOLD POINT
section | 5.0 - Post Construction
checkpoint | 5.1 - As built records
label | RESPONSIBILITY - GA-JV
label | REQUIREMENTS / REFERENCE - Watercare Standard Specification 225.31
label | CONFORMANCE CRITERIA - As built records - containing a list of materials used in the pipeline and their relevant material test certificates, and a copy of the joint welding data for all the welded joints, indexed to recognisable features on the Drawings
label | METHOD - Survey Drawings
label | FREQUENCY/PROCESS HELD - General
label | TYPE - H
label | ATTENDANCE REQUIRED - Watercare
label | RECORDS OR CHECKLISTS - As built Records
holdpoint | HOLD POINT
checkpoint | 5.2 - Final Submission Via Aconex
label | RESPONSIBILITY - GA-JV
label | CONFORMANCE CRITERIA - All QA documents to be placed in appropriate packages to be submitted
label | METHOD - Aconnex Mail
label | FREQUENCY/PROCESS HELD - After Construction
label | TYPE - H
label | ATTENDANCE REQUIRED - Watercare
label | RECORDS OR CHECKLISTS - Aconex Request
holdpoint | HOLD POINT
checkpoint | CONFORMANCE / VERIFICATION STATEMENT
label | This closed lot conforms in all respects with the standards and requirements specified in the Contract Documents. The lot verification records are complete, and any non-conformances have been closed out in accordance with the Projects requirements.
label | Construction Lot checked by the Senior Project Engineer responsible for the works
textbox | Senior Project Engineer - PRINT NAME:
date | Senior Project Engineer - DATE:
label | Construction Lot verified and closed by Quality Management Representative
textbox | Quality Management Representative - PRINT NAME:
date | Quality Management Representative - DATE:
label | Independent Verification Review (if required) by:
textbox | PRINT NAME:
date | DATE:
holdpoint | ADD SIGNATURE
checklist | GAJV-ITP-00184_5.0 - Concrete work Diversion Chamber & Confluence Chamber | itp |  |  |  |  | GAJV-ITP-00184_5.0 - Concrete work Diversion Chamber & Confluence Chamber
section | 1.0 - Preliminaries
checkpoint | 1.1 - Check - Drawings are IFC and current
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Ensure the latest IFC drawings are used and available onsite
label | CONFORMANCE CRITERIA - Sighting of drawings
label | METHOD - Retain drawings
label | FREQUENCY/PROCESS HELD - Before project execution
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - DWG register with the drawing revision.
holdpoint | HOLD POINT
checkpoint | 1.2 - Check - CEP, SWMS, TMP and ESCP in place and signed off by personnel
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Ensure latest IFC plans are used and available onsite
label | CONFORMANCE CRITERIA - Sighting of plans
label | METHOD - Retain plans
label | FREQUENCY/PROCESS HELD - Before project execution
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Plan register with the revision used
holdpoint | HOLD POINT
section | 2.0 - Materials (approval)
checkpoint | 2.1 - Steel reinforcing
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 2012036 Series, NZS 4671/ 3109 GC-C4P – 4.1 and 4.1.1.10
label | CONFORMANCE CRITERIA - Grade 500E
label | ○ Produced using micro-alloy process
label | ○ GRP 16
label | ○ Chemical Anchor
label | METHOD - Review mill certificate, Reinforcing ID
label | FREQUENCY/PROCESS HELD - Each batch
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Mill Certificates
checkpoint | 2.2 - Concrete Mix Design (base, wall, benching)
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - NZS3104, MS-41P – 5P, 5.2P, DWG 2012036.861
label | CONFORMANCE CRITERIA - Grade 45 MPa OPC
label | METHOD - Review mix design
label | FREQUENCY/PROCESS HELD - Each mix design
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Aconex approval mail
checkpoint | 2.3 - Block out infill concrete
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 201236.862
label | CONFORMANCE CRITERIA - Infill concrete to be S45/10
label | ○ Additional dosage of shrink reduction admixture as per drawing to be Sika control plus as or approved equivalent at 2.25% by weight of cement mass and shall comply with manufacturers requirements.
label | ○ Additional dosage of admixture as per drawing to be Xypex admix C-5000 additive or approved equivalent at 0.6% by weight of cementitious content and shall comply with manufacturers requirements.
label | METHOD - Review dockets
label | FREQUENCY/PROCESS HELD - Each delivery
label | TYPE - S
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material dockets
checkpoint | 2.4 - Epoxy grout
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 2012036.908, DWG 2012036.863, GC-C4P
label | CONFORMANCE CRITERIA - As per manufacturers data sheet
label | ○ 25W x 20 NITOSEAL SC600 SEALANT
label | METHOD - Review product data sheet
label | FREQUENCY/PROCESS HELD - Each delivery
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material dockets
checkpoint | 2.6 - Concrete pipe DN2100
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - DWG 2012034.183 MS-03
label | CONFORMANCE CRITERIA - RCRRJ Class 4
label | METHOD - Review shop drawings
label | FREQUENCY/PROCESS HELD - Each Delivery
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - QA from supplier
checkpoint | 2.7 - Hydrophilic Strip
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 2012036.873, DWG 2012036.908
label | CONFORMANCE CRITERIA - CJ-0725-3K or approved equivalent
label | METHOD - Review product data sheet
label | FREQUENCY/PROCESS HELD - Prior to commencement of work
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material dockets
checkpoint | 2.8 - PE Liner & filler rod
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - CG-C27P - Table 5-1
label | CONFORMANCE CRITERIA - Technical data sheets
label | ○ Manufacturers certificates of compliance
label | METHOD - Manufacturers certificate of compliance
label | FREQUENCY/PROCESS HELD - Prior to commencement of work
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material certificate and aconex mail approval
checkpoint | 2.9 - Approved Curing compounds
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - MS-41P 11.3P
label | CONFORMANCE CRITERIA - Curing to be accepted by the engineer
label | ○ Curing to meet the requirements of MS-41P
label | ○ E-cure As per GAJV-MAR-000035
label | METHOD - Review technical data
label | FREQUENCY/PROCESS HELD - Prior to commencement of work
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material certificate and aconex mail approval
checkpoint | 2.10 - Materials for Concrete Repairs
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - MS-41P
label | CONFORMANCE CRITERIA - Technical data sheets
label | METHOD - Review technical data
label | FREQUENCY/PROCESS HELD - Prior to commencement of work
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material data sheet and aconex mail approval
checkpoint | 2.11 - Manhole Covers
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 2012036 Series NZS 3996 CG-
label | CONFORMANCE CRITERIA - PAMREX DN700
label | ○ Gatic GM302C1212D, GM309C66D, GM303C6122D
label | ○ Class D400 HN-HO-72 rated
label | ○ Manufacturers certificates of compliance
label | ○ Shop drawings.
label | METHOD - Manufacturers certificate of compliance
label | FREQUENCY/PROCESS HELD - Prior to commencement of work
label | TYPE - S
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Dockets
checkpoint | 2.12 - Stainless Steel Safety Grille
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 2012034.161, NZS 3996
label | CONFORMANCE CRITERIA - Manufacturers certificates of compliance
label | ○ Shop drawings.
label | METHOD - Final design and detail to be submitted to Watercare for review and approval
label | FREQUENCY/PROCESS HELD - Prior to commencement of work
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material Approval
checkpoint | 2.13 - Water stop
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C4P 4.1.2P DWG 2012036.862
label | CONFORMANCE CRITERIA - Supercast Rearguard R or approved equivalent
label | METHOD - Review product data sheet
label | FREQUENCY/PROCESS HELD - Prior to commencement of work
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material dockets
checkpoint | 2.14 - Backfill Material – 7/3
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - Table C2-1 - Behind walls or chambers, CG_1 GAJV-RFI-002719
label | CONFORMANCE CRITERIA - Approved DM7/3
label | METHOD - Material order review
label | FREQUENCY/PROCESS HELD - Before procurement
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Delivery dockets, Quarry material test results for PSD, MDD
checkpoint | 2.15 - Backfill Material – Flowable Fill
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - GAJV-RFI-002719
label | CONFORMANCE CRITERIA - Min 5 MPa flowable fill
label | METHOD - Review mix design
label | FREQUENCY/PROCESS HELD - Each mix design
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Aconex approval mail
section | 3.0 - Construction: Reinforcing Cages
checkpoint | 3.1 - Reinforcement Placement
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 2012036 Series
label | ○ DWG 2012036.861
label | ○ DWG 2012036.909
label | ○ DWG 2012036.907
label | ○ DWG 2012036.906
label | ○ DWG 2012036.903
label | ○ DWG 2012036.902
label | ○ DWG 2012036.900
label | ○ DWG 2012036.893
label | ○ DWG 2012036.891
label | ○ DWG 2012036.890
label | ○ DWG 2012036.889
label | ○ DWG 2012036.888
label | ○ DWG 2012036.887
label | ○ DWG 2012036.886
label | ○ DWG 2012036.883
label | ○ DWG 2012036.882
label | ○ DWG 2012036.881
label | ○ DWG 2012036.880
label | ○ DWG 2012036.879
label | ○ DWG 2012036.878
label | ○ DWG 2012036.877
label | ○ DWG 2012036.876
label | ○ DWG 2012036.875
label | ○ DWG 2012036.872
label | ○ DWG 2012036.871
label | ○ DWG 2012036.870
label | ○ CG-C4P - 4.1.1 and 4.1.1.17 in accordance to NZS3109
label | CONFORMANCE CRITERIA - Ensure that the placed reinforcement complies in all respects with the Design Drawings and this Specification
label | ○ Minimum cover over reinforcement shall be as noted on the Design Drawings
label | ○ Lap lengths shall generally be as detailed on the Design Drawings or otherwise as per 2012036.861
label | ○ Not more than 50% of the reinforcing bars shall be lapped at any one section, i.e. laps shall be staggered.
label | METHOD - Visual Inspection and measurement on site
label | FREQUENCY/PROCESS HELD - During and after steel placement
label | TYPE - HP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Pre-pour checklist Photographs
holdpoint | HOLD POINT
checkpoint | 3.2 - Chemical Anchors/ Chem Set Bars
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 2012036.909, DWG 2012036.861
label | CONFORMANCE CRITERIA - SAF2507 Stainless Steel Anchors.
label | ○ HILTI RE-500-SD Injection Adhesive
label | METHOD - Review product data sheet. Manufacturers certificate of compliance.
label | FREQUENCY/PROCESS HELD - Prior to and after installation.
label | TYPE - HP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Installation checklist
holdpoint | HOLD POINT
checkpoint | 3.3 - Rebar Couplers
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - NZS 3101, DWG 2012036.862
label | CONFORMANCE CRITERIA - ReidBar Steel coupler
label | ○ Use EPCON C8 XTREME as per manufactures instructions.
label | ○ RB25CS instead.
label | METHOD - Review product data sheet. Visual inspection.
label | FREQUENCY/PROCESS HELD - During and after placement
label | TYPE - HP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Pre-pour checklist
holdpoint | HOLD POINT
checkpoint | 3.4 - Construction Joints and Water Stop Placement
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C4P - 4.1.2P
label | ○ NZS 3109, Clause 5.6.3
label | ○ DWG 2012036 Series
label | ○ DWG 2012036.861
label | ○ DWG 2012036.862
label | ○ DWG 2012036.863
label | ○ DEG 2012036.873
label | ○ DWG 2012036.903
label | CONFORMANCE CRITERIA - Construction joints shall conform to NZS 3109, Clause 5.6.3, type B
label | ○ Joint position shall be as shown on the Design Drawings unless otherwise agreed with the engineer
label | ○ Water stops shall be placed as indicated on the drawings
label | ○ Installed as per manufacturer’s specification and care taken to prevent damage during concrete placement.
label | METHOD - Visual inspection with reference to DWGS
label | FREQUENCY/PROCESS HELD - Before concrete pour
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Pre-pour checklist
section | 4.0 - Construction: Formwork
checkpoint | 4.1 - Formwork
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 2012036 Series CG-C4P - 4.5P, NZS 3109 Section 5
label | CONFORMANCE CRITERIA - Formwork adequately supported and restrained – Design approved if necessary.
label | ○ Formwork to be treated with release agent where in direct contact with concrete.
label | ○ Formwork must produce cast surfaces within a tolerance of +15 or -12mm on the given dimensions for width and ± 12mm for vertical height, and without visible offsets, bulges, or misalignment of the concrete.
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Prior to concrete pour
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Pre-pour checklist Photographs
checkpoint | 4.2 - Cast in items
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-P
label | ○ DWG 2012034.185
label | ○ DWG 2012036.863
label | CONFORMANCE CRITERIA - Carry out inspection and confirm correct position prior to concrete pour.
label | ○ Ensure correct cover is achieved around the item.
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Prior to concrete pour
label | TYPE - HP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Pre-pour checklist
holdpoint | HOLD POINT
checkpoint | 4.3 - Block-out infill pipe penetration (if required)
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C4P-4, DWG 2013036.862
label | CONFORMANCE CRITERIA - Ensure all reinforcement is to be continuous through block-outs during construction.
label | ○ Ensure correct cover is achieved prior to concrete pour.
label | METHOD - Visual Inspection, Construction methodology and associated reinforcement curtailment details for approval before construction
label | FREQUENCY/PROCESS HELD - Prior to concrete pour
label | TYPE - HP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Pre-pour Checklist
holdpoint | HOLD POINT
section | 5.0 - Post Construction: Concrete Works
checkpoint | 5.1 - Concrete Testing (Consistency, 28-day compressive strength, Shrinkage, Permeability, Water absorption, Sulphite content, Alkali content, Chloride content, Temperature rise)
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - MS-41P - 5P MS-41P - 12P, MS-41P – table 6.1P
label | ○ Consistency: NZS 3109 and NZS 3112
label | ○ 28-day compressive strength: NZS 3109 Section 9 and NZS 3112
label | ○ Shrinkage: AS 1012.13
label | ○ Permeability: DIN 1048
label | ○ Water absorption: AS 4058 Appendix F
label | ○ Sulphite content: AS 1012.14
label | ○ Alkali content: Chloride content: AS 1012.14
label | ○ Temperature rise: Not applicable as pours are less than 0.9m thick (as per MPS Temperature Control Plan)
label | CONFORMANCE CRITERIA - Consistency: For water retaining structures, slump tolerances shall be half those given in Table 9.1 of NZS 3109
label | ○ 28-day compressive strength: 45 MPa
label | ○ Shrinkage: 430mS at 21 days, 600 mS at 56 days with variance 10% precast & 15% for cast in-situ
label | ○ Permeability: <20mm
label | ○ Water absorption: <6.5%
label | – Sulphite content: <4% by mass
label | – Alkali content: <2.5kg/m3
label | – Chloride content: As per table 5-1 of MS-41P
label | – Temperature rise: The lesser of: Thermal Control Plan limits
label | ○ <70°C maximum
label | ○ <40°C temperature rise from its fresh concrete casting temperature
label | METHOD - IANZ Lab tests
label | FREQUENCY/PROCESS HELD - Consistency: Slump test every batch
label | ○ 28 days compressive strength: 3 Cylinders (1x7day, 2x28 day per shift or per 75m3 poured (NZS 3104), whichever is more frequent.
label | ○ Shrinkage: Every 1,500m3 of concrete
label | ○ Permeability: Every 1,500m3 of concrete Water absorption: Every 1,500m3 of concrete Sulphite content: Every 1,500m3 of concrete
label | ○ Shrinkage: Every 1,500m3 of concrete
label | ○ Permeability: Every 1,500m3 of concrete Water absorption: Every 1,500m3 of concrete Sulphite content: Every 1,500m3 of concrete
label | ○ Temperature rise: Not applicable as pours are less than 0.9m thick (as per MPS Temperature Control Plan)
label | TYPE - WP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Lab Results. Witness point release after witnessing of in-situ/immediate tests and sampling for longer tests.
checkpoint | 5.2 - Concrete Curing
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - NZS 3109 Clause 7.8 MS-41P 11P
label | CONFORMANCE CRITERIA - Curing of cast-in-situ concrete elements shall be undertaken in accordance with the appropriate Material Specification
label | METHOD - Visually monitored on site as per thermal control plan
label | FREQUENCY/PROCESS HELD - Hourly during peak sun hours and as required elsewhere
label | TYPE - WP
label | ATTENDANCE REQUIRED - SEIPP
label | RECORDS OR CHECKLISTS - Post pour check sheet
checkpoint | 5.3 - Concrete finishes
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C4P - 4.1.6P DWG 2012036.900
label | CONFORMANCE CRITERIA - Concrete finishes to be in line with the design drawings and specification.
label | ○ Concrete finish to be U3/ F3 or approved finish where not PE lined.
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Post pour
label | TYPE - WP
label | ATTENDANCE REQUIRED - SEIPP
label | RECORDS OR CHECKLISTS - Post pour check sheet
checkpoint | 5.4 - Concrete Benching
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 2012034.161, DWG 2012034.183 CG-C4.2.1
label | CONFORMANCE CRITERIA - Benching slope shall be 1:12 minimum unless otherwise noted in the drawings.
label | ○ Plastering over the concrete finish is not accepted. The troweled finish is to be a U2 finish.
label | ○ Should have the same grade as walls and base slab.
label | METHOD - Visual inspection
label | FREQUENCY/PROCESS HELD - Post pour
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Post-pour check sheet
checkpoint | 5.5 - Concrete Grouting lid panel joints
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 2012036.908
label | CONFORMANCE CRITERIA - Ensure joint details are as per the drawings
label | METHOD - Visual inspection
label | FREQUENCY/PROCESS HELD - Before epoxy
label | TYPE - WP
label | ATTENDANCE REQUIRED - SEIPP
label | RECORDS OR CHECKLISTS - QA Check sheet
checkpoint | 5.6 - Post Pour Inspection
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - MS-41P
label | CONFORMANCE CRITERIA - Full post pour inspection review of the concrete finish to identify surface defects, ensuring the specified curing has been undertaken, concrete cover checks or any other defects identified or non-conformances.
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Post pour
label | TYPE - HP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Post pour check sheet
holdpoint | HOLD POINT
checkpoint | 5.7 - Concrete Repairs
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C4P-4.6.1.4P
label | CONFORMANCE CRITERIA - Concrete repair using resin as per concrete structures specification.
label | ○ As per GAJV-CEP-00272 Mangere Pump Station Defect Repair Procedure
label | METHOD - Visual Inspections
label | FREQUENCY/PROCESS HELD - Post Pour
label | TYPE - HP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Post pour check sheet
holdpoint | HOLD POINT
section | 6.0 - Construction: Construction PE Liner
checkpoint | 6.1 - PE Liner shop drawing
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - CG-C27P
label | CONFORMANCE CRITERIA - Shop drawing to be submitted to WSL
label | METHOD - Submission
label | FREQUENCY/PROCESS HELD - 4 weeks prior to installation
label | TYPE - HP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Shop drawing submission
holdpoint | HOLD POINT
checkpoint | 6.2 - Extrusion weld certificates
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C27P
label | CONFORMANCE CRITERIA - Welders’ certificates for welding
label | METHOD - Copy of certificates
label | FREQUENCY/PROCESS HELD - All welders
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Copy of certificates
checkpoint | 6.3 - PE Liner Prior To Pour
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C27P
label | CONFORMANCE CRITERIA - Final inspection of the liner to ensure its adequately restrained, no visible holes, no fixings left on the inside face, drainage lines are correctly positioned, no folds, bulges, all joints on the liner are adequately secured.
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Each pour
label | TYPE - HP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Pre-Pour Inspection
holdpoint | HOLD POINT
checkpoint | 6.4 - Extrusion weld testing
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C27P, ASTM D4437, ASTM D5641, DVS 2227-1
label | CONFORMANCE CRITERIA - As a minimum all site welds shall be tested.
label | METHOD - Either vacuum box testing or high voltage spark testing, Visual inspection
label | FREQUENCY/PROCESS HELD - All welds
label | TYPE - WP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - As recommended by the manufacturer, Checklist for visual inspection
checkpoint | 6.5 - Tapping Survey
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - AGRU Design & Installation Handbook. CG-C27P
label | CONFORMANCE CRITERIA - Tapping survey to identify voids
label | ○ Voids to be repaired as recommended by the manufacturer.
label | ○ Pages 24 & 34 of Design & Installation handbook.
label | METHOD - As recommended by the manufacturer. Rubber mallet delamination survey.
label | FREQUENCY/PROCESS HELD - As recommended by the manufacturer
label | TYPE - WP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Post pour check sheet
checkpoint | 6.6 - Liner repairs
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - AGRU Design & Installation Handbook. CG-C27P, DVS 2227-1
label | CONFORMANCE CRITERIA - As recommended by the manufacturer
label | ○ Clearly mark out areas for repair
label | ○ Extrusion welding
label | ○ As per GAJV-CEP-00272 Mangere Pump Station Defect Repair Procedure
label | METHOD - Visual Inspection. Surfacing welds. Blanks. Panel strips.
label | FREQUENCY/PROCESS HELD - As recommended by the manufacturer
label | TYPE - HP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - PE Liner Checklist
holdpoint | HOLD POINT
section | 7.0 - Post Construction
checkpoint | 7.1 - Final As built including PE membrane
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - IFC Drawings – 2012036 series, 2012034 series
label | CONFORMANCE CRITERIA - Survey
label | METHOD - Survey
label | FREQUENCY/PROCESS HELD - At completion
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - As built drawings
checkpoint | 7.2 - Hydrostatic testing
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - GC_1 10.5.2 D)
label | CONFORMANCE CRITERIA - Infiltration test for manholes over 3.5m deep
label | ○ There are no visible leaks, wet patches or “sweating” at any of the pipe penetrations, seals or riser joints.
label | METHOD - Infiltration test
label | FREQUENCY/PROCESS HELD - At completion
label | TYPE - HP
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Test record sheet
holdpoint | HOLD POINT
checkpoint | 7.3 - Backfilling – 7/3
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - GAJV-RFI-002719
label | CONFORMANCE CRITERIA - Compacted to 90% of Maximum Dry Density
label | METHOD - NDM Test
label | FREQUENCY/PROCESS HELD - 1 Test per 500mm layer surrounding chamber
label | TYPE - HP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - NDM Test Results
holdpoint | HOLD POINT
checkpoint | 7.4 - Concrete Testing – Flowable Fill (Consistency, 28-day compressive strength)
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - GAJV-RFI-002719
label | ○ Consistency: NZS 3109
label | ○ 28-day compressive strength: NZS 3109 Section 9 and NZS 3112
label | CONFORMANCE CRITERIA - Consistency: +/- 40mm - NZS 3109
label | ○ 28-day compressive strength: 5 MPa
label | METHOD - IANZ Lab tests
label | FREQUENCY/PROCESS HELD - Consistency: Slump test every batch
label | ○ 28 days compressive strength: 3 Cylinders (1x7day, 2x28 day per shift
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Lab Results. Witness point release after witnessing of in-situ/immediate tests and sampling for longer tests.
checkpoint | CONFORMANCE / VERIFICATION STATEMENT
label | This closed lot conforms in all respects with the standards and requirements specified in the Contract Documents. The lot verification records are complete, and any non-conformances have been closed out in accordance with the Projects requirements.
label | Construction Lot checked by the Senior Project Engineer responsible for the works
textbox | Senior Project Engineer - PRINT NAME:
date | Senior Project Engineer - DATE:
label | Construction Lot verified and closed by Quality Management Representative
textbox | Quality Management Representative - PRINT NAME:
date | Quality Management Representative - DATE:
label | Independent Verification Review (if required) by:
textbox | PRINT NAME:
date | DATE:
holdpoint | ADD SIGNATURE
checklist | GAJV-ITP-00215_3.0 - Installation of DN2100 Concrete Bypass Pipe | itp |  |  |  |  | GAJV-ITP-00215_3.0 - Installation of DN2100 Concrete Bypass Pipe
section | 1.0 - Preliminaries
checkpoint | 1.1 - Check - Drawings are IFC and current
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Ensure the latest IFC drawings are used and available onsite
label | CONFORMANCE CRITERIA - Sighting of drawings
label | METHOD - Retain drawings
label | FREQUENCY/PROCESS HELD - Before project execution
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - DWG register with the drawing revision.
holdpoint | HOLD POINT
checkpoint | 1.2 - Check - CEP, SWMS, TMP and ESCP in place and signed off by personnel
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Ensure latest IFC plans are used and available onsite
label | CONFORMANCE CRITERIA - Sighting of plans
label | METHOD - Retain plans
label | FREQUENCY/PROCESS HELD - Before project execution
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Plan register with the revision used
holdpoint | HOLD POINT
section | 2.0 - Materials (approval)
checkpoint | 2.1 - Concrete Pipe DN2100
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - IFC drawings
label | ○ 2012034.174
label | ○ 2012034.181
label | ○ 2012034.183
label | ○ MS-03
label | CONFORMANCE CRITERIA - RCRRJ Class 4
label | ○ Pipe free from defects and meets requirements of specification
label | METHOD - Visual inspection
label | FREQUENCY/PROCESS HELD - Each delivery
label | TYPE - MAR
label | ATTENDANCE REQUIRED - WSL GAJV
label | RECORDS OR CHECKLISTS - Pipe Inspection Checklist Delivery dockets, Manufacturer’s QA Photos
checkpoint | 2.2 - Pipe Surround/Backfilling
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - 2012034.174
label | CONFORMANCE CRITERIA - Approved DM7/3
label | METHOD - Material order review
label | FREQUENCY/PROCESS HELD - Before procurement
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Delivery dockets, Quarry material test results for PSD, MDD
checkpoint | 2.3 - Stabilised sand (if required to replace undercut)
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - 2012034.174
label | CONFORMANCE CRITERIA - Approved stabilised sand
label | METHOD - Material order review
label | FREQUENCY/PROCESS HELD - Before procurement
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Delivery dockets, Quarry material test results for PSD, MDD
checkpoint | 2.4 - Flowable fill to below pipe and haunching
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - 2012034.174
label | CONFORMANCE CRITERIA - To be 5Mpa as per drawing
label | METHOD - To be 5Mpa as per drawing
label | FREQUENCY/PROCESS HELD - Prior to commencement of work
label | TYPE - MAR
label | ATTENDANCE REQUIRED - WSL GAJV
label | RECORDS OR CHECKLISTS - Delivery dockets Mix design certificate
checkpoint | 2.5 - Underside of pipe - Wrapping layer
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - 2012034.174
label | CONFORMANCE CRITERIA - ABELFLEX or approved closed cell foam
label | METHOD - Material order review
label | FREQUENCY/PROCESS HELD - Prior to commencement of work
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Delivery Dockets
checkpoint | 2.6 - Subbase material
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - WSL GCCS – C1.4, WSL CG C2.16 2012034.174 ATCOP
label | CONFORMANCE CRITERIA - GAP 65
label | ○ Subbase material shall consist of clean crushed rock, all passing 65mm standard sieve in accordance with ATCOP section 16
label | METHOD - Material order review
label | FREQUENCY/PROCESS HELD - Before procurement
label | TYPE - MAR
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Delivery dockets, Quarry material test results for PSD, MDD
section | 3.0 - Construction
checkpoint | 3.1 - Survey and set out
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Drawings
label | ○ 2012034.174
label | ○ 2012034.181
label | ○ 2012034.183
label | CONFORMANCE CRITERIA - Survey and set out as per design drawings.
label | METHOD - Survey set out
label | FREQUENCY/PROCESS HELD - Each line
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Survey request Aconex mail
checkpoint | 3.2 - Excavate Trench
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - Drawings 2012034.174, WSL GCCS – C2.9
label | CONFORMANCE CRITERIA - Trench excavated as per design drawing.
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Ongoing
label | TYPE - S
label | ATTENDANCE REQUIRED - S/C
label | RECORDS OR CHECKLISTS - Pipe laying checklist
checkpoint | 3.3 - Trench foundation (1)
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - Drawing: 2012034.174
label | CONFORMANCE CRITERIA - Subgrade at the base of the trench is to have a minimum of 30Kpa. If the minimum is not achieved the base of the trench requires undercut until 30KPa achieved.
label | METHOD - Shear Vane
label | FREQUENCY/PROCESS HELD - Every 15m.
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Field test results
holdpoint | HOLD POINT
checkpoint | 3.3 - Trench foundation (2)
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - Drawing: 2012034.174
label | CONFORMANCE CRITERIA - Subgrade at the base of the trench is to have a minimum of 30Kpa. If the minimum is not achieved the base of the trench requires undercut until 30KPa achieved.
label | METHOD - Shear Vane
label | FREQUENCY/PROCESS HELD - Every 15m.
label | TYPE - W
label | ATTENDANCE REQUIRED - WSL
label | RECORDS OR CHECKLISTS - Field test results
checkpoint | 3.4 - Place stabilised sand (if required)
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - Drawing: 2012034.174 GC C3.1.2
label | CONFORMANCE CRITERIA - Compacted to 95% of Maximum Dry Density
label | METHOD - NDM Test
label | FREQUENCY/PROCESS HELD - 1 Test per 230mm layer per 20m of trench length
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - NDM test results
holdpoint | HOLD POINT
checkpoint | 3.5 - Laying pipes
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - Drawings
label | ○ 2012034.181
label | ○ 2012034.183
label | ○ WSL GCCS – C3.9.3
label | CONFORMANCE CRITERIA - Pipes installed to flat gradient and to design alignment
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Each line
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Pipe laying checklist
checkpoint | 3.6 - Wrap Install
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - Drawing: 2012034.174
label | CONFORMANCE CRITERIA - Installed as required on drawings and to manufacturer’s instructions
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Each line
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Pipe laying checklist
checkpoint | 3.7 - Jointing pipes
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - Manufactures Specification CG-C18P Section 18P, CG 10.5.2
label | CONFORMANCE CRITERIA - Ensure the rubber sealing ring is installed and seated appropriately on the initial pipe groove. Deflection should not exceed 0.5º to ensure the joint is sealed
label | ○ Leakage testing as per GAJV-RFI-002693 – Pipe joint testing to 24kPa, if there are no visible leaks and pressure holds or drops no less than 7kPa in 5 seconds then acceptable.
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Each joint
label | TYPE - H
label | ATTENDANCE REQUIRED - WSL GAJV
label | RECORDS OR CHECKLISTS - Pipeline checklist Test results
holdpoint | HOLD POINT
checkpoint | 3.8 - Placing sandbags
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - Drawing: 2012034.174
label | CONFORMANCE CRITERIA - Sandbags in location as required.
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Each location
label | TYPE - S
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Pipe laying checklist Photos
checkpoint | 3.9 - Flowable fill pour
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - Drawing: 2012034.174
label | CONFORMANCE CRITERIA - Sandbags in location before pour as per drawing. Flowable fill min 5MPa
label | ○ 300mm surrounding pipe required.
label | METHOD - Review of results
label | FREQUENCY/PROCESS HELD - Each pour
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Concrete delivery dockets, IANZ Lab report
checkpoint | 3.10 - DM7/3 Backfill
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - Drawing: 2012034.174 GC C3.1.2
label | CONFORMANCE CRITERIA - Compacted to 95% of Maximum Dry Density
label | METHOD - NDM Test
label | FREQUENCY/PROCESS HELD - 1 Test per 230mm layer per 20m of trench length
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - NDM test results
holdpoint | HOLD POINT
checkpoint | 3.11 - Warning Strip
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - Drawing: 2012034.174, WSL GCCS – C3.1
label | CONFORMANCE CRITERIA - Continuous length of cream coloured warning strip installed. Warning strip to be 100mm wide at 450mm above pipeline. The wording in black on the warning strip shall be “caution-sewer below” as per note 2 on Drawing: 2012034.174
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Entire line
label | TYPE - W
label | ATTENDANCE REQUIRED - S/C WSL GAJV
label | RECORDS OR CHECKLISTS - Pipeline checklist
checkpoint | 3.12 - GAP65 Subbase Compaction
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - Drawing: 2012034.174 GC C3.1.2
label | CONFORMANCE CRITERIA - Compacted to 95% of Maximum Dry Density
label | METHOD - NDM Test
label | FREQUENCY/PROCESS HELD - 1 Test per 230mm layer per 20m of trench length
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - NDM test results
holdpoint | HOLD POINT
section | 4.0 - Post Construction
checkpoint | 4.1 - CCTV Inspection
label | RESPONSIBILITY - S/C
label | REQUIREMENTS / REFERENCE - WSL GCCS
label | CONFORMANCE CRITERIA - On completion the line shall be CCTV inspected for defects
label | METHOD - CCTV Inspection
label | FREQUENCY/PROCESS HELD - Entire line
label | TYPE - W
label | ATTENDANCE REQUIRED - WSL GAJV
label | RECORDS OR CHECKLISTS - CCTV inspection form, CCTV video and report from CCTV Subcontractor
checkpoint | 4.2 - As built records
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - WSL GCCS – C3.1.1
label | CONFORMANCE CRITERIA - Pipe shall be installed to the line and level required on the specific drawings. The position tolerance for pipe laying at any point along the length of the installation shall be within +/- 30mm from the specified design.
label | METHOD - Survey
label | FREQUENCY/PROCESS HELD - Each line
label | TYPE - H
label | ATTENDANCE REQUIRED - WSL GAJV
label | RECORDS OR CHECKLISTS - As built
holdpoint | HOLD POINT
checkpoint | CONFORMANCE / VERIFICATION STATEMENT
label | This closed lot conforms in all respects with the standards and requirements specified in the Contract Documents. The lot verification records are complete, and any non-conformances have been closed out in accordance with the Projects requirements.
label | Construction Lot checked by the Senior Project Engineer responsible for the works
textbox | Senior Project Engineer - PRINT NAME:
date | Senior Project Engineer - DATE:
label | Construction Lot verified and closed by Quality Management Representative
textbox | Quality Management Representative - PRINT NAME:
date | Quality Management Representative - DATE:
label | Independent Verification Review (if required) by:
textbox | PRINT NAME:
date | DATE:
holdpoint | ADD SIGNATURE
checklist | GAJV-ITP-00283_3.0 - SITE REINSTATEMENT | itp |  |  |  |  | GAJV-ITP-00283_3.0 - SITE REINSTATEMENT
section | 1.0 - Preliminaries
checkpoint | 1.1 - Check CEP and SWMS are in place and signed off by personnel
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - N/A
label | CONFORMANCE CRITERIA - GAJV procedures.
label | METHOD - Document Review
label | FREQUENCY/PROCESS HELD - Each Lot/ Construction start
label | TYPE - HP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Copy of SWMS and CEP on site and signed by site personal.
holdpoint | HOLD POINT
checkpoint | 1.2 - Check Drawings are IFC and current
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - N/A
label | CONFORMANCE CRITERIA - IFC Drawings and the current version used.
label | ○ Site restoration plans to be approved by Council prior to works
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Before project execution
label | TYPE - HP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Copy of IFC drawings onsite DWG register
holdpoint | HOLD POINT
checkpoint | 1.3 - Legislative requirements – Work Safe notifiable works documents submitted and verified
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - WSL CS-C01P-4.1P WSL
label | ○ General Civil Construction Standards C2.7
label | CONFORMANCE CRITERIA - Documents (Health and safety at Work Act 2015) as per WorkSafe requirements cited, reviewed, and retained on site. Copy of notification supplied to Watercare.
label | METHOD - When required
label | FREQUENCY/PROCESS HELD - Prior to construction
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV WSL
label | RECORDS OR CHECKLISTS - Notification to work safe - if applicable
checkpoint | 1.4 - Service Location
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - GC C Standard Version 1
label | CONFORMANCE CRITERIA - Clearly identify existing services in proximity of works.
label | METHOD - Document review, Site mark out
label | FREQUENCY/PROCESS HELD - Before works commencement & During Construction
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Survey Request and As-built drawing of services
section | 2.0 - Materials (approval)
checkpoint | 2.1 - Soil for plantation backfill
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - IFC Drawings
label | CONFORMANCE CRITERIA - Clearly identify soil type before placement.
label | METHOD - Docket review
label | FREQUENCY/PROCESS HELD - Prior to construction
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Delivery Dockets
checkpoint | 2.2 - Mulch (for playground – Miranda site)
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - IFC Drawings
label | CONFORMANCE CRITERIA - Clearly identify mulch type before placement.
label | METHOD - Docket review
label | FREQUENCY/PROCESS HELD - Prior to construction
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Delivery Dockets
checkpoint | 2.3 - Tree Reinstatement
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - CEP
label | CONFORMANCE CRITERIA - Specific tree to be reinstated.
label | ○ Native trees to be eco sourced.
label | METHOD - Delivery docket
label | FREQUENCY/PROCESS HELD - Prior to placement
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Delivery Dockets
section | 3.0 - Site Excavation & Temporary Works Removal
checkpoint | 3.1 - Survey Setout of project boundaries: Pothole location for tree reinstatement, Site reinstatement boundary
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Work Methods Statement, CS-C01P General Requirements 29.3P
label | CONFORMANCE CRITERIA - Surveyed line and level in accordance with drawings
label | METHOD - Survey Record
label | FREQUENCY/PROCESS HELD - Prior to construction
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Photos of Setout, Survey report
checkpoint | 3.2 - Excavation depth to be determined
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Work Methods Statement
label | CONFORMANCE CRITERIA - Geologist to determine satisfactory minimum soil depth required for future plant growth
label | METHOD - Geologist Report
label | FREQUENCY/PROCESS HELD - Prior to construction
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV WSL
label | RECORDS OR CHECKLISTS - Survey As Built
checkpoint | 3.3 - Spoil removal
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Work Methods Statement
label | CONFORMANCE CRITERIA - Any material removed from site to be sent to appropriate disposal destination as determined by spoil removal team
label | METHOD - Spoil Report
label | FREQUENCY/PROCESS HELD - Prior to construction
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Spoil removal dockets
checkpoint | 3.4 - Temporary Works Removal – (Flood Walls, Capping Beams, SBP etc.)
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - IFC Drawings
label | CONFORMANCE CRITERIA - Temporary Works to be removed to 1.5m below Finished Ground Level
label | METHOD - Survey Record
label | FREQUENCY/PROCESS HELD - Final As Built
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Survey As Built
section | 4.0 - Tree Plantation & Reinstatement
checkpoint | 4.1 - SITE PREPARATION: Site Engineer and subcontractor to confirm site ready for reinstatement
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Work Methods Statement, IFC Drawings
label | CONFORMANCE CRITERIA - Area cleared in accordance with drawings.
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Prior to construction
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - ITP signed
checkpoint | 4.2 - POTHOLE: Ensure that potholes are the correct positioned in spacing, depth and diameter prior to reinstating tree
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Work Methods Statement, IFC Drawings
label | CONFORMANCE CRITERIA - Hole depth, diameter and spacing dug out as specified
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Prior to construction
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - ITP signed, photographs of the potholes
checkpoint | 4.3 - SUREPAVE INSTALLATION
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - IFC Drawings GAJV-RPT-00201 Section 6.3.1
label | CONFORMANCE CRITERIA - Subbase testing to achieve a minimum CBR of 3%
label | ○ Installation as per Manufacturers Guidelines
label | METHOD - Visual Inspection DCP/Scala Penetrometer
label | FREQUENCY/PROCESS HELD - During Installation
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Photos Test results
checkpoint | 4.4 - Vehicle Crossings, Driveways, Footpaths, Kerb & Channel
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - IFC Drawings CEP, ATCOP
label | CONFORMANCE CRITERIA - Auckland Transport Code of Practice
label | ○ Driveways will need to have a vehicle crossing permit and be inspected by council.
label | METHOD - Document review
label | FREQUENCY/PROCESS HELD - Prior construction
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV WSL
label | RECORDS OR CHECKLISTS - Dockets, Inspection check sheet
checkpoint | 4.5 - Air duct/vent stack installation
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - IFC Drawings CEP
label | CONFORMANCE CRITERIA - Ensure minimum vertical and horizontal spacing as per IFC drawings
label | METHOD - Delivery dockets
label | FREQUENCY/PROCESS HELD - Prior construction
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Visual inspection, material certs and photographs
checkpoint | 4.6 - Road restoration
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - IFC Drawings ATCOP, WSL-LETTER-001346
label | CONFORMANCE CRITERIA - Roads will be restored to Auckland Transport requirements.
label | ○ Paving reinstatement to match existing surfaces.
label | ○ Over 10m2 to be laid by paver layer machine.
label | ○ Backfill test to min 95% MDD
label | ○ Contractor to organise a joint inspection of the relevant works with the Engineer
label | METHOD - Nuclear Densometer
label | FREQUENCY/PROCESS HELD - During construction
label | TYPE - HP
label | ATTENDANCE REQUIRED - GAJV WSL
label | RECORDS OR CHECKLISTS - Delivery Dockets, IANZ NDM Lab Test Results
holdpoint | HOLD POINT
checkpoint | 4.7 - Topsoil specifications
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - IFC Drawings
label | ○ GAJV-RPT-00201 Section 7.3.3
label | ○ ATCOP Section 14.4.2
label | CONFORMANCE CRITERIA - The topsoil shall be screened to a 12mm maximum particle size and shall not contain any foreign matter.
label | ○ Topsoil should have an acidity range of pH 5.5 to 7.5 and be suitable for the plant species being used.
label | METHOD - Lab test review
label | FREQUENCY/PROCESS HELD - Prior Installation
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV WSL
label | RECORDS OR CHECKLISTS - Delivery Docket, topsoil lab results, photos
checkpoint | 4.8 - Bollard installation (If applicable)
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - IFC Drawings, Auckland Parkland Design Guideline
label | CONFORMANCE CRITERIA - As per IFC drawings
label | ○ Bollards should be spaced at gaps of a maximum 1.5m
label | METHOD - Visual / measure on site
label | FREQUENCY/PROCESS HELD - During Installation
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Delivery Docket, Photos
checkpoint | 4.9 - Planter installation (If applicable)
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - IFC Drawings
label | CONFORMANCE CRITERIA - As per IFC drawings
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Post Construction
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Photos
checkpoint | 4.10 - Rain garden and/or swale installation (If applicable)
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - IFC Drawings
label | CONFORMANCE CRITERIA - As per IFC drawings
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Post Construction
label | TYPE - WP
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Photos
section | 5.0 - Post Construction
checkpoint | 5.1 - Final As built
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - IFC Drawings
label | CONFORMANCE CRITERIA - Survey as built
label | METHOD - Survey
label | FREQUENCY/PROCESS HELD - Reinstated area
label | TYPE - WP
label | ATTENDANCE REQUIRED - WSL
label | RECORDS OR CHECKLISTS - As built
checkpoint | CONFORMANCE / VERIFICATION STATEMENT
label | This closed lot conforms in all respects with the standards and requirements specified in the Contract Documents. The lot verification records are complete, and any non-conformances have been closed out in accordance with the Projects requirements.
label | Construction Lot checked by the Senior Project Engineer responsible for the works
textbox | Senior Project Engineer - PRINT NAME:
date | Senior Project Engineer - DATE:
label | Construction Lot verified and closed by Quality Management Representative
textbox | Quality Management Representative - PRINT NAME:
date | Quality Management Representative - DATE:
label | Independent Verification Review (if required) by:
textbox | PRINT NAME:
date | DATE:
holdpoint | ADD SIGNATURE
checklist | GAJV-ITP-00329_3.0 - Confluence Chamber Precast Elements | itp |  |  |  |  | GAJV-ITP-00329_3.0 - Confluence Chamber Precast Elements
section | 1.0 - Preliminaries
checkpoint | 1.1 - Check - Drawings are IFC and current
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Ensure latest IFC drawings are used and available onsite
label | CONFORMANCE CRITERIA - Sighting of drawings
label | METHOD - Retain Drawings
label | FREQUENCY/PROCESS HELD - Before project execution
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - DWG register with the drawing revision.
holdpoint | HOLD POINT
checkpoint | 1.2 - Check – Shop Drawings
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - Ensure latest IFC drawings and are approved by GAJV
label | CONFORMANCE CRITERIA - Sighting of drawings
label | METHOD - Retain Drawings
label | FREQUENCY/PROCESS HELD - Before project execution
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - DWG register with the drawing revision.
holdpoint | HOLD POINT
section | 2.0 - Materials
checkpoint | 2.1 - Concrete
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - 2012034 & 2012036, DWG Series, MS-18P
label | CONFORMANCE CRITERIA - Approved mix used – Allied/Holcim Mix 451PFA40CI
label | METHOD - Review
label | FREQUENCY/PROCESS HELD - Each Mix
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material certificate
holdpoint | HOLD POINT
checkpoint | 2.2 - Reinforcing Steel
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - DWG 2012036 Series NZS 4671/ 3109, GC-C4P – 4.1 and 4.1.1.10
label | CONFORMANCE CRITERIA - Grade 500E
label | ○ Produced using micro-alloy process
label | METHOD - Review
label | FREQUENCY/PROCESS HELD - Each batch
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material certificate
checkpoint | 2.3 - Bearing Strip
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - 20120036.863 DWG
label | CONFORMANCE CRITERIA - FOSROC Cellfix or approved alternative
label | METHOD - Review
label | FREQUENCY/PROCESS HELD - Each delivery
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Delivery dockets
checkpoint | 2.4 - Gatic frames & Grates – Roof slabs only
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - 20120036 DWG Series
label | CONFORMANCE CRITERIA - Gatic covers delivered as per the drawings
label | METHOD - Review
label | FREQUENCY/PROCESS HELD - Each delivery
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Delivery dockets
checkpoint | 2.5 - PE Liner & Weld Rod
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-27P Table 5.1
label | CONFORMANCE CRITERIA - Technical data sheets
label | ○ Manufacturers Certificates of compliance
label | METHOD - Review
label | FREQUENCY/PROCESS HELD - Prior to commencement of work
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material Cert
checkpoint | 2.6 - PEF Rod & Sealant
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - GAJV-DCRQST-000344
label | CONFORMANCE CRITERIA - Closed cell Polyethene foam backing strip – FOSROC expandafoam or approved similar.
label | ○ Fosroc Nitoseal SC600 or approved equivalent
label | METHOD - Review
label | FREQUENCY/PROCESS HELD - Each delivery
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Delivery dockets
checkpoint | 2.7 - Non-shrink grout
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - 2012036.863
label | CONFORMANCE CRITERIA - High strength non-shrink grout
label | METHOD - Review
label | FREQUENCY/PROCESS HELD - Prior to commencement of work
label | TYPE - MAR
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Material Approval Request
checkpoint | 2.8 - Epoxy (for dowel bar post install)
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - 2012036.863
label | CONFORMANCE CRITERIA - Hilti HIT-RE-500 or approved similar
label | METHOD - Review
label | FREQUENCY/PROCESS HELD - Each delivery
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Delivery dockets
checkpoint | 2.9 - Galvanised dowel bars
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - 2012036.863
label | CONFORMANCE CRITERIA - 600mm long hot dip galvanised bars
label | METHOD - Review
label | FREQUENCY/PROCESS HELD - Each delivery
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Material certificate
section | 3.0 - Concrete Element Construction
checkpoint | 3.1 - Reinforcement Placement
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C4P – 4.1.2.12P
label | ○ CG-C4P – 4.1.1
label | ○ 2012036 DWG Series Approved shop drawings
label | CONFORMANCE CRITERIA - Ensure that the placed reinforcement complies in all respects with the Design Drawings and Specification
label | ○ Minimum cover over reinforcement shall be as noted on the Design Drawings
label | ○ Lap lengths/cover shall generally be as detailed on the Design Drawings or 2012053 series
label | METHOD - Visual inspection
label | FREQUENCY/PROCESS HELD - After steel placement
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV/WSL
label | RECORDS OR CHECKLISTS - Pre-pour checksheet, Precast HQ QA Pack
holdpoint | HOLD POINT
checkpoint | 3.2 - Formwork/moulds
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C4P – 4.1.2.12P
label | ○ MS-41P – 12.1P
label | ○ CG-C4P – 4.5P
label | ○ NZS3109 Approved shop drawings
label | CONFORMANCE CRITERIA - Dimensional tolerances as per NZS 3109 Table 5.1
label | ○ Formwork to be treated with release agent where in direct contact with concrete
label | ○ Exposed concrete edges to have minimum 10mm chamfer unless otherwise shown on the drawings
label | ○ Formwork must provide cast surface in line with concrete finish requirements (U2 for floor & roof slabs)
label | METHOD - Visual Inspections
label | FREQUENCY/PROCESS HELD - Prior to concrete pour
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Pre-pour checksheet, Precast HQ QA Pack
holdpoint | HOLD POINT
checkpoint | 3.3 - Penetrations and Cast-in Items (including PE liner)
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C4P – 4.1.7P
label | ○ Approved shop drawings CG-C27P 6.2P
label | CONFORMANCE CRITERIA - Penetrations shall be as per the design drawings
label | ○ Installation of CPL to form a smooth continuous surface free of sags, wrinkles bubbles and bulges.
label | METHOD - Visual Inspections
label | FREQUENCY/PROCESS HELD - Prior to concrete pour
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV/WSL
label | RECORDS OR CHECKLISTS - Pre-pour checksheet, Precast HQ QA Pack
holdpoint | HOLD POINT
checkpoint | 3.4 - Concrete Testing (Consistency, 28-day compressive strength, Shrinkage, Permeability, Water absorption, Sulphite content, Alkali content, Chloride content, Temperature rise)
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - MS-41P - 5P MS-41P - 12P
label | ○ MS-41P – table 6.1P
label | ○ Consistency: NZS 3109 and NZS 3112
label | ○ 28-day compressive strength: NZS 3109 Section 9 and NZS 3112
label | ○ Shrinkage: AS 1012.13
label | ○ Permeability: DIN 1048
label | ○ Water absorption: AS 4058 Appendix F
label | ○ Sulphite content: AS 1012.14
label | ○ Alkali content: Chloride content: AS 1012.14
label | ○ Temperature rise: Not applicable as pours are less than 0.9m thick (as per MPS Temperature Control Plan)
label | CONFORMANCE CRITERIA - Consistency: For water retaining structures, slump tolerances shall be half those given in Table 9.1 of NZS 3109
label | ○ 28-day compressive strength: 45 MPa
label | ○ Shrinkage: 430mS at 21 days, 600 mS at 56 days with variance 10% precast & 15% for cast in-situ
label | ○ Permeability: <20mm
label | ○ Water absorption: <6.5%
label | – Sulphite content: <4% by mass
label | – Alkali content: <2.5kg/m3
label | – Chloride content: As per table 5-1 of MS-41P
label | – Temperature rise: The lesser of: Thermal Control Plan limits
label | ○ <70°C maximum
label | ○ <40°C temperature rise from its fresh concrete casting temperature
label | METHOD - IANZ Lab tests
label | FREQUENCY/PROCESS HELD - Consistency: Slump test every batch
label | ○ 28 days compressive strength: 3 Cylinders (1x7day, 2x28 day per shift or per 75m3 poured (NZS 3104), whichever is more frequent.
label | ○ Shrinkage: Every 1,500m3 of concrete
label | ○ Permeability: Every 1,500m3 of concrete Water absorption: Every 1,500m3 of concrete Sulphite content: Every 1,500m3 of concrete
label | ○ Shrinkage: Every 1,500m3 of concrete
label | ○ Permeability: Every 1,500m3 of concrete Water absorption: Every 1,500m3 of concrete
label | ○ Sulphite content: Every 1,500m3 of concrete
label | ○ Temperature rise: Not applicable as pours are less than 0.9m thick (as per MPS Temperature Control Plan)
label | TYPE - W
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Precast HQ QA Pack
checkpoint | 3.5 - Construction Joints (Baffle wall & Beam only)
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C4P - 4.1.2P
label | CONFORMANCE CRITERIA - Construction joints shall conform to NZS 3109, Clause 5.6.3, type B
label | ○ Joint position shall be as shown on the Design Drawings unless otherwise agreed with the engineer
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Post Pour
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Post pour check sheet, Precast HQ QA Pack
checkpoint | 3.6 - Concrete Curing
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - MS-41P - 11.1
label | ○ CG-C4P – 4.1.12.6P
label | ○ NZS 3109 Clause 7.8
label | CONFORMANCE CRITERIA - All concrete shall be properly and adequately cured.
label | ○ Concrete shall be maintained at a reasonable constant temperature with minimum moisture loss for the curing period
label | ○ The curing period shall be 7 days
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Post Pour
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Post pour check sheet, Precast HQ QA Pack
checkpoint | 3.7 - Concrete Finishes
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C4P - 4.1.6P
label | ○ CG-C4P – 4.1.2.12P
label | CONFORMANCE CRITERIA - Concrete finishes to be in line with the design drawings and specification.
label | ○ Full post pour inspection review of the concrete finish to identify surface defects, concrete cover checks or any other defects identified or non-conformances.
label | ○ Repair work shall be carried out using a method approved by the Engineer
label | ○ Penetrations and cast-in items to be measured and location confirmed
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Post Pour
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Post pour check sheet, Precast HQ QA Pack
section | 4.0 - Installation
checkpoint | 4.1 - Survey and Set out
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - 2012034 & 2012036 DWG Series
label | CONFORMANCE CRITERIA - Set out to be as per drawings.
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - As required
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - N/A
checkpoint | 4.2 - Precast inspection (delivery)
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C4P – 4.1.2.12P
label | ○ Approved shop drawings
label | CONFORMANCE CRITERIA - Precast units shall be handled in such a manner that will not cause damage of any kind.
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Each delivery
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV/WSL
label | RECORDS OR CHECKLISTS - Post pour check sheet
checkpoint | 4.3 - PE liner inspection
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C27P 4.5P
label | ○ CG-C27P 5.1P
label | CONFORMANCE CRITERIA - Tapping survey completed to identify voids
label | ○ Surface inspection of The CPL. CPL shall be free from cracks, cleavages, or other defects.
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Post Pour
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV/WSL
label | RECORDS OR CHECKLISTS - Post pour check sheet
holdpoint | HOLD POINT
checkpoint | 4.4 - PE extrusion weld certificates
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C27P
label | CONFORMANCE CRITERIA - Welders PE extrusion certs
label | METHOD - Copy of Certificate
label | FREQUENCY/PROCESS HELD - All welders
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Copy of certificate
checkpoint | 4.5 - PE extrusion weld testing
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - CG-C27P
label | ○ ASTM D4437, ASTM D5641
label | ○ DVS2227
label | CONFORMANCE CRITERIA - All site welds shall be tested
label | METHOD - High voltage spark test, Visual inspection
label | FREQUENCY/PROCESS HELD - All welds
label | TYPE - W
label | ATTENDANCE REQUIRED - WSL/GAJV
label | RECORDS OR CHECKLISTS - Visual Inspection
checkpoint | 4.6 - Gatic Cover Installation (Post-installed)
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - Gatic installation guides
label | CONFORMANCE CRITERIA - Installation as per the Gatic installation guidelines
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Each frame & cover
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Installation checklist
checkpoint | 4.7 - Precast installation
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - 2012034 & 2012036 DWG Series
label | CONFORMANCE CRITERIA - Bearing strip in position
label | ○ Unit sitting level/plumb
label | ○ Unit positioned in the correct location
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - After Installation
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Installation Checklist
checkpoint | 4.8 - Dowel bar installation (drill & epoxy fix) (1)
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - As per manufacturer’s installation instructions
label | CONFORMANCE CRITERIA - Hole cored to correct diameter and depth
label | ○ Hole clean and free of loose debris
label | ○ Epoxy placed in the hole and dowel bar installed to correct depth
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Prior to placement of epoxy
label | TYPE - W
label | ATTENDANCE REQUIRED - WSL
label | RECORDS OR CHECKLISTS - Installation Checklist
checkpoint | 4.8 - Dowel bar installation (drill & epoxy fix) (2)
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - As per manufacturer’s installation instructions
label | CONFORMANCE CRITERIA - Hole cored to correct diameter and depth
label | ○ Hole clean and free of loose debris
label | ○ Epoxy placed in the hole and dowel bar installed to correct depth
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Prior to placement of epoxy
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Installation Checklist
holdpoint | HOLD POINT
checkpoint | 4.9 - Grouting of lifting points & dowel bar connections
label | RESPONSIBILITY - SEIPP
label | REQUIREMENTS / REFERENCE - 2012036.904 note Manufacturer’s installation instructions
label | CONFORMANCE CRITERIA - Grout lifting eyes and dowels with non- shrink grout
label | ○ Area to be free of dust
label | METHOD - Visual Inspection
label | FREQUENCY/PROCESS HELD - Each pour
label | TYPE - W
label | ATTENDANCE REQUIRED - GAJV
label | RECORDS OR CHECKLISTS - Installation Checklist
section | 5.0 - Post Construction
checkpoint | 5.1 - As built records
label | RESPONSIBILITY - GAJV
label | REQUIREMENTS / REFERENCE - Watercare Standard Specification 225.31
label | CONFORMANCE CRITERIA - Tables 5.1 & 5.2 of NZS 3109 – (+-10mm)
label | METHOD - Survey asbuilt
label | FREQUENCY/PROCESS HELD - At completion
label | TYPE - H
label | ATTENDANCE REQUIRED - GAJV/WSL
label | RECORDS OR CHECKLISTS - As built records
holdpoint | HOLD POINT
checkpoint | CONFORMANCE / VERIFICATION STATEMENT
label | This closed lot conforms in all respects with the standards and requirements specified in the Contract Documents. The lot verification records are complete, and any non-conformances have been closed out in accordance with the Projects requirements.
label | Construction Lot checked by the Senior Project Engineer responsible for the works
textbox | Senior Project Engineer - PRINT NAME:
date | Senior Project Engineer - DATE:
label | Construction Lot verified and closed by Quality Management Representative
textbox | Quality Management Representative - PRINT NAME:
date | Quality Management Representative - DATE:
label | Independent Verification Review (if required) by:
textbox | PRINT NAME:
date | DATE:
holdpoint | ADD SIGNATURE