## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | AES-NZ1005-STE-ITP-PMT-0025 - Combined Services Fire Hydrostatic Pressure Test |  |  |  |  | Yes | AES-NZ1005-STE-ITP-PMT-0025 - Combined Services Fire Hydrostatic Pressure Test | 04cb4854-68c5-41cc-b95a-c903ee335c35
checkpoint-group |  |  | section | MATERIAL COMPLIANCE
checkpoint-status |  |  | checkpoint | RDM & Consent Approval - CPB Hold Point
label | bab2db0e-7948-589e-9b92-8a802c084e72 |  | note | CRITERIA - RDM approval tracker Consent approval tracker
checkpoint-status |  |  | checkpoint | General - CPB Hold Point
label | e27ffffb-b691-5b73-ad5c-d794df089099 |  | note | CRITERIA - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
label | f9fbaa03-01c9-53f3-a4b1-59ab7d558a0a |  | note | • Specifications & QA Documents Approved
label | 65eba237-7609-57c8-a065-9b823317c0b1 |  | note | • Drawings are confirmed
label | 96b594b7-9fea-5ed7-b6e6-05806dcc0c51 |  | note | • Equipment fit for purpose
checkpoint-group |  |  | section | CONNECT PRESSURE PUMP TO DCW RING MAINS
checkpoint-status |  |  | checkpoint | Accept delivery of pump to site
label | a0764a28-5db5-5877-944f-89bd1ac9453e |  | note | CRITERIA - 1. Check pump is rated for pressure test
label | 09303136-d91e-5acd-808c-787f6a6fbeb8 |  | note | 2. Check all supplied attachments are correct and in good order
label | e9a00b57-87dd-5603-b9a7-08a12cfb1745 |  | note | 3. Check fluid levels & fill as necessary
checkpoint-status |  |  | checkpoint | Connect pump to Fire ring mains
label | 965fc0fe-1856-523c-ab9c-e9ccc273196b |  | note | CRITERIA - Confirm connections are safe and correct
checkpoint-status |  |  | checkpoint | Connect calibrated gauges for pressure test
label | f40babb5-fe8a-5288-b1a7-811481130b99 |  | note | CRITERIA - Confirm position is correct, gauge is in good order for test & calibrated
checkpoint-group |  |  | section | HYDROSTATIC TEST
checkpoint-status |  |  | checkpoint | Fill Fire ring mains with domestic water
label | c780e7e8-627b-58b3-8fb4-f15e01e3aef8 |  | note | CRITERIA - Completely fill closed loop system with water releasing all air from the Valves at each Building
checkpoint-status |  |  | checkpoint | Gradually increase system pressure to 15.5 Bar
label | 90eacdea-6b58-5bba-a99d-be91352a377f |  | note | CRITERIA - Slowly raise system pressure to 15.5 Bar
label | 1abd5484-6f42-59c8-a890-aa69e24ea847 |  | note | • Checking for any signs of leaks or pressure drops
checkpoint-status |  |  | checkpoint | Stabilize 15.5 Bar pressure (START WITNESSED) - CPB/IR Hold Point
label | 4de5437a-f431-587a-a4f7-3947fefca462 |  | note | CRITERIA - Record START time & photograph gauge
label | a92cfe97-8ea0-5078-adb7-6a268738680d |  | note | • All relevant parties to witness starting pressure of 15.5 Bar
checkpoint-status |  |  | checkpoint | Hold 15.5 Bar pressure for 4Hours (END WITNESSED) - CPB/IR Hold Point
label | 87a4844d-a442-5736-8023-935b359722e5 |  | note | CRITERIA - Record FINISH time & photograph gauge
label | 36d4b22f-8e92-5bba-a6f8-626009369f14 |  | note | • All relevant parties to witness pressure of 15.5 Bar
checkpoint-status |  |  | checkpoint | Pressure released or reduced for next test
label | 950b7423-d9a6-5a48-a67e-a7658c2939a1 |  | note | CRITERIA - Supervisor to ensure energy (pressure) is only stored while under test
checkpoint-status |  |  | checkpoint | Discharge pressure leave system in a safe state
label | 1db726e8-c9b3-5d14-8201-5925268e0495 |  | note | CRITERIA - Discharge system pressure, ensure area is left in a safe state meeting site requirement
checkpoint-group |  |  | section | COMPLETION RECORDS
checkpoint-status |  |  | checkpoint | Testing Results - CPB/IR Hold Point
label | f9970583-a837-5b5d-aa74-ea7fe7bdedee |  | note | CRITERIA - All pipework pressure test reports shall be provided
checklist-flat | fc4c08b1-af97-4fae-926a-57bb2455500d |  | checklist | RBG Combined Services HDPE Potable Water Pipework Installation V2 |  |  |  |  | Yes | RBG Combined Services HDPE Potable Water Pipework Installation V2 | 0568c749-af0f-4547-9684-73ab891bf437
checkpoint-status | 10d55dd1-243f-4f24-9d26-effabcac4faa |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | baedbd5b-1415-4016-bb93-9dcb5cb7f21b |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | 9b6966b3-ce32-45b2-b43a-01bc0da9371e |  | checkpoint | Inspect trench depth, width and pipe alignment
label | 72d345b4-c6e6-598b-a90a-98710f130f7c |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | da128105-03fd-5ceb-ba4b-abc3a36571f7 |  | note | QA documents to be provided prior to installing pipework in trenches . CPB to provide to AE Smith.
checkpoint-status | 51ee531c-7656-41b6-8e28-63f3247f0b9c |  | checkpoint | Number of pipes and dimensions of pipes shall be shown on the drawing
checkpoint-status | e3dcc19a-50d1-470d-8191-2185ad92fbc1 |  | checkpoint | Location of pipe
label | edd8a7b6-1931-5594-b340-a720bf7ab179 |  | note | Shall be as shown on the drawings
label | 46150486-e848-5f26-958a-eb85e5b277b4 |  | note | Ensure correct clearances between water service and other underground services.
checkpoint-status | 0b94a859-2989-4a83-afaa-0a26813012a8 |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
holdpoint | 205ba956-b95e-494a-a279-2ae0aa302ebe |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 84701b10-3cfc-4f42-9f8c-b8aa14cc00f5 |  | checkpoint | Jointing of pipes only via. Rotatable steel flanges, EF Coupling and Butt Welding.
checkpoint-status | 811b93a0-4752-4dd6-8121-b2fedf593963 |  | checkpoint | Electrofusion Welding Checklist completed for each joint?
checkpoint-status | 6d78e9de-0f58-4987-be78-98f62a8ce947 |  | checkpoint | Butt welding checklist completed for each joint ?
checkpoint-status | eaad8f09-17f7-4681-ae77-3ddd3a636f72 |  | checkpoint | Install valves, tees and bends
label | 5ff09d41-48a3-50e6-bc92-43c9450cf876 |  | note | Install all connections as per construction drawings
label | 17853516-b1c9-5fe4-8b6c-777b7cdd3676 |  | note | All valve 100mm and above will require a 1050mm manhole.
checkpoint-status | bbdb1a7a-a5d3-4b8e-8fde-84d494efdd53 |  | checkpoint | Installation of ductile iron bends
label | 367d1efb-e21c-5d7b-9a09-5a0836da7cad |  | note | Inspect pressure class on fittings and ensure correct pressure rating prior to installation.
label | caeab218-c37e-5ed4-8858-9af405c68cb0 |  | note | Ensure correct gaskets are installed.
label | 290bcb62-208b-51d3-b175-cbfb92e5c1ec |  | note | Washers installed on both sides of the flange.
label | 47f627c9-5fd7-5d16-935c-636f875d3cc5 |  | note | Bolts to be tightened in correct tightening sequence.
checkpoint-status | 2c745297-939e-4543-be67-fd12494a1b79 |  | checkpoint | Install Thrust and Anchor Blocks
label | bc99addc-af6e-52c4-9c72-c67970241d6a |  | note | Minimum dimensions as per IFC drawings.
label | 4a49130b-6af9-5945-931e-e34db297e473 |  | note | A protective Denso or black coating membrane is to be installed around the pipe and the concrete anchor/thrust blocks to prevent abrasive damage.
holdpoint | 7c07ef8a-b437-4ce3-96d3-261ec29618cf |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | b7fa29bb-fde0-41cc-a331-f3c351040d44 |  | checkpoint | Completed Construction Pressure Testing with Air
checkpoint-status | c386e340-f90b-45ce-aa9a-509f7e5e2e36 |  | checkpoint | Pre-Pipework Pressure Testing Inspection
label | 8d4cd252-08dc-513b-a8dd-e497bc2cc6cf |  | note | Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | 05b76734-436a-5c52-a541-b99a206fa01f |  | note | Ensure each test length is capped and ball valve installed.
label | 58ec742c-626d-51c4-9622-15ae74f5b9a9 |  | note | Ensure all valves in the system are in the correct position and tagged �DO NOT OPEN� or �DO NOT CLOSE�
label | 7ad70c76-4c7f-5481-8e46-a85c104b4eb9 |  | note | All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing.
checkpoint-status | ffd447f0-5263-4a02-9eee-3be9d9061ecd |  | checkpoint | Introduction of Air to 300 kPa
label | d10d34f4-e78d-5dd6-ae09-c507d3d284dc |  | note | Gradually introduce air into the system to a pressure of 300 kPa and hold for 1 hour.
label | 6f6e953e-8b6c-500b-ade2-0ba077e56ea2 |  | note | Monitor for any drop-in pressure.
label | a1799260-2f92-528c-8993-51666703ad82 |  | note | If a leak is identified discharge the air prior to rectifying any leaks.
checkpoint-status | aeada704-d0ad-4aa7-a49d-d734ffd54959 |  | checkpoint | Increasing Test Pressure
label | 4752b001-8afc-59a2-bb57-4b784b63e52a |  | note | If no leaks are identified Increase pressure by 10% increments until test pressure is achieved.
checkpoint-status | 7d7517a8-15c8-48b4-af1f-5aac0a4a7190 |  | checkpoint | Pipework Pressure Test Report Completed
checkpoint-status | e1a6513d-df0c-4a82-a991-976fea325067 |  | checkpoint | Installation of Trace Wire
label | 2b159c13-4377-5d31-80d6-deb67556cb34 |  | note | Install Trace Wire and ensure tracer wire is continuous between valves and any excess coiled in valve box.
label | 95113112-30d8-5941-acf6-fecde999b91e |  | note | Test Trace Wire following installation.
holdpoint | 8d664468-28ef-4e66-babb-fa7c5872ff9d |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | c3db849d-9204-42d8-8e63-336ed369aa84 |  | checkpoint | As-Builts Completed.
holdpoint | 006d0d48-4c68-4bf5-ba79-d5ba556fda1c |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 84f1edd6-92d1-4095-b761-3c20f7184d5e |  | checklist | Combined Services HDPE Natural Gas Installation |  |  |  |  | Yes | Combined Services HDPE Natural Gas Installation | 0945f706-e66f-4b50-8d17-9a9730a1c2a3
checkpoint-status | 0a3175aa-fe41-4b3d-90b1-f8f0094544c9 |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | a8cc2176-8380-4925-bd8a-218cd6b96d04 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | c2633378-7b57-4d29-842e-850f3303719b |  | checkpoint | Confirm trench depth, width and pipe alignment.
label | 1362d58b-790a-5bf7-ae6c-46c24049fcec |  | note | QA documents to be received from sub-contractor prior to installation of conduit in trench.
checkpoint-status | e6094e81-94ca-4d9d-950c-39e28deaa4bc |  | checkpoint | Number of pipe dimensions shown on the drawings.
checkpoint-status | 8494e1a3-1f51-4714-ba4f-d8880c45c0f3 |  | checkpoint | Location of pipes shall be shown on the drawings.
checkpoint-status | d060a17a-9506-475f-9663-83bcb0f89d02 |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | b842a126-9259-4258-b424-da306dfbbf3d |  | checkpoint | Installation of Valves
label | e6b327b2-1ab3-50da-8e5a-1f74e07840a1 |  | note | Valves Installed as per approved drawings
label | ac7906b2-b8cc-5c24-b10d-c7629c2465ea |  | note | All works have been completed by a registered gas fitter ?
checkpoint-status | 7a8d2d0b-1a5b-40ae-be98-4c3fbfa7742d |  | checkpoint | Pipework Pressure Test Report Completed ?
checkpoint-status | 3b47c0f9-7509-41f8-aad2-7c04494e4d10 |  | checkpoint | As-Builts Completed.
holdpoint | 770763b2-60b2-4a52-bd9c-629cb339c4fb |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 2071fdce-71e6-48f5-a16e-3e869c90e011 |  | checklist | Electrical and Communications Conduit Installation |  |  |  |  | Yes | Electrical and Communications Conduit Installation | 0ac1c466-5cab-4995-b8c8-2e310a39fd64
checkpoint-status | 89ca0071-978f-46b2-a4e2-2e7e94dc2d8c |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 2bd8548e-95dd-488d-93b9-ad086383f072 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | b40091b8-fcd4-44c9-a134-579c66a61246 |  | checkpoint | Confirm trench depth, width and pipe alignment, QA documents to be received from sub-contractor prior to installation of conduit in trench.
checkpoint-status | b7700a38-cba9-450c-9482-923f55821e7a |  | checkpoint | Number of conduit dimensions shall be shown on drawings.
checkpoint-status | bd2227c6-325f-427c-a471-1bfb352116d2 |  | checkpoint | Location of conduits shall be shown on the drawings.
checkpoint-status | a9e6b61f-846b-4aa4-a4fe-f8efb63ed756 |  | checkpoint | After Installation all conduits shall be free from foreign matter and from rough edges which could damage the cable during Installation.
checkpoint-status | 7a0ee8dc-b02f-4d17-aa02-3eb795f97afb |  | checkpoint | Where practicable conduits shall enter and exit the pit at the same height and orientation.
checkpoint-status | 301b1e76-1927-4a3c-a012-7277bee08cec |  | checkpoint | A draw rope shall be installed in each conduit run and shall extend a minimum of 500mm above the top of pit collar.
checkpoint-status | 80bb38ef-e6fc-440e-830d-ffa071494bb6 |  | checkpoint | Rope ends shall be firmly secured to prevent the ends being lost in a conduit.
checkpoint-status | 3e601c5a-5007-4205-8db0-449f1d223a2b |  | checkpoint | As-built drawings completed.
holdpoint | 1d6b6049-ac4b-4177-bc81-571764e33f00 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat |  |  | checklist | B7A - Functional Tests of Terminal Units |  |  |  |  | Yes | B7A - Functional Tests of Terminal Units | 124bc065-0357-4219-bd9c-0dc38bb28b3b
checkpoint-status |  |  | checkpoint | B7A - Functional Tests of Terminal Units complete
text | 08c4630b-6ee9-5ca7-a800-f20660515166 |  | textbox | Plant ref
text | 67e2ca71-8b68-5043-80c7-08016619a816 |  | textbox | Test by
text | cccdd03f-afb6-5be2-afb4-5ce0cef677e0 |  | textbox | Test date
text | dd044b6c-ce6d-59dd-b260-18b5a0220a99 |  | textbox | Revision
text | e0dc2e7f-4c84-5fd7-9c64-340eae93c9d6 |  | textbox | System
text | 45110706-1468-538b-8c0b-f879e998d9fe |  | textbox | Specified flow (L/min)
text | a03ce393-b20a-569a-a4f4-01491873a9d2 |  | textbox | Specified pressure drop (kPa)
checkpoint-status |  |  | checkpoint | In accordance with the contract specification and paragraphs 15.77–15.78
text | f7373a57-c60e-576e-9fa4-23d65eb4a2c2 |  | textbox | Terminal unit number
text | 0fb25664-ff6b-57a4-86c5-38eb1ba6f43a |  | textbox | Room number
checkpoint-status |  |  | checkpoint | Specified flow achieved
boolean | f77cc819-e7b3-5049-a1e5-c36c4cf4e5a4 |  | tickbox | Yes
boolean | 4463c6e7-e395-5db3-9da9-40becfd7850d |  | tickbox | No
checkpoint-status |  |  | checkpoint | Specified pressure drop achieved
boolean | ff1b2465-4669-5735-ae72-617d4655036f |  | tickbox | Yes
boolean | 3b57671d-641e-52e8-a828-9f0219e1374e |  | tickbox | No
text | 5315a658-4207-55d0-b659-cc33cd6b4e38 |  | textbox | Mechanical function
text | bd1ee49a-d3f7-5e42-b518-2cf84e913649 |  | textbox | Gas specificity
checklist-flat | 910b4d2f-20e6-4202-b30f-e5a98f1673b7 |  | checklist | Butt Welding |  |  |  |  | Yes | Butt Welding | 1af85a7b-4718-4fbb-9bfd-d718da1b261e
checkpoint-status | c8dee859-39ca-4784-9e6e-7d9941180258 |  | checkpoint | Weld Details Completed
text | ed0b2069-38ae-51a6-b0c2-c74383a77503 |  | textbox | Weld Number
select | 654e0c4e-ae75-5efb-9283-fce9597f1eee |  | dropdown | Weld Completed By: | Benjamin Habon, EB Lindayao, Jefferson Calla, Redennis Teves, Steve Reeves, William Sabino, Calvin Cheyne, Mark Bateman, John Chingkaw
select | d7bd3611-6574-5e7b-985b-31213b80e0b3 |  | dropdown | Welding Machine # | Machine 1, Machine 2, Machine 3
text | 1ef3ca77-bad6-5887-9679-d203af4d134f |  | textbox | Certificate #
checkpoint-status | 9348f672-5bb8-48af-8f81-f1ebc2d0197e |  | checkpoint | Pre-weld checks - Visual Inspection of Pipe
label | c297085c-730f-5bd0-a703-add028ac308b |  | note | Ensure branding markings correct
text | 72f28d58-c2ea-537b-88a4-d9afc569fad0 |  | textbox | Record pipe batch number as labelled on the pipe.
text | 72602a86-7457-55e5-9585-0023a698231b |  | textbox | Record pipe wall thickness and inspect.
label | aa5c60b5-1bda-547e-b1ba-b0ddb3e8d4df |  | note | External surfaces are free from scratches deeper than 10% of wall thickness.
label | 307a431e-3d7e-5560-bb54-19623f62c94f |  | note | Inspect internal surface of pipe for scratches.
label | 741c3ce7-5ff4-5c6d-a4a4-44176bfa9235 |  | note | Inspect pipe for cracks.
label | 31efab25-044f-586a-afc0-b20d72a11a63 |  | note | Inspect internal ridges or ripples exceeding 0.5mm in height.
label | 69994fdc-2df3-5a06-889c-37bd5e3df477 |  | note | Clean and wipe pipe with Isopropanol.
label | 78fbbf96-1404-5ecd-bb1b-106fd6853b90 |  | note | Inspect pipe ends are dry from any water content.
checkpoint-status | 73772ba4-d361-4e96-8692-3d8c064313f8 |  | checkpoint | Pre-Weld Checks - Weld Machine Checks
checkpoint-status | 305a8ae4-dd9b-47d5-a05a-c98a7c967f08 |  | checkpoint | Heater plate temperature checks taken and recorded
label | 1392f678-f011-5811-8d91-60940c6de348 |  | note | Ensure pipe ends are capped, welding area isolated to regulate cooling and prevent airborne contaminants.
checkpoint-status | 1ea12469-42df-4f80-8fdc-0a2f3f53ec8c |  | checkpoint | Post Weld - Visual Checks
label | 76f5e0b6-ffdb-5394-8452-e2113022e127 |  | note | Alignment of pipes is less than 10% of pipe wall thickness?
label | d23a7c58-7cf9-5b49-93d3-f2f4774a6d5d |  | note | Fusion beads symmetrical on both sides of weld
label | 8a940c97-118c-5404-a362-346945f8027d |  | note | Ensure Beads are fully rolled over
label | e44185ee-cac1-5d5e-881e-703a3e83133c |  | note | Inspect for cracks in beads and welds are free of pitting and bubbling.
label | f6237a4a-5669-50c3-8fc2-c13123f6f9ee |  | note | Inspect for inclusions or other obvious faults present.
label | ab1817be-06cf-55e1-9e24-276ba3926f96 |  | note | Internal weld beads removed from pipe?
checkpoint-status | 0c3354d5-b811-4786-a402-b6cc6a3c35f5 |  | checkpoint | Weld Records and Inspections
label | bd6b904f-1749-5199-a285-561c0b2364f8 |  | note | Data logger records printed, checked and attached?
label | a35d4317-dd9a-5182-809b-b0cc5628a06c |  | note | Weld completed, inspected by AE Smith Supervisor and CPB ?
holdpoint | adfc0216-485c-4223-9d0d-7e70004f848a |  | signoff | Post weld checks by CPB and AE Smith - Request Signoff/ Raise Remedial
checklist-flat | b88a90a9-8ec6-4bd0-83c3-fd66b1c09e1e |  | checklist | LV Installation |  |  |  |  | Yes | LV Installation | 1f616609-c97b-4805-9d58-b0c438af1678
checkpoint-status | f6f8947b-16e3-42f5-b382-14f40af2a14c |  | checkpoint | ROM & consent approval received by the client and approved?
checkpoint-status | 01ba2610-6a11-4cc6-a387-b38b547c4293 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
label | 20b157e9-b034-5ac5-9178-f48ec267f675 |  | note | Attach: material inspection checklist
checkpoint-status | 05176e80-99a4-4af5-b990-7a10b1a87b26 |  | checkpoint | Inspect trench depth, width & cable rout
label | 6541afb4-6977-516a-84fe-01d3731ad744 |  | note | Shall be as shown on the drawings,
label | ea6a8db4-e541-5866-aa8b-4e4c739964a1 |  | note | Attach: Excavation Checklist & Photos
holdpoint | eccd7719-6e0f-4d47-ab5b-a0d3d744b3f8 |  | signoff | CPB HP - Documents
checkpoint-status | 39dc7763-49fc-49ab-82ab-ce0aad17d71e |  | checkpoint | Drum Delivery Test Certificate
label | 90dbdc7d-0a0d-562c-927a-6379f7cae1f6 |  | note | Attach documentation
checkpoint-status | c7ec6c07-df6a-4f84-90cd-e58ef52d5978 |  | checkpoint | Pre-haul Checks
label | 2b1feea8-6aa7-500f-8145-14c400401fb4 |  | note | Verify Cable is in good order and condition prior to haulage
checkpoint-status | 1278206a-c6d8-4a27-a1f2-37a1cbcec1d5 |  | checkpoint | Confirm correct lubricant available for use, where applicable
label | ab1952ea-66e5-5f57-a12a-3a9797764f36 |  | note | Verify correct type, and that sufficient quantities are available
checkpoint-status | b8c26706-a470-49bb-ac5b-923e9084a10f |  | checkpoint | Observe the Haul
label | 4a9e158f-1159-5f38-b3d5-42508a837221 |  | note | Stop the haul if a potential risk of damage is identified
checkpoint-status | 74fd391a-362b-47d6-8692-f3991b4e738b |  | checkpoint | Inspect cable sheath during the haul
label | be7810fc-da3e-501a-b9c6-1b4f14ab99a7 |  | note | Stop the haul if any damage is identified
checkpoint-status | 5ae5906a-12da-441a-b865-fdd0fa1a4280 |  | checkpoint | Inspect cable sheath at the completion of the haul
label | 6bdb4bce-12f2-5a04-9b45-4a02d9897f89 |  | note | identity an signs of damage
checkpoint-status | 38149d36-9dad-4880-b775-dd5bd7f9f7f7 |  | checkpoint | Install Seismic Loop
label | 3ce3d06c-192b-5896-8be2-5f8c08470a27 |  | note | Visual Inspections
checkpoint-status | 2661cab7-a202-4a9f-9833-3cf886c4fb9b |  | checkpoint | Install cables into building and contain to prevent damage
label | c37cbda9-6226-5395-9079-b0f7a5cba406 |  | note | Visual Inspections
checkpoint-status | d1cae302-f0f6-4760-a3e5-083dd37ccdf7 |  | checkpoint | Install lime & compact
label | 894a01bf-fb1f-5ffb-8aaa-1794b623e518 |  | note | Visual Inspections
label | 2b8489db-ac3e-5b1a-babe-b4c979046391 |  | note | Check bedding depth
checkpoint-status | 84502995-5f0d-48e8-beaf-4a90bfa69b07 |  | checkpoint | Install Mag slab
label | 83721026-e99f-5e82-980f-7d62bc3e06d7 |  | note | Visual Inspections
label | ff91f54b-3071-56f3-b020-08f322a9b16c |  | note | Make sure Mag slab is covering the buried cabes
checkpoint-status | 3c52f741-f68b-47e2-86b4-f8d49adcd6b3 |  | checkpoint | Test cables installed
label | f6ac7679-c0a4-5ea4-89c4-eea3d434c355 |  | note | Insulation Resistance Test
label | a6d45549-037e-5b13-b029-d13d92311665 |  | note | Continuity Test
checkpoint-status | a4b0a609-1299-46cc-88bd-bc7b029b64f4 |  | checkpoint | ITP Sign off Witness Points
label | 29cdc45a-af28-5375-a178-cfa3dec4505c |  | note | 2.1 Inspect trench, depth, width & cable route
label | 3bbb9dd7-9eec-50f8-8a36-6645dc30f998 |  | note | 2.2 Testing of cable prior to cable pulling/laying
label | 728f1e3b-95b7-5c1a-9717-a1544b49ad83 |  | note | 3.1 Pre-haul checks
label | 15c4337c-a488-52aa-b5bf-a73a060037ca |  | note | 3.2 Confirm correct lubricant is available for use where applicable
label | 5ca599cc-816f-52a4-a302-2d1229e4b777 |  | note | 3.3 Observe haul
label | 712cb674-76b5-50a1-a57b-2b0aaed7b7fc |  | note | 3.4 Inspect cable sheath during the haul
label | 9327cbd3-c1a0-5e99-a762-01134c1d0d75 |  | note | 3.5 Inspect cable sheath at the completion haul
label | 2287ee07-3f86-5d92-a79e-dc381784dd82 |  | note | 3.6Install Seismic Loop
label | b7a11b53-a188-542d-892c-f9577407548f |  | note | 3.7 Install cables into Building and contain to prevent damage
label | 7f94abb9-094e-55f4-bb04-9fb4926bda29 |  | note | 3.8 Install lime & compact
label | 76f7ac0a-ad0a-54d4-b510-a8d53469f91d |  | note | 3.9 Install Mag slab
label | d7b94529-0a8b-5f0e-adb9-61317507fd36 |  | note | 3.10 Test cables installed
holdpoint | 3e9cf2b7-7bf0-4bbd-b4bb-9ab9b75a6587 |  | signoff | CPB & AES signoff / raise remedial
checkpoint-status | 90606b12-d76c-4017-892b-3f7ae964268f |  | checkpoint | Inspection by Supervisor
label | ef27fa2d-b4ea-5367-aed9-dfd66dfe8bf2 |  | note | QA check sheets, visual inspection and test requirements to AS/NZS 3000:2007 measurements verified
holdpoint | 74029f19-7cb6-4128-9f52-358edd020d90 |  | signoff | CPB & AES signoff / raise remedial
checkpoint-status | d7365079-3b6f-4c32-8f4b-6777dbe34376 |  | checkpoint | Notice of completion
label | ebfec110-9fff-5a00-80e2-b681ced02f7c |  | note | Had back trench to CPB at Mag slab demarcation point.
holdpoint | 17f076d0-9135-4c57-a4cf-ce3cee3e35b1 |  | signoff | CPB & AES signoff / raise remedial
checklist-flat | ec1354de-7626-474b-a8b4-fc7cbed034c0 |  | checklist | Combined Services HDPE Natural Gas Installation Part 2 of V3 |  |  |  |  | Yes | Combined Services HDPE Natural Gas Installation Part 2 of V3 | 2d1dc380-47a6-4f94-9b4a-f3be38081c7f
checkpoint-status | 2eabd90c-616f-4fa4-a244-03681f75bba5 |  | checkpoint | Confirm trench depth, width and pipe alignment.
label | 731c5841-9b8d-5389-ac3f-4fdb57c311d1 |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | f34c87b3-0d5a-507b-9f85-ff3614ed1abc |  | note | Excavation Checklist to be completed prior to installing services.
checkpoint-status | 5d6048c1-3f68-4a1b-b7cb-c22c5ff395cd |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
holdpoint | bbdafedc-5f86-4625-9ada-b5f44c70a9c6 |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 6c7b726e-11b3-4735-836a-7b59b777bb87 |  | checkpoint | As-constructed survey
label | e5a27f82-a093-56bb-af59-74e85a6a61d7 |  | note | As-constructed survey must capture the horizontal and vertical locations of all newly constructed or relocated underground trenches and pipework.
checklist-flat |  |  | checklist | Back-Flush |  |  |  |  | Yes | Flushing - Back-Flush | 334b15c6-7b49-453c-a5df-1af2377ee9a4
checkpoint-status |  |  | checkpoint | Chemical cleaning is completed and clear water is visible at the main drain valve.
checkpoint-status |  |  | checkpoint | Terminals backward and forward flushed and water drained at the terminals until clear water is visible.
text | f7c77e5a-9d25-5472-bd8b-5567f6e7bed5 |  | textbox | List the terminals backward & forward flushed.
checkpoint-status |  |  | checkpoint | Water sample is taken from the furthest terminal, and labeled as "Back-flushed terminal" and dates.
text | cf18e5fc-59b4-562d-bacb-a59df9ad39aa |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Sulphate
text | a7801e30-a7c7-563d-8edb-c18e23fa5c3a |  | textbox | Site measurement
text | b9f6bbd2-a112-5545-b5ad-a1410f182880 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Chloride
text | 97d85d45-decf-5d92-9477-37321bd0931d |  | textbox | Site measurement
text | 09c3df4b-115a-5fd3-92c2-c2530285f6ff |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | pH
text | 8e19a47e-3135-55d7-9861-67decc201e53 |  | textbox | Site measurement
text | 22a8937b-5118-5583-b690-3c62d66505bc |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Conductivity
text | 6768b150-a787-5503-a7a0-28ff7b4ee142 |  | textbox | Site measurement
text | d886c0d4-f102-59f4-ac59-93f9facc07aa |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | 04249184-1ace-51ec-9707-34a396b5a6dc |  | textbox | Site measurement
text | ca1db508-3bb3-57ed-b19f-4c92a23e4d1c |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TVC (Total viable count: the total numbers of microorganisms, such as bacteria, yeast or mould species)
text | 43364d67-e71b-55cf-bc7c-06337d965c80 |  | textbox | Site measurement
text | dcd89c77-1616-5eaf-a50c-fd3404dbc959 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Pseudomonads (microorganism that can create biofilm)
text | f842f9c9-f160-54fe-9aca-88845c75d64a |  | textbox | Site measurement
text | fcab0ba0-ddab-51a9-adcf-c5b8ddba7e16 |  | textbox | Lab test results
checklist-flat | 6652d6e4-22a6-44dd-89b7-d9fad6a9cbf7 |  | checklist | Electrical and Communications Conduit Trench Riser Installation checklist |  |  |  |  | Yes | Electrical and Communications Conduit Trench Riser Installation checklist | 361f1b9f-66ee-4838-867f-e932b5a66fb7
checkpoint-status | bb6a80f2-e56b-42fe-91b4-c3c48af7640f |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | d344d940-9c45-4416-8d0d-709cd2e09d24 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | b1c2655c-59f2-4b9d-aa70-f02d8956f8df |  | checkpoint | Confirm trench depth, width and pipe alignment, QA documents to be received from sub-contractor prior to installation of conduit in trench.
checkpoint-status | af235ead-2c4f-498a-9467-7806fd4c8469 |  | checkpoint | Number of conduit dimensions shall be shown on drawings.
checkpoint-status | 3b54bd5e-1b9d-40cc-8133-7a9cdae089d9 |  | checkpoint | Location of conduits shall be shown on the drawings.
checkpoint-status | bf2ffa7e-f109-47b4-bf39-a9e6a4102ccf |  | checkpoint | After Installation all conduits shall be free from foreign matter and from rough edges which could damage the cable during Installation.
checkpoint-status | dbdcf3a6-e1a8-48b3-80f7-022be8bc2258 |  | checkpoint | Where practicable conduits shall enter and exit the pit at the same height and orientation.
checkpoint-status | e2b8b3af-7c7d-439c-81cc-ffa9d765f60c |  | checkpoint | A draw rope shall be installed in each conduit run and shall extend a minimum of 500mm above the top of pit collar.
checkpoint-status | 18acff54-f214-40d7-8f3f-6605891d1785 |  | checkpoint | Rope ends shall be firmly secured to prevent the ends being lost in a conduit.
checkpoint-status | 8c57b926-1fe7-4512-9631-1b5495a5183a |  | checkpoint | As-built drawings completed.
holdpoint | 3522a344-b88d-4993-9a37-38f6669926a3 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 89983eeb-40b8-4d9a-846b-86db75106d69 |  | checklist | Document: |  |  |  |  | Yes | Project Documentation | 39a14167-4ddb-4a2f-9155-27e491efa078
checkpoint-no-status | 78d25478-5723-4f8e-b4d8-3b7b8d9a0cd0 |  | checkpoint | Document Attached
checklist-flat |  |  | checklist | Dynamic Flushing Checklist |  |  |  |  | Yes | Flushing - Dynamic Flushing Checklist | 40344506-d308-40da-81d2-b9aa8db91eb3
checkpoint-status |  |  | checkpoint | Uploaded highlighted drawing.
text | d92e4ec0-9a51-597c-84a4-c5ad2ddd1b34 |  | textbox | List the zones / terminals / branches flushed during this step.
checkpoint-status |  |  | checkpoint | Confirm all other terminals isolated
checkpoint-status |  |  | checkpoint | Turn the pump on and run it at 20 Hz (or at minimum speed)
checkpoint-status |  |  | checkpoint | Increase the pump speed to 50 Hz and measure the total waterflow
text | 48ca6c6d-fe2f-5d0e-84fa-fcd5817050e6 |  | textbox | Record total and terminal waterflows on the "Flushing Water Flows" test sheet and upload here.
checkpoint-status |  |  | checkpoint | Circulate water for 2-4 hours by sampling the drain water quality. Record the duration.
label | 881aee60-091d-5133-9532-c909b3cb5bf0 |  | note | The duration of this process depends on the size of the system and may required to be extended.
text | 6748fe0c-d52b-5d25-a558-556a4d8621a3 |  | textbox | Duration
checkpoint-status |  |  | checkpoint | Clean strainers as required. Upload dirt and clean strainer photos here.
checkpoint-status |  |  | checkpoint | Photo of water sample at the end of the dynamic flushing
checklist-flat | 2baeceb8-38d8-4273-93a3-5e95292911a0 |  | checklist | Pressure Test Report QCC-01.01 |  |  |  |  | Yes | Pressure Test Report QCC-01.01 | 47e74aba-1a0a-48ca-bcd5-30013cba44bf
checkpoint-status | ea703a41-ec2f-42c2-b741-d07e7c401b23 |  | checkpoint | Details of pressure test
text | 125a1f58-fb93-4fca-b207-81062af299ba |  | textbox | System Name/No.
text | 42b4109d-b3ba-450d-a96a-9217ffe123f7 |  | textbox | Location / Drawing No.
text | ddddbb20-aebf-4150-af44-058724908df6 |  | textbox | Test Instrument & Serial Number.
text | 1ffb4b68-825a-4ff9-a9c6-87fa9700d497 |  | textbox | Normal Working Pressure
text | 22d523d8-c31a-4752-ba5d-2a1ebce470fe |  | textbox | Start test ambient temperature
text | c20847d5-6182-4dec-9899-d1888d45e3d4 |  | textbox | Start test date
text | 31e3a80b-edab-4454-bb5f-ac357745cc76 |  | textbox | Start test time
text | 917ef879-4510-4dcc-a2c1-691a80ea5c5f |  | textbox | Start test pressure
text | dd5b4735-e182-4d04-841c-f425c1267348 |  | textbox | Finish test ambient temperature
text | 2c810d16-e75f-4644-99cc-359aa4d8a695 |  | textbox | Finish test date
text | b675deb2-9fad-453e-be71-589c96095ef0 |  | textbox | Finish test time
text | 4e71ffa8-f76f-4832-8216-a4f15f2ff734 |  | textbox | Finish test pressure
text | cbeee8b8-03d5-46b6-a5ea-8522baa6875f |  | textbox | Corrected pressure at test completion
label | 7990a0c7-14a7-4f43-b773-fb56a6ae93c1 |  | note | Attach photos of the gauges as required
label | 6059a464-043f-4bd0-8b04-c2f8cbad5042 |  | note | FORMULA :
label | 71330246-4fe0-4294-921b-beb085d495cb |  | note | Pc = P x (Ts + 273) / (T + 273) kpa
label | 1a04a208-c0e5-4d52-ad08-4300aed9e545 |  | note | Pc = P x ( +273 ) / ( + 273) kPa
label | 9f8ea800-f4bb-49af-a8b5-389758071961 |  | note | Pc = kPa
label | 57105522-72b0-4769-8f26-25359e8f238e |  | note | WHERE:-
label | 26a80af3-2173-40a6-9868-00ed118f3db0 |  | note | P = PRESSURE REQUIRING CORRECTION i.e. PRESSURE ACTUALLY READ AT TEST END
label | ed49c168-0d5b-4b0f-a64e-e31771f502a8 |  | note | Pc = CORRECTED PRESSURE
label | 241239a4-61f2-4368-98de-7a04516ebd82 |  | note | Ts = AMBIENT TEMPERATURE oC AT START OF TEST
label | 8e6e5ef8-edf4-47ec-9cd1-094d5e762d8d |  | note | T = AMBIENT TEMPERATURE oC AT SAME TIME OF READING P.
checklist-flat | dc5debdb-78dd-41df-9d0d-7175d51df667 |  | checklist | Trench Pipe Riser Installation Checklist |  |  |  |  | Yes | Trench Pipe Riser Installation Checklist | 49ab133b-deac-4693-89d0-576f5af3330c
checkpoint-status | 202c1457-00e8-45cc-a9b0-96400a8f8c13 |  | checkpoint | RDM & Consent Approval received by the client and approved?
checkpoint-status | 7daeeea3-35bf-4161-8815-2566626375ba |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | a5e9b983-bfa3-4fc2-adb2-24dbab8c0672 |  | checkpoint | Confirm trench depth, width and pipe alignment.
checkpoint-status | 2e7a780f-196b-4d1b-a6e0-a1c448c36e7c |  | checkpoint | All pipe flanges are capped, and ball valve installed on pipe ends exiting the trench.
checkpoint-status | 775b3bbe-579b-4041-aa6e-77949cffe878 |  | checkpoint | Each pipe shall be pressure tested prior to installation , Refer to separate pressure test report QCC-01.01
checkpoint-status | 3af545b2-1344-450d-a87c-ce6dd3dfc5f3 |  | checkpoint | 100Kpa of air to remain in pipework to verify no leakage, Refer to separate pressure test report QCC-01.01
checkpoint-status | 8d53cfa0-a2bd-41e4-98cb-e5090f5126fe |  | checkpoint | Number of pipework dimensions shall be shown on drawings.
checkpoint-status | 0f01edef-aad1-4f6a-ba4b-c885a1a8fb93 |  | checkpoint | Location of pipework shall be shown on the drawings.
checkpoint-status | 151b52dd-ba2d-4afb-a04a-cc4aac9b792d |  | checkpoint | Pipework exiting the trench shall conform to the location and dimensions shown on construction drawings and specification.
checkpoint-status | 79d455d7-8c87-49f3-a4b6-389e05da6bf9 |  | checkpoint | Before backfilling inspect all installed pipework and insulation for damage
checkpoint-status | 22c2ead9-6a8c-4fe6-98ef-c247518d52cd |  | checkpoint | Pipework pressure to be verified of no pressure drop prior to connecting to mains pipework
checkpoint-status | d2b04c28-bef1-4754-a1e2-e973211527db |  | checkpoint | As-Builts Completed.
holdpoint | 73c83ccf-d94e-4b6a-aa1e-0e83384c3ca8 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 68c8296b-1494-4c30-991b-785b37ce0b40 |  | checklist | Project Details |  |  |  |  | Yes | Project Details | 51f170ee-0a3a-41ea-bf26-683743dc17d2
checkpoint-status | 08b8e56a-f13a-4198-99cc-0515de89b333 |  | checkpoint | Project Information
text | b6deda1f-d359-47ad-8507-719dc8afe130 |  | textbox | Project Name:
text | 2c5f2213-0e59-43bb-8f75-04b868c594a1 |  | textbox | Project Address:
text | bb311aed-d63c-427b-9031-081bb148d86b |  | textbox | AE Smith Site Manager:
text | 3ed7586f-75c1-49e4-82a2-88dd04bbeecb |  | textbox | Consultant:
text | 10ea1d41-1768-4262-a1aa-060af1a01618 |  | textbox | Client
checkpoint-no-status | 0d418e81-f3d0-47a5-9552-fb4b3cca3e14 |  | checkpoint | Quality Plan for the Project
checklist-flat | ef2c9b78-1c6d-4fa6-8494-8a3d34acbad1 |  | checklist | RBG Combined Services HDPE Potable Water Pipework Installation |  |  |  |  | Yes | RBG Combined Services HDPE Potable Water Pipework Installation | 587a1ea2-2d98-4741-ba46-97a1e1066ff2
checkpoint-status | b1a4af62-9333-4280-a529-7825350fe64a |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | f5ba4de4-fc2b-425f-848e-50c68f6eafa6 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | 3c37ebf1-7478-4272-ac50-916c999f0b14 |  | checkpoint | Inspect trench depth, width and pipe alignment
label | 1f5f14d0-0a46-5076-942c-70387bd78029 |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | 6a4a5612-500c-5daa-bd17-158ae30120b8 |  | note | QA documents to be provided prior to installing pipework in trenches . CPB to provide to AE Smith.
checkpoint-status | 66dda95b-a0c2-480b-b08d-f6b2b72b9e26 |  | checkpoint | Number of pipes and dimensions of pipes shall be shown on the drawing
checkpoint-status | a8c24b3e-58e0-422a-96b1-35c9232254ea |  | checkpoint | Location of pipe
label | 45226daf-6ddc-5f22-b9bb-9acd558e6145 |  | note | Shall be as shown on the drawings
label | a5246ab5-35fc-533a-b91d-6751d7cac815 |  | note | Ensure correct clearances between water service and other underground services.
checkpoint-status | 407771b4-c998-4e44-8c81-6fa5d0efcd52 |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
checkpoint-status | d1cdc9b0-6e1e-4915-af80-0e2a8f247346 |  | checkpoint | Jointing of pipes only via. Rotatable steel flanges, EF Coupling and Butt Welding.
checkpoint-status | f3722075-ca1e-4c00-9c18-2ab560e3d02e |  | checkpoint | Electrofusion Welding Checklist completed for each joint?
checkpoint-status | 199c706a-f340-46b6-9060-509c9f712a10 |  | checkpoint | Butt welding checklist completed for each joint ?
checkpoint-status | c85e8094-f833-4797-a369-0165404fe739 |  | checkpoint | Install valves, tees and bends
label | be38ee2f-c50f-5cd6-a263-61d2ff548f69 |  | note | Install all connections as per construction drawings
label | 854b0cf7-bceb-5a8c-bf65-f3f39f7a1bac |  | note | All valve 100mm and above will require a 1050mm manhole.
checkpoint-status | 7000a464-b8f7-44e7-ab56-bfe1c5e247a4 |  | checkpoint | Installation of ductile iron bends
label | 239721b3-cd49-5229-ad74-33b6b8f3e1fe |  | note | Inspect pressure class on fittings and ensure correct pressure rating prior to installation.
label | 870c7f91-0842-5318-ae66-2460a7e070f9 |  | note | Ensure correct gaskets are installed.
label | c89b836f-47cb-5356-9c6b-993f45c05393 |  | note | Washers installed on both sides of the flange.
label | 31696213-b74a-56ab-b33d-6caed3a04cbb |  | note | Bolts to be tightened in correct tightening sequence.
checkpoint-status | 50ba9efa-0143-40a0-b7fb-23772d49d35f |  | checkpoint | Install Thrust and Anchor Blocks
label | 8d55a9f7-0068-5557-9082-1fefd9343b29 |  | note | Minimum dimensions as per IFC drawings.
label | 03ef9c7c-b704-55b1-94a2-6735ab38d270 |  | note | A protective Denso or black coating membrane is to be installed around the pipe and the concrete anchor/thrust blocks to prevent abrasive damage.
checkpoint-status | 98962c2f-97c6-4dd8-9289-d82f083be9a5 |  | checkpoint | Completed Construction Pressure Testing with Air
checkpoint-status | d197186e-5f6a-4ac5-98e6-9da1a5d8fef6 |  | checkpoint | Pre-Pipework Pressure Testing Inspection
label | 61d9d852-7ecd-5861-a244-c91d0f6396dd |  | note | Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | f7077cef-3021-58ed-b88e-8fec14790ab5 |  | note | Ensure each test length is capped and ball valve installed.
label | e444efc0-92d9-5d01-bda1-d6877f023ef8 |  | note | Ensure all valves in the system are in the correct position and tagged “DO NOT OPEN” or “DO NOT CLOSE”
label | adc2a524-0490-549e-bf2d-5fc9217af438 |  | note | All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing.
checkpoint-status | 7b5cfb5a-3e20-44fa-8397-e16bc0dff973 |  | checkpoint | Introduction of Air to 300 kPa
label | 7f2d9410-77f4-5211-b135-0ceb2a497fd4 |  | note | Gradually introduce air into the system to a pressure of 300 kPa and hold for 1 hour.
label | f54a9352-5577-55ab-9ff9-43c105880bad |  | note | Monitor for any drop-in pressure.
label | 4126733c-45e2-5e4c-8b7b-8576d8fe8f17 |  | note | If a leak is identified discharge the air prior to rectifying any leaks.
checkpoint-status | 9a127470-f19d-4d84-854a-544d47b83642 |  | checkpoint | Increasing Test Pressure
label | 012fd3ad-5953-580b-b117-92a9225d48f5 |  | note | If no leaks are identified Increase pressure by 10% increments until test pressure is achieved.
checkpoint-status | 9bce60e2-322f-4ae7-bf33-1d43167fcfbf |  | checkpoint | Pipework Pressure Test Report Completed
checkpoint-status | 1f012bda-dc7f-49f3-bead-30c191a85678 |  | checkpoint | Installation of Trace Wire
label | 5f304721-e92b-5fbd-af5a-41c3fc4507fb |  | note | Install Trace Wire and ensure tracer wire is continuous between valves and any excess coiled in valve box.
label | 0e802672-3652-5d6e-8f9d-3987542f091c |  | note | Test Trace Wire following installation.
checkpoint-status | e1706b07-87c1-463b-8e8a-ec10239d8048 |  | checkpoint | As-Builts Completed.
holdpoint | 54c918c7-8c76-4c87-9a13-f313df2a3332 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat |  |  | checklist | B5A - Area valve service units – closure and zoning test |  |  |  |  | Yes | B5A - Area valve service units – closure and zoning test | 62221e2e-562a-4bac-95e0-43884d80a0b0
checkpoint-status |  |  | checkpoint | B5A - Area valve service units – closure and zoning test complete
text | 4724c0fb-b223-5bbd-8b5e-b6dabcef804a |  | textbox | Plant ref
text | ed57b170-5faf-5075-a862-c15c38bddf5a |  | textbox | Test by
text | fd66c3b4-910e-58dd-8b36-ae2774f3add5 |  | textbox | Test date
text | 94b4f34e-4f93-5e88-b75d-ef8f88fe85ec |  | textbox | Revision
checkpoint-status |  |  | checkpoint | This is to certify that CLOSURE and ZONING of the AVSUs was tested in accordance with paragraphs 15.63–15.68 on the pipeline system as follows:
text | 41048983-90ef-5923-94c6-0017798f3999 |  | textbox | AVSU number
text | aa684395-8586-596e-9930-8096665abfa3 |  | textbox | Test pressure (kPa)
text | 16c41161-e274-5db9-87dd-bcf91f5b8a58 |  | textbox | Downstream/upstream pressure change after 15 min (kPa)
text | c77b7edc-447c-5f6a-b2ab-aff7d89d22ab |  | textbox | Terminal units controlled (total no)
text | e0cb3f72-36aa-5881-9102-72a1e322cf90 |  | textbox | Terminal unit labelling
text | 47fd0373-b061-50a1-be4d-d78c365106e4 |  | textbox | Contractors representative:
checkpoint-status |  |  | checkpoint | Sign Off Complete
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
checkpoint-status |  |  | checkpoint | Signed off By Witness
text | ce95209f-f790-5d18-9cd4-f1c820e1dac7 |  | textbox | Witness Name
checkpoint-status |  |  | checkpoint | Signed off by Consultant
text | 3df14d22-f7fc-5eb9-ad2d-913d1ea77942 |  | textbox | Consultant Name
checklist-sectioned |  |  | checklist | AES-NZ1005-STE-ITP-PMT-0028 - Tank farm installation |  |  |  |  | Yes | AES-NZ1005-STE-ITP-PMT-0028 - Tank farm installation | 633ae41f-f9e3-4e71-a9ee-da0e16c23f7c
checkpoint-group |  |  | section | MATERIAL COMPLIANCE
checkpoint-status |  |  | checkpoint | RDM & Consent Approval - CPB Hold Point
label | 2a45dd9e-be03-53a3-95ed-7a06491cff25 |  | note | Resp. - CPB
label | 234e1a78-dc67-5928-8b02-a534685b5f01 |  | note | Referenced Documentation - RDM Tracker Consent Tracker
label | 21e4fb9c-1840-5ad0-836c-9d287cec2ee7 |  | note | Conformance Criteria - RDM approval tracker Consent approval tracker
label | d799d082-cd45-5c9d-a8ce-a2656759387d |  | note | Method - Document Review
label | 4e77abe4-c8ae-5300-b2a2-dd575997b471 |  | note | Frequency - By Building/ Site Wide
label | 68b07d44-a10f-5ce9-a17f-42b2a19b0fbb |  | note | Hold Point - CPB
label | ca7021a5-fa69-5fdf-a3fc-334bbd865485 |  | note | Records - Receipt of Approval by Client
checkpoint-status |  |  | checkpoint | General - CPB Hold Point
label | b56036c4-38f7-56f1-9ba5-fa6c21c99676 |  | note | Resp. - SE
label | f4997887-24f7-56dc-bc87-1f135fb73414 |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001
label | 5924640d-4bfb-5fc6-950d-c04b23b5c6d5 |  | note | Conformance Criteria - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
label | f19d21a5-0695-5035-b862-4c93da8672c3 |  | note | • Specifications & QA Documents Approved
label | 3bbc2cb1-9928-5123-afa7-1cb4f12f8e24 |  | note | • Drawings are confirmed
label | 957b2539-544f-54c8-baf9-1f423bb9af60 |  | note | • Equipment fit for purpose
label | 049d1a76-eaca-5616-b365-d0dce2d77ec4 |  | note | Method - DR
label | a4974a4e-ea72-5def-9e0c-455295b02377 |  | note | Frequency - Each material
label | 1a11f39a-220a-5ed7-b17c-746a7b4588bc |  | note | Hold Point - CPB
label | 6306119e-8ae5-588c-adc0-aca0943aea56 |  | note | Records - Aconex approval Incoming Inspection Checklists Drawing Register
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | HDPE Support system & seismic Loops
label | 84e3f886-1f36-5449-9c62-4b6deaed1b41 |  | note | Resp. - SUP
label | 6260195e-c4d3-5c65-bad3-149d406ecb91 |  | note | Referenced Documentation - AES-NZ1005-TNK-DSH-SEI-0001 AES-NZ1005-STE-DSH-SEI-0002
label | e93c6f35-9395-5a64-9f62-1c6dbb72865c |  | note | Conformance Criteria - Check the piping support system has been installed as per the Modframe design
label | 6f837dc1-184a-57fa-91d6-f35b0974e550 |  | note | Method - V
label | 00e8723d-4586-5e6d-9026-5d31d0bb497e |  | note | Frequency - Once
label | 610a51af-c22f-52cc-89d8-29f323f62650 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | HDPE installation and testing - CPB Hold Point
label | c7932979-219e-5c5d-a028-49af8957328c |  | note | Resp. - SUP
label | fd5d27a3-aeef-5463-a4c3-f75bf9523ab8 |  | note | Referenced Documentation - AES-NZ1005-STE-ITP-PMT-004
label | e2e10e7d-48f3-517b-b9bd-eab83cf3786c |  | note | Conformance Criteria - Refer to AES-NZ1005-STE-ITP-PMT-004 for the installation and testing of HDPE pipework
label | 1a6f6a3e-8956-5c12-a3b8-fb5cf3d6f0b6 |  | note | Method - V
label | 0c5b1987-3454-558c-9053-202bf994f67b |  | note | Frequency - Once
label | fea5faf0-6608-55a3-b69f-212de49c0dc7 |  | note | WP - AE Smith
label | 6b8e41f9-3d51-501e-8287-312708eaad36 |  | note | Hold Point - CPB
label | e3760b40-fcf0-59e5-9429-f1dd510a8da7 |  | note | Records - FRT +weld test reports +QCC (refer site wide testing check lists)
checkpoint-status |  |  | checkpoint | Confirm DCW flushing and disinfection complete - CPB Hold Point
label | 8915abde-f97a-5c14-94d3-9a08062ac85d |  | note | Resp. - SUP
label | 65581445-23ff-5917-8a2b-b3074a81fa60 |  | note | Referenced Documentation - AES-NZ1005-STE-CMP-HYD-0001 NZT5007-STE-HSSP-0001
label | 459114de-62e7-5c4b-87d6-b53b973a9474 |  | note | Conformance Criteria - Completed with the flushing and disinfection of the site wide ring main Refer to the Flushing and Disinfection commissioning plan
label | 047aeb17-c5f9-5ceb-9ae7-a8463c79ba73 |  | note | Method - V + DR
label | 38b0c829-5a36-5fc7-bbea-6406e916bbde |  | note | Frequency - Once
label | e8ad34c5-2c29-5593-bc9a-3884e23c565a |  | note | WP - AE Smith
label | 9927e2ea-e071-510e-a4d1-1c33c8504da8 |  | note | Hold Point - CPB
label | d8583f16-45b1-5ca0-9754-1e7ad44791d4 |  | note | Records - CMP + Check Sheet
checkpoint-status |  |  | checkpoint | Confirm Hydrostatic pressure testing complete - CPB/IR Hold Point
label | 0e1b0361-ecff-54da-bfe8-c3bf1783ea68 |  | note | Referenced Documentation - AES-NZ1005-STE-ITP-PMT-0024
label | 060064a8-ad6b-5285-998c-9ae9eb24dea0 |  | note | Conformance Criteria - Refer to AES-NZ1005-STE-ITP-PMT-0024 for Hydrostatic pressure testing
label | d3b103ad-b5f0-527e-b536-574dc8fd7630 |  | note | Method - V+M
label | 1a56c8e5-92c7-51af-8f78-6ddf97028ff5 |  | note | Frequency - Once
label | b3114ad6-259d-51f8-a3b0-3596594e61e3 |  | note | WP - AE Smith
label | 3f90a580-1eb6-54d7-ba17-e98b8d677637 |  | note | Hold Point - AE Smith / CPB / IR
label | 12d0b62d-4ef3-57aa-ac30-3f14d4202600 |  | note | Records - Check Sheet + Photos
checkpoint-status |  |  | checkpoint | Electrical Installation Complete - CPB Hold Point
label | 357db98c-cbcb-5fc7-9bf0-dcf9a6a3f3b9 |  | note | Resp. - SUP
label | af1261a2-4497-5a95-8de1-819b601c796e |  | note | Referenced Documentation - AEC-NZ1005-STE-SPC-ELE- 0002 AS/NZS 3000:2007 AES-NZ1005-TNK-SHD-ELE-0002
label | 1ad6c54c-d501-5530-bcba-12ca31fa01c4 |  | note | Conformance Criteria - HSSB installed. Mains terminated Feeds run to filter controls Feeds run to pump drive board Feeds run to chlorine dosing units Labelled & Tested
label | b6e2b596-1f29-5bfc-9697-fa994477bbf3 |  | note | Method - V + FTR
label | 1ffed8f7-d629-50ae-b91b-3de5f1c31401 |  | note | Frequency - Once
label | ef6286db-118e-57ce-a103-4d0d152f240f |  | note | WP - Ae Smith
label | 46f8c546-d8b5-578d-a623-37593f5c9ad4 |  | note | Hold Point - CPB
label | d2e93161-9e15-572e-b34b-70b5ed44b7ec |  | note | Records - Check Sheet + COC
checkpoint-status |  |  | checkpoint | Chlorine dosing Install & commissioning (Include PRVs)
label | 75604a1d-383f-5770-802c-e25e7146cd15 |  | note | Resp. - SUP
label | 91d422dd-95a6-5282-9221-4710bf51ba4e |  | note | Referenced Documentation - AES-NZ1005-STE-CMP-HYD-0004 Tank Farm Commissioning Plan NZT5007-STE-HSSP-0001 AS/NZS 3000:2007
label | 6fb58ff5-c54b-5fc5-bfae-8098805347d1 |  | note | Conformance Criteria - 1. Access is suitable to service dosing equipment
label | 233dd80e-36ce-571c-8020-aa0974330ec3 |  | note | 2. All electrical checks are complete and permanent power is on
label | cb26cb60-c91d-5087-8646-669a8591279e |  | note | 3. BMS connection is complete by others
label | c0d6d4c7-d64a-520b-b6ea-d859e1739051 |  | note | 4. Pipe work checks are complete
label | 15163f0d-8836-5dfe-a408-590429ff077b |  | note | 5. Isolation is provided to enable either system to be maintained seperately without affecting the operation of the other
label | 05fabeb9-e9bd-5964-be50-1a88af73891e |  | note | 6. Equipment mountings are complete
label | 1525c875-af5a-5e37-abfd-eadc859489a8 |  | note | 7. Pressure reducing valves are installed in the correct flow direction and set to desired pressure
label | 5bb296e0-3e2d-5f2e-93f0-b027b734d258 |  | note | 8. Dosing control sensors are installed.
label | ec7ce5de-ae76-58d2-8e5c-9fc846cf297d |  | note | 9. Non return valves are installed in the correct flow direction
label | 8b9652be-f5b6-59d6-8ad1-7ef10d3c68d9 |  | note | 10. Dosing specalist to commission and provide report
label | 3d9a765e-27ca-5cc9-bf0f-0f3415df14e0 |  | note | 11. BMS monitoring is commissioned
label | 434e8636-b502-514b-a963-e4dd16b84d73 |  | note | 12. Confirm treated water meets the requirements of the NZ drinking water standard.
label | 17d5b75d-9e45-52c1-81f4-2cc4c28a2bb9 |  | note | Method - V
label | ddea88ba-fbbd-5093-9fcd-dc6b2d1b4903 |  | note | Frequency - Once
label | 37ce3ef2-85f8-5d02-8f62-1edba7b64804 |  | note | WP - AE Smith
label | 38118d4f-7450-573c-9128-fcddd3a101d8 |  | note | Records - Check Sheet + FTR + LTR + CMP Report
checkpoint-status |  |  | checkpoint | Domestic Cold water Pumps & Drives
label | ad2b2032-f437-5066-ba19-f8db91f4b82f |  | note | Resp. - SUP
label | a7a98268-1ad2-5776-bd15-ec9e6185e645 |  | note | Referenced Documentation - AES-NZ1005-STE-CMP-HYD-0004 Tank Farm Commissioning Plan NZT5007-STE-HSSP-0001 AS/NZS 3000:2007
label | ed366755-9db8-5f89-b728-7f276c32a1f0 |  | note | Conformance Criteria - 1. Confirm pumps & drives are as approved submission.
label | 08e2f469-902a-55f2-b61e-ead44099df37 |  | note | 2. Installation is as per shop drawings.
label | 96477c45-d741-5953-9bde-244bcc663d4a |  | note | 3. Motor drive board installed & wiring to pumps complete.
label | 17cf5c89-d0bf-5f77-b4cd-6d39ec4d6f6f |  | note | 4. All electrical checks are complete and permanent power is on
label | f1aa671f-ed40-5efa-86aa-2270112094f3 |  | note | 5. Pipe work checks are complete
label | 1963e42e-f7a8-55c0-be0e-3ffb0f052d11 |  | note | 6. Pump mounting and vibration pads and seismic restraints are complete
label | 6a3bac7c-4e32-5c01-82a0-d0da80e52d90 |  | note | 7. Non return valves are installed in the correct flow direction
label | 80aef274-6108-5c61-91e6-0a5e20d1d4ac |  | note | 8. Isolation is provided to allow maintenance of any individual pump
label | 06ef9287-b971-5546-a0d6-9f6ad352eac3 |  | note | 9. Grundfos to commission and provide report
label | dfca2db0-3ec1-5aaa-854e-e331b8abdb09 |  | note | 10. BMS monitoring is commissioned
label | a5aef818-fa2b-507b-866f-5278413f3b3e |  | note | Method - V + FT
label | c62d0235-fcfc-5c7f-ae80-0d3796742d16 |  | note | Frequency - Once
label | ed74a462-3da7-58b4-9ba8-0564c53dbe22 |  | note | WP - AE Smith
label | f0585c91-1e0b-5e6a-8bf7-812bb1e49423 |  | note | Records - Check Sheet + FTR + CMP Report
checkpoint-status |  |  | checkpoint | Primary and secondary Filtration systems
label | 40115666-9f0e-5af3-aa29-b6a851aac91f |  | note | Resp. - SUP
label | 820dd0d2-d1f4-55c7-b7b4-96f90b8de445 |  | note | Referenced Documentation - AES-NZ1005-STE-CMP-HYD-0004 Tank Farm Commissioning Plan NZT5007-STE-HSSP-0001
label | 0077c1c4-10ff-574a-a720-590650215e66 |  | note | Conformance Criteria - 1. Confirm filters are as approved submission
label | 61be2606-f3cc-5997-89ed-5192cedf1964 |  | note | 2. Installation is as per approved drawings
label | 640e222c-9142-578d-afdf-84ef95803eb7 |  | note | 3. Pipe work connection checks are complete and without leaks
label | d07ac9e6-8357-5e98-81ab-016af384233a |  | note | 4. Mountings are complete
label | 91264d1f-b2f3-51c6-a9d3-f28e0b30fb68 |  | note | 5. Non return valves are installed in the correct flow direction
label | 2f22484c-bb2b-57f0-889e-e6b72fe09212 |  | note | 6. Isolation is provided to allow maintenance of any filter
label | 3ca08122-7517-5292-b5e3-fc8ff181324d |  | note | 7. Backflow drains provided
label | 80e264a0-5338-5029-9a43-88b6f6586b07 |  | note | 8. Southland Filters to test and commission filters and provide report
label | 5266f9de-60c0-5ab0-b3f5-5f0aadd3efd9 |  | note | 9. BMS monitoring is commissioned
label | f8ff4f02-82d5-58a5-b230-df1ee74fdb8d |  | note | Method - V + FT
label | 8dc9e933-2acf-51ce-926b-98da86f78bde |  | note | Frequency - Once
label | ebe5b600-21fc-5125-aebc-865f092985a7 |  | note | WP - AE Smith
label | 2bbb4dab-65a5-5949-a195-71206e0a50d5 |  | note | Records - Check Sheet + M + FTR + CMP Report
checkpoint-status |  |  | checkpoint | Motorised control valves
label | 34fd67b4-a07b-5960-a64f-536b5c6a8893 |  | note | Resp. - SUP
label | b0d5a89e-bb3d-5bb9-94fc-4d94a48084f2 |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001
label | 78a62309-e6e8-5564-b2fa-cebd0b46ec72 |  | note | Conformance Criteria - 1. Confirm valves are as approved submission
label | b221bafa-37e3-5ff1-8ef3-b20a50673c0f |  | note | 2. Installation is as per approved drawings
label | 28ea9aec-06e9-5698-aeeb-045a24fdf380 |  | note | 3. All electrical checks are complete and permanent power is on
label | 3da0f7a0-87bd-5e50-8d15-484ff75ff690 |  | note | 4. Pipe work connection checks are complete and without leak
label | 45728eab-cc19-5916-8e90-6786cdaf456b |  | note | 5. BMS control is opertional- check motorised valve positions in normal and emergency operating modes
label | d9ff9bfe-3a1a-50a1-be6a-5d2c29a80a5a |  | note | 6. Plantroom bypass Button is operational – check motorised valve positions in activated and deactivated modes.
label | c33d51c8-4299-5a61-abc9-9743bdaa6532 |  | note | 7. Check button is clearly labelled.
label | 71f359c3-6442-597e-9269-5aa8bfbb5c46 |  | note | Method - V
label | 25004a47-1d1c-56fd-a475-3331a33a5d8b |  | note | Frequency - Once
label | 617ce502-8cb5-5398-b735-717c99d005cd |  | note | WP - AE Smith
label | b6dcc20e-94dd-5f11-bbdc-22125506ea72 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | Potable Water Tank Level Control valves
label | 24cf8682-041e-58aa-91e6-44d50373fa0b |  | note | Resp. - SUP
label | 14f3626e-e59b-5175-ab7b-671f602c08d1 |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001
label | dda027ca-6665-50d3-8686-3a141dd1d6e9 |  | note | Conformance Criteria - 1. Confirm control valves are as approved submission
label | 9db39203-c657-50fe-b53c-ec3cd74c1825 |  | note | 2. Installation is as per design
label | d04a8bc5-e5f0-5fd2-8b2f-9f887e637004 |  | note | 3. Float valves are adjusted to to ensure overflow state does not occur
label | d292e473-ab7d-56fe-83fc-5838f13ca290 |  | note | Method - V
label | 45e8002f-6923-52a5-ab2b-d08d314b201c |  | note | Frequency - Once
label | 03f47be1-c05e-54ca-82ab-afba54c6cc51 |  | note | WP - AE Smith
label | 9cf468af-e720-543c-bcf8-e2f98abe032b |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | Alarm indication on and tank level montoring on BMS
label | 2a01afd3-f3e3-5087-a8fb-3ba6d12f97d3 |  | note | Resp. - SUP
label | 33ae1418-074a-532d-aa38-6717eebdd59e |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001
label | e203e4b7-3958-5380-b241-e280735eb463 |  | note | Conformance Criteria - 1. Tank level monitors are installed as specified
label | 1d0407c3-9c55-5740-adae-a24f53879b5c |  | note | 2. Tank level monitors are connected to the BMS by others
label | bcf466e3-2303-564e-9b72-c9f4162b8bbf |  | note | 3. Verify BMS level output
label | d98f3d79-490a-5d71-9be8-a6943db7d3aa |  | note | Method - V
label | e13da049-99a1-5ecb-8e3d-794c88700eb8 |  | note | Frequency - Once
label | 04e25f2f-0837-5b6d-8fad-8d2f028d2e30 |  | note | WP - AE Smith
label | e629aa78-8f7e-5e2e-bdb7-55aa48d3ccf5 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | Back flow preventors
label | 8e590377-ebe4-5870-ac13-b98a5c57c781 |  | note | Resp. - SUP
label | 74c124e8-2c27-572a-90a8-b3562441e8d6 |  | note | Referenced Documentation - AS/NZS 3500.1:2018
label | 5e5cc6ab-5d23-5579-a7fa-157b6eb37e8a |  | note | Conformance Criteria - 1. Confirm backflow preventors are as approved submission
label | ec2fcf79-65e2-5f1f-b393-170106bd5200 |  | note | 2. Installed as per design
label | 6dd38f3a-516b-5578-b735-505d950feb09 |  | note | 3. Pipe work connections are complete and without leak
label | 77c2cb14-e4e9-5a78-9d0e-debbb676dc2c |  | note | 4. Check flow direction
label | 3691d8ae-233c-53c0-bc5f-7a4bdc82b24d |  | note | 5. Check strainers are clear 6. IQP test
label | 46ecaf3c-5738-54ee-acd8-5393328fb024 |  | note | Method - V + DR + FTR
label | b1368ceb-5ede-55a1-adfb-06c17b1410e7 |  | note | Frequency - Once
label | fa53b4d0-c242-52ef-9370-8bae5a28e822 |  | note | WP - AE Smith
label | 7df8e4af-bda5-5a35-933b-21c461d0a842 |  | note | Records - Check Sheet + IQP - FTR
checkpoint-status |  |  | checkpoint | Wash bay supply & RPZ
label | fb47e634-4f5e-5313-b5f2-cfcbfbe89a52 |  | note | Resp. - SUP
label | 096bca39-e684-5b1c-8bcd-f2de2f6f1edc |  | note | Referenced Documentation - AES-NZ1005-STE-ITP-PMT-004 AES-NZ1005-STE-ITP-PMT-027 AS/NZS 3500.1:2018
label | f4fcb876-83f9-56e3-a0b7-1836ef08a5b8 |  | note | Conformance Criteria - 1. Confirm pipe work has been installed, tested, flushed and disinfected as per items 2.2, 2.3 and 2.4 2. Confirm RPZ Back flow preventor has been installed tested as per item 2.11
label | f97c237b-41d1-5bdc-aa1c-ddd125a5d971 |  | note | Method - V + DR
label | 6c5dfcb7-012e-5ccd-a39c-b5ee9c474a2c |  | note | Frequency - Once
label | 6ee31139-4a38-55a9-979c-f311ad6fc522 |  | note | WP - AE Smith
label | a1dd0799-b90d-5b78-a06c-76e30ed9291d |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | “As built” drawings
label | d4fae8c4-56d3-51d7-96f8-8e91aab35e20 |  | note | Resp. - SUP
label | c078be11-df31-5b4b-bbfc-3edac73d6025 |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001
label | 0afa98e9-8608-5472-b337-063323fce631 |  | note | Conformance Criteria - 1. Mark up construction drawings with as constructed changes.
label | 4f5ccf0d-644e-5e1e-9ad4-fc9e179e3cbb |  | note | Method - V
label | 1270b917-a4e5-5e0e-a45e-dde272d39cea |  | note | Frequency - Once
label | 6678f18c-43c2-5132-b538-ac6122c945a6 |  | note | WP - AE Smith
label | c4236d3c-d4e6-5b3e-9ccb-93bf610d35fa |  | note | Records - Check sheet
checkpoint-group |  |  | section | Completion Testing
checkpoint-status |  |  | checkpoint | Works Completion Test WCT 54 - CPB/IR Hold Point
label | d97701b7-4b48-548c-a82d-056e07b19466 |  | note | Resp. - SUP
label | e460ec16-1e41-5167-9f3f-53d8da0bee9b |  | note | Referenced Documentation - Schedule 11 WCT 54 (e)(f)
label | 1b59fb43-3835-5b3c-b8d2-94cddd87f6b0 |  | note | Conformance Criteria - The EIS for the New Waikeria Facility have been installed in accordance with the FDD. This includes EIS testing and satisfactory commissioning (including interfaces with other services) has been completed, recorded and compliance results presented to the Independent Reviewer for the following systems: (e) general power; (f) earthing system;
label | be5d2bb0-1f1d-580f-8434-331d4bc34a7d |  | note | Method - FTR + V + DR
label | 217922a2-ec70-568f-8d12-7d253b9fe057 |  | note | Frequency - Once
label | df6e0e7f-d008-5322-970c-1b7a58a3c33d |  | note | WP - AE Smith / LJE
label | ba53e52c-2366-5c1c-bc60-2d1bdeb4a6c1 |  | note | Hold Point - AE Smith / CPB / IR
label | e3a6f5dc-96cc-5adc-a7f0-2121ae9b8ddd |  | note | Records - Check Sheet + QA documents + COC
checkpoint-status |  |  | checkpoint | Works Completion Test WCT 68 - CPB/IR Hold Point
label | 8009e1a2-a8b7-55fb-9ae4-cea2e0961ad7 |  | note | Resp. - SUP
label | fd16ed07-844e-59d1-895c-a4238fa34dde |  | note | Referenced Documentation - Schedule 11 WCT 68 (a)
label | 149dbade-0682-5c9c-9ee8-5570b0cd4fc2 |  | note | Conformance Criteria - PDS testing and satisfactory commissioning (including interfaces with other services) has been completed, recorded and compliance results presented to the Independent Reviewer for the – · pressure test all cold and domestic hot water pipe lines, · operation of all valves, backflow devices, pressure devices; · BMS connections to building management systems; · tank control systems testing; and · water metering testing. Independant reviewer to: (i) Attend and witness a selection of PDS commissioning at the Independent Reviewer’s discretion (Contractor to invite Independent Reviewer to all); and (ii) Receive and review
label | 73174ba8-d9c1-5fc4-a7e3-5dc11f1cd5e7 |  | note | Method - DR + V
label | f8e93757-d757-5e87-9296-0133f1922ab0 |  | note | Frequency - Each lot
label | 8c5ce9c5-aa56-5410-af37-453431851a3f |  | note | WP - AE Smith
label | b96b7ea2-52f3-5023-91a0-763dbc424fc0 |  | note | Hold Point - AE Smith / CPB / IR
label | 470662fe-2d82-50f5-adba-43c19c026adb |  | note | Records - Check Sheet QA Documents IQP certificates
checkpoint-status |  |  | checkpoint | Works Completion Test WCT 80 Potable Water storage tank and Pump - CPB/IR Hold Point
label | dd8f8157-fd20-57cf-a5fe-1681fdfc7625 |  | note | Resp. - SUP
label | b5962026-52b0-5527-a462-a29c2ed90e49 |  | note | Referenced Documentation - Schedule 11 WCT 80
label | ea721daf-cbb7-5cbf-b4d4-24ee02f00748 |  | note | Conformance Criteria - Demonstrate operation of potable water storage tanks and pumps, providing onsite potable water for a minimum of 72 hours at normal demand in the event that mains water supply to the site is compromised. Activate emergency supply remotely with the BMS Independent Reviewer to (a) Attend and witness verification testing. (b) Receive and review documentary evidence of quantity.
label | fb11080d-b6bb-5cd3-a770-e03a7176f2eb |  | note | Method - V+M+FT
label | 1557b438-92c5-5489-9771-8508729eb285 |  | note | Frequency - Once
label | 1de491c9-8a3d-56ce-9995-57a1948c0435 |  | note | WP - AE Smith
label | 3fcfcac1-a410-54b2-81e6-049e439b9e78 |  | note | Hold Point - AE Smith / CPB / IR
label | 20f41b47-fe35-58cf-93bb-05ee0d445235 |  | note | Records - Check Sheet QA Documents
checkpoint-status |  |  | checkpoint | Works Completion Test WCT 81 Tanker connection point - CPB/IR Hold Point
label | 347fbd0b-718b-58a3-bac3-1b31fc181aa1 |  | note | Resp. - SUP
label | a01d2fe6-03d3-561f-93fa-da30f03c2ec2 |  | note | Referenced Documentation - Schedule 11 WCT 81
label | 4b373b02-c886-5144-a29f-907a5d4715af |  | note | Conformance Criteria - Verify the tanker connection points to the potable water storage tanks are provided. Independent reviewer to visually verify
label | 13f3f531-4d71-5b44-a047-bb865523f9cb |  | note | Method - V+M
label | 85e9e0d3-8c83-5ce6-9670-1056a60c37e8 |  | note | Frequency - Once
label | 5f0dac52-551c-5d4f-acce-465eae7238cc |  | note | WP - AE Smith
label | a6717214-2bf5-59f5-a1bf-a6440626d89f |  | note | Hold Point - AE Smith / CPB / IR
label | bdb557f5-e052-52a6-814c-7673009f0233 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | Works Completion Test WCT 82 Loss of mains. - CPB/IR Hold Point
label | f3336363-5638-592e-9ad5-9a2dce8b7fd4 |  | note | Resp. - SUP
label | e4bbf5b0-b8a6-5123-9ac8-d88dfe482d1c |  | note | Referenced Documentation - Schedule 11 WCT 82
label | 37d5a85a-0217-5ff3-bbaf-c37b4d0281b5 |  | note | Conformance Criteria - Simulate loss of mains supply by isolating the incoming mains supply. Verify The potable water pump operates to supply water in the event of loss of water supply from the site system. The test will evidence that the valve from the storage tank opens, the potable water pump starts up on generator power, and the pumps ramps up and down to maintain a pressurised potable water main to the New Waikeria Facility Site. Outlets within the New Waikeria Facility Site will be opened to simulate water consumption on the New Waikeria Facility Site. Independent reviewer to attend and witness
label | 329cf43d-7170-5758-862c-8bafcf6f2cbc |  | note | Method - V+M+FT
label | 6a5dbee4-1875-5657-a475-e5eceda0d910 |  | note | Frequency - Once
label | 79d34c5e-c491-509e-8a4d-c881dce96bbe |  | note | WP - AE Smith
label | eca331ac-108a-5ade-bbb3-f80dc2c7c2f8 |  | note | Hold Point - AE Smith / CPB / IR
label | e38671a9-b02c-5075-b330-e18a125ba31b |  | note | Records - Check Sheet
checkpoint-group |  |  | section | COMPLETION RECORDS
checkpoint-status |  |  | checkpoint | Testing Results
label | f7598548-3f19-587e-8e7e-3ccbc24d607b |  | note | Resp. - SUP
label | 4ef8316e-7340-5aaa-9500-cbdb9dd77ef3 |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001 AS/NZS 3500.1:2018
label | 917c7ede-ca63-57e5-a31c-91b89aebbfff |  | note | Conformance Criteria - All pipework pressure test reports shall be provided
label | 171e7cd2-7c3e-5e0a-9868-44f82e2a9543 |  | note | Method - DR
label | 7aafb87c-3e99-5963-9a48-4744f0a4ce3f |  | note | Frequency - Each lot
label | 9abf7a34-4d24-5513-90fc-1344d2c91ee4 |  | note | WP - AE Smith
label | fac24578-9b39-5a55-b19f-b3c2cf95cf43 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | Dosing system - CPB/IR Hold Point
label | 903c6f1b-f9a8-53d1-98b6-4edfa4711555 |  | note | Resp. - SUP
label | 569517ac-f6f2-512b-bcd1-7aa45e359925 |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001 DWSNZ-2005:2018
label | 09fec7e4-5ce8-5932-9993-736277a05873 |  | note | Conformance Criteria - Dosing testing and commissioning report shall be provided. Water testing results shall be provided
label | 397c5f88-cea8-5311-b77c-5768cf0c8ed3 |  | note | Method - DR
label | 1ec42603-a6af-5ebf-b485-22eacf90f576 |  | note | Frequency - Once
label | b04086cf-3774-51ab-955b-1899d1465b2b |  | note | WP - AE Smith
label | caf302ae-8b15-58b1-a1a2-9af5ded9115a |  | note | Hold Point - AE Smith / CPB / IR
label | e020815f-635b-533f-a2c3-19bb824766e8 |  | note | Records - Check Sheet, + FTR +LTR
checkpoint-status |  |  | checkpoint | DCW Pressure Pump set
label | 837b16e4-922a-5b42-946b-b73e7dbf6e2c |  | note | Resp. - SUP
label | a6837087-2662-5b07-b9c4-51e62b282b88 |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001
label | 0a34b975-281a-5476-a351-1ddeae0e7e6e |  | note | Conformance Criteria - DCW Pressure pumpset testing and commissioning results shall be provided
label | 7cf7da94-68fb-51f3-9321-a77c168bb3d9 |  | note | Method - DR
label | ce12f178-51d9-5902-9e0d-e418e7d5445f |  | note | Frequency - Once
label | 463fa840-5873-5f8d-bef5-3b81528ce85c |  | note | WP - AE Smith
label | aa9ceaed-6b02-5206-a8e0-e409abe616d0 |  | note | Records - Check Sheet +FTR
checkpoint-status |  |  | checkpoint | Emergency water supply activation - CPB Hold Point
label | ecb8818d-e2d7-5f1c-8c4f-9e1e34c73699 |  | note | Resp. - SUP
label | 49601a8a-fdb3-55a7-8b02-4b49e9e56a81 |  | note | Referenced Documentation - NZT5007-STE-HSSP-0001
label | 1bbbbc14-e902-5f41-85d0-8bd02b409c5c |  | note | Conformance Criteria - Verification of emegency water supply activation
label | 8025d589-e45a-5849-bc32-628fadd7fd43 |  | note | Method - DR
label | 740efebb-1448-5f1e-8e64-7d08bbe42b4c |  | note | Frequency - Once
label | af3dced6-cd6d-5b5c-a62a-87bf971960e3 |  | note | WP - AE Smith / HWL
label | 6a7c298d-a957-5fdf-9cfc-161619f7769d |  | note | Hold Point - CPB
label | fc9d2e3d-aa02-546b-a593-ec3cd9525d06 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | Manual Bypass Button
label | 98de14ee-deaf-5a7d-b62c-5330448a31e5 |  | note | Resp. - SUP
label | e39eebb5-b528-5fbf-918b-caa76bc072f0 |  | note | Referenced Documentation - AEC-NZT5007-TNKHSDG-1006
label | dbebef82-fc51-53ed-a64f-b15f7e40143c |  | note | Conformance Criteria - Verification of mains supply by passing treatment system by manual activation of plantroom Bypass button
label | 3eb203f3-b018-5feb-b987-00f762d0a2ee |  | note | Method - DR
label | 2c43ae2f-bc42-5102-bee8-4b8c0d1599bd |  | note | Frequency - Once
label | 1d949ae4-e755-5347-b01f-1f36677ce00c |  | note | WP - AE Smith
label | a88a9146-5c29-529d-a821-4f6ecec771a9 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | Backflow Preventors
label | 4369b2aa-8b5a-5a98-9389-34ef505a8c6a |  | note | Resp. - SUP
label | 4d64f4cb-4a78-5c92-a2c5-bcdd44da3787 |  | note | Referenced Documentation - AS/NZS 3500.1:2018
label | 441f6802-6d43-57b5-9484-6c2460e6ff81 |  | note | Conformance Criteria - Backflow testing
label | 3e85acb1-0d21-51d1-bfc5-7effb59fd81f |  | note | Method - FT
label | 8b9e17b0-35af-5c1b-a400-519e34b0b612 |  | note | Frequency - Once
label | 4bcbfa14-9774-5b1b-b2ac-831c3a777254 |  | note | WP - AE Smith
label | 22cbb4a7-66d2-558e-a4cd-6c1e12d722a2 |  | note | Records - Check Sheet + IQP Test report / Certificate
checklist-sectioned |  |  | checklist | Combined Services HHW & CHW Hydrostatic Pressure Test |  |  |  |  | Yes | Combined Services HHW & CHW Hydrostatic Pressure Test | 671b7bcb-df87-464e-9ecc-d989ebd88852
checkpoint-group |  |  | section | 1.0 MATERIAL COMPLIANCE
checkpoint-status |  |  | checkpoint | 1.1 - RDM & Consent Approval
label | 7dbf5a1d-3e62-5ff7-a807-10202d7feaef |  | note | Resp. - CPB
label | 7068cb13-8a4e-5117-a02b-886d68a72062 |  | note | Referenced Documentation - RDM Tracker Consent Tracker
label | 10ac9966-51b9-5e5f-b75c-612427073944 |  | note | Conformance Criteria - RDM approval tracker Consent approval tracker
label | 1e938b70-bf83-5788-8df2-ba2802153eec |  | note | Method - Document Review
label | 70421ff2-d41e-5945-ade2-a3f9a5e2ee0c |  | note | Frequency - By Building/Site Wide
label | 4868e02e-b10c-509f-ac33-3d24962a2277 |  | note | HP - CPB
label | 400fc825-4443-59aa-a7f5-3776822350da |  | note | Records - Receipt of Approval by Client
holdpoint |  |  | signoff | CPB HP
checkpoint-status |  |  | checkpoint | 1.2 - General
label | b4b1bfa7-67b6-5492-b9b1-dbc7bee28926 |  | note | Resp. - SE
label | 1100b3f8-2643-54fa-b922-ab802557fbce |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | 6c83f425-27f5-5ce5-825a-a886c3e8ba36 |  | note | Conformance Criteria - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
label | 13d75c94-d94a-54a0-aa06-5065be361919 |  | note | Specifications & QA Documents Approved
label | 6f7d24f6-c43d-5104-970a-a51871de567d |  | note | Drawings are confirmed
label | 635e2f35-7bcf-50ec-b776-c346b66740d1 |  | note | Equipment fit for purpose
label | 3d23aee5-7c2a-5301-8c3b-c0eea4f2a12a |  | note | Method - DR
label | aff1dc65-583c-5776-84f5-2a6cd94c92fd |  | note | Frequency - Each material
label | 85d7d66a-96a9-5464-b4ba-c1c65aec068a |  | note | HP - CPB
label | 1381b675-e8cd-5145-8931-d1ef426aee8c |  | note | Records - Aconex approval
label | 423785e1-26aa-58a1-8aed-76a8f25f8a93 |  | note | Incoming Inspection Checklists
label | 940cd259-ff1d-5d90-b724-31739c929023 |  | note | Drawing Register
holdpoint |  |  | signoff | CPB HP
checkpoint-group |  |  | section | 2.0 CONNECT PUMP TO HHW & CHW RING MAINS
checkpoint-status |  |  | checkpoint | 2.1 - Accept delivery of pump to site
label | 8a3c6ca6-3e46-5cb1-b04c-95be0253baa2 |  | note | Resp. - SUP
label | 5273458c-fb42-5630-a4a5-ea1f6322dd66 |  | note | Referenced Documentation -
label | 899f68dd-c714-50d4-b0f0-ad25046816ac |  | note | Conformance Criteria - 1. Check pump is rated for pressure test
label | 9fec7b3a-4656-5ca6-b3ba-e1cd23988c1f |  | note | 2. Check all supplied attachments are correct and in good order
label | 3670af12-6d1a-50c7-8834-dd6c01cc3ed5 |  | note | 3. Check fluid levels & fill as necessary
label | f6b5903a-f6ef-5996-89c1-d230d11cce5f |  | note | Method - V
label | d0e85f6d-2bbf-55d2-89e3-b9fae7a19590 |  | note | Frequency - Once
label | c46851d0-1b6e-5563-84c1-c8e448cba74f |  | note | WP - AE Smith
label | b2551c16-66f3-5290-92b9-509e4344ef33 |  | note | Records - Check sheet
checkpoint-status |  |  | checkpoint | 2.2 - Connect pump to CHW & CHW ring mains
label | be681df3-d4c2-5a49-8e13-3afa4bae9cfd |  | note | Resp. - SUP
label | daaa3565-e268-590d-ac5c-c406bb132a38 |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | 14f177b4-79b5-53fd-89d3-b2203831ad16 |  | note | Conformance Criteria - Confirm connections are safe and correct
label | 6c9e5c51-225b-5045-95ca-5419bcc700b4 |  | note | Method - V
label | 1a3a9102-55a2-55fc-8f89-16dfd595802e |  | note | Frequency - Once
label | 99fe6aad-b494-5af8-893a-7c086ef87cd5 |  | note | WP - AE Smith
label | 611687d5-9a18-57db-995a-c22f07a03ee1 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | 2.3 - Connect calibrated gauges for pressure test
label | 2ae8e0ee-1bd0-5ca6-b0b9-270a23554167 |  | note | Resp. - SUP
label | 08fc09dd-d090-5c24-bb58-8dfb379c342c |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | d4efb201-1aa1-5e97-8645-ede28ab3726b |  | note | AS 4041:2006
label | c83faef9-9f6c-570a-89f3-d72406fe6ca9 |  | note | Conformance Criteria - Confirm position is correct, gauge is in good order for test & calibrated
label | e7c5abbb-ccf6-5957-a8c2-5008179b80cc |  | note | Method - V + DR
label | 3797bf8b-9ac3-5e4e-a8f3-e66ca0276072 |  | note | Frequency - Each test
label | 686687f7-d200-528c-ad7f-efdc954c03bb |  | note | WP - AE Smith
label | b99b86f2-8f65-5603-8b28-514a0a9dc50c |  | note | Records - Check Sheet + Document
checkpoint-group |  |  | section | 3.0 HYDROSTATIC TEST (STAGE ONE)
checkpoint-status |  |  | checkpoint | 3.1 - Fill CHW & HHW ring mains with domestic water
label | 9b92cadb-c80f-56a6-9353-44402e1cf846 |  | note | Resp. - SUP
label | 046d0a6c-e59d-5c6d-9a64-e0601068fed1 |  | note | Referenced Documentation -
label | 45d26c64-2f78-5b0b-9e90-4afac3e46407 |  | note | Conformance Criteria - Completely fill closed loop system with water releasing all air
label | c82756b6-11e9-5828-bbde-9a6100154b5f |  | note | Method - V
label | dda75679-105b-5504-824b-7d29fbf48b6a |  | note | Frequency - Every time system is opened
label | 28e4626a-0b4a-51c5-b3ff-a948582d5a3f |  | note | WP - AE Smith
label | 5d8878f2-7c65-535e-8429-d4f6b2855f78 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | 3.2 - Gradually increase system pressure to 10 bar
label | 18910c8d-2c5b-53c3-910d-f106233f308c |  | note | Resp. - SUP
label | a58e799b-db12-5d2f-9e21-b365b9c7af98 |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | dd81a14a-6e4d-579c-9a36-d4db2149bb80 |  | note | AS 4041:2006
label | 1bbe82eb-0bd7-5c3c-a88e-9aae0ef783b7 |  | note | Conformance Criteria - Slowly raise system pressure to 10 bar
label | fd23c0c5-48b6-52ad-afdf-6539c10fce90 |  | note | Checking for any signs of leaks or pressure drops
label | 474f6137-6ed5-5de0-938e-435a4f3ad4c5 |  | note | Method - V+M
label | adc12b43-6b60-5929-871c-89708ca816fe |  | note | Frequency - Constantly Monitored
label | d23e8aa7-c3c0-597f-8d10-2e637c18f44e |  | note | WP - AE Smith
label | 887b80ed-fafd-50c1-876a-2cbbf98828e9 |  | note | Records - Check sheet
checkpoint-status |  |  | checkpoint | 3.3 - Hold 10 bar pressure for 2 hours (START WITNESSED)
label | 2bb489a1-50e7-5edd-8681-3cf62d6799c3 |  | note | Resp. - SUP
label | 28786a04-2364-586a-bc82-f1f48436da2a |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | 90a4af89-4f24-50e2-85dd-d8b5b1e9912d |  | note | AS 4041:2006
label | ebd38305-13e0-5571-a800-fb9b188ee56c |  | note | Conformance Criteria - Record START time & photograph gauge
label | 81012cc2-daa9-551a-a420-4ed2636b68fb |  | note | All relevant parties to witness starting pressure of 10 bar
label | ea5e12a7-0d59-58fe-ab0a-5e648e2d1cc1 |  | note | Method - V+M
label | c79dc6c0-0ac5-51db-ab6e-55375e82a145 |  | note | Frequency - Once
label | e17d3be8-52b3-5aeb-88ca-1042def825f9 |  | note | WP - AE Smith
label | 3ae15633-cceb-58e5-a992-c2a3c2d411a4 |  | note | HP - AE Smith / CPB / IR
label | e9954e1a-00bf-58e8-8e83-8ad8f07dacfb |  | note | Records - Check Sheet + Photos
holdpoint |  |  | signoff | AE Smith / CPB / IR HP
checkpoint-status |  |  | checkpoint | 3.4 - Hold 10 bar pressure for 2 hours (END WITNESSED)
label | 5adca4bb-7c79-5fd1-ad9b-0ac1d5c35aa5 |  | note | Resp. - SUP
label | 2adb0c69-470a-5218-b41d-e0dc97ac1352 |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | aed28a3d-5528-5e1b-9ab9-53193b0991c8 |  | note | AS 4041:2006
label | 6aa4f695-5187-5eff-8175-64a96519fc7a |  | note | Conformance Criteria - Record FINISH time & photograph gauge
label | 02ef5a7e-b6c4-5187-acce-fdfc48b1a6b8 |  | note | All relevant parties to witness starting pressure of 10 bar
label | 03b4a320-b280-5045-bd4e-b316424cbae9 |  | note | Method - V+M
label | 68b89544-6730-5ac4-9b8b-978be80ff9ad |  | note | Frequency - Once
label | 02bb7b70-97e2-534a-91b4-ff1ec24cfe25 |  | note | WP - AE Smith
label | ea7e6ae4-d8ce-5edf-b4a8-de7c6272de21 |  | note | HP - AE Smith / CPB / IR
label | a32cea25-ac72-5200-a83b-d4d35095ba57 |  | note | Records - Check Sheet + Photos
holdpoint |  |  | signoff | AE Smith / CPB / IR HP
checkpoint-status |  |  | checkpoint | 3.5 - Pressure released or reduced for next test
label | bf1f51e7-adc6-52ea-8f49-58dc533c1c0f |  | note | Resp. - SUP
label | d57dbb05-0293-5170-84b4-97ebc85e733b |  | note | Referenced Documentation -
label | a65f7e36-5021-5c9d-bff4-0db99b13befa |  | note | Conformance Criteria - Supervisor to ensure energy (pressure) is only stored while under test
label | 8bf25700-e15d-597f-a950-61298c87e67e |  | note | Method - V+M
label | 6d2280b6-f38c-5302-8096-4fc4f50591fc |  | note | Frequency - Once
label | b0f32a39-6163-5ae2-b63d-1d67aa723943 |  | note | WP - AE Smith
label | b7c9bde4-ee73-5dbd-b976-55ae99b77ac3 |  | note | Records - Check Sheet
checkpoint-group |  |  | section | 4.0 HYDROSTATIC TEST (STAGE TWO)
checkpoint-status |  |  | checkpoint | 4.1 - Ensure pressure is 7 bar for second stage of test
label | 5d708d81-da7b-5ade-8e75-28ce05c250ad |  | note | Resp. - SUP
label | 26843b87-3d08-5a38-8ef0-8d47d00a41d9 |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | 3f9992f8-3fbd-5575-9150-061c3bf295f8 |  | note | AS 4041:2006
label | 9cbba29e-509e-5da8-916b-1ea746f8adab |  | note | Conformance Criteria - Ensure system pressure has been reduced from previous test to 7 bar or Gradually raise to 7 bar
label | cd85c35d-dcdb-5d53-9b41-fc25ee4948c7 |  | note | Method - V+M
label | f9141b88-0b1b-599d-a1d2-2041d822468a |  | note | Frequency - Constantly Monitor
label | 7ee6823a-f710-5271-9941-7370117b820d |  | note | WP - AE Smith
label | ac722452-010a-51ef-8761-8b40790184f7 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | 4.2 - Hold 7 bar pressure for 24 hours (START WITNESSED)
label | 4594d04e-a6cd-586b-ac1a-41e3689d00db |  | note | Resp. - SUP
label | 85fe9aa3-147e-54e2-8821-1d711baaff7f |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | 478ea59e-81a5-552f-81e5-cac7da79c4ef |  | note | AS 4041:2006
label | a28e89b0-1452-5097-a237-456578551d32 |  | note | Conformance Criteria - Record START time & photograph gauge
label | 06b779f2-3cef-51b8-b0d6-ae10117a0f92 |  | note | All relevant parties to witness starting pressure of 7 bar
label | 962b97ee-4b9f-52e0-a0f6-953b51dd3042 |  | note | Method - V+M
label | 21477c11-1ab3-5706-8371-2e775da809c9 |  | note | Frequency - Once
label | 7edbbfe0-3815-50df-87f0-30f7949e3741 |  | note | WP - AE Smith
label | 0225d7b1-bc69-5476-9e96-0e0eed51a5f9 |  | note | HP - AE Smith / CPB / IR
label | 210213be-20e4-5344-9b00-b68a35110df3 |  | note | Records - Check Sheet + Photos
holdpoint |  |  | signoff | AE Smith / CPB / IR HP
checkpoint-status |  |  | checkpoint | 4.3 - Hold 7 bar pressure for 24 hours (FINISH WITNESSED)
label | 097ea108-7745-5a88-9a78-2c104924e12e |  | note | Resp. - SUP
label | 6d5f8547-ce40-54a4-b043-3bac197cc2f1 |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | 1e27c264-de09-5470-8a75-6d03cd4854b8 |  | note | AS 4041:2006
label | a1e95013-a1d2-568a-b6fb-231d2d92d8b3 |  | note | Conformance Criteria - Record FINISH time & photograph gauge
label | 80e7be97-909f-50e2-8424-f8a7ff92e806 |  | note | All relevant parties to witness starting pressure of 7 bar
label | 46bfe84c-0169-52cb-9037-a64390bdb6a0 |  | note | Method - V+M
label | d7caeaf0-a0ce-5597-8a82-5a078fbb41b1 |  | note | Frequency - Once
label | 49d4390d-e91a-5bfc-b6e1-b380299cf257 |  | note | WP - AE Smith
label | fdc958d7-ad2e-55ff-9c27-483af0d4eca8 |  | note | HP - AE Smith / CPB / IR
label | 253e59b3-6a9a-5f52-97c5-33bb5e440532 |  | note | Records - Check Sheet + Photos
holdpoint |  |  | signoff | AE Smith / CPB / IR HP
checkpoint-status |  |  | checkpoint | 4.4 - Discharge pressure leave system in a safe state
label | 2205f140-adef-591e-8f28-1c57c4a17dff |  | note | Resp. - SUP
label | 3effbc24-41ec-573f-893c-c9925a36f98e |  | note | Conformance Criteria - Discharge system pressure, ensure area is left in a safe state meeting site requirement
label | 52f4eb68-889a-505c-8cde-e71d2e684491 |  | note | Method - V+M
label | bcb53b27-eb39-5f0a-85af-7dc25328be1a |  | note | Frequency - Once
label | 97b93e35-c645-58a4-bbc0-0533bba95e43 |  | note | WP - AE Smith
label | e2873380-00ca-5dcc-a670-60802ffba1ac |  | note | Records - Check Sheet
checkpoint-group |  |  | section | 5.0 COMPLETION RECORDS
checkpoint-status |  |  | checkpoint | 12.1 - Testing Results
label | a004c4f2-70e8-533c-a8e7-c308002f263f |  | note | Resp. - SE SUP
label | a83dd325-b2f7-524d-9a69-8fb7ccb229b1 |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | 586c4cf5-3ab9-514b-8232-5c2012fd07e1 |  | note | AS 4041:2006
label | 803a3439-7540-5589-bf6c-83320d24b176 |  | note | Conformance Criteria - All pipework pressure test reports shall be provided
label | f8062733-1d7f-50a5-b0ac-b3251fa9b2b6 |  | note | Method - DR
label | 30e6220b-4575-5fe7-9db7-16d700cd68d2 |  | note | Frequency - Each lot
label | 9ab8994d-93a6-54ee-b033-79a812b844fc |  | note | WP - AE Smith
label | b480c72d-4a8b-561a-9a08-1f6c3518ec5e |  | note | HP - AE Smith / CPB / IR
label | f993d506-50dd-594c-8be5-45c630baf3e3 |  | note | Records - Check Sheet
holdpoint |  |  | signoff | AE Smith / CPB / IR HP
checklist-flat | 93007974-954d-45f7-a8ce-a5d51ebae12a |  | checklist | Combined Services HDPE Natural Gas Installation V3 |  |  |  |  | Yes | Combined Services HDPE Natural Gas Installation V3 | 6f88628a-3aa3-4b51-ba7d-adb8c5679307
checkpoint-status | 81d9d1c3-2ca4-4755-aed4-9dd51ccdcaa9 |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 0fb1a183-6dbd-482b-be42-c8e0a34072b3 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | 09f69685-fc69-4bc7-88c7-9198fe341b83 |  | checkpoint | Confirm trench depth, width and pipe alignment.
label | 825b3a50-18bf-57e0-97c4-987d3c605216 |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | b5aa1df9-51c8-5b16-aa17-a51bdc5279b9 |  | note | Excavation Checklist to be completed prior to installing services.
checkpoint-status | 909a3597-29fd-4927-8a6d-2ff7e662fdeb |  | checkpoint | Number of pipe dimensions shown on the drawings.
checkpoint-status | 99b2c206-aacd-45e1-9a8c-4efd37ea0974 |  | checkpoint | Location of pipes shall be shown on the drawings.
checkpoint-status | f8d40eab-e855-4581-a10a-3da602616382 |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
holdpoint | 847199ee-28f0-489d-b68f-a6b1ea2692f0 |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 9428b30e-e48b-4682-8abc-0cd2f6173d12 |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | 8a669313-2aef-4a04-9df8-66e7cc9d1a74 |  | checkpoint | Installation of Valves
label | 3003871f-c66e-5f8a-83f1-7d2b5155bc25 |  | note | Valves Installed as per approved drawings
label | cad845f9-dc68-557b-8a8a-22fee268b063 |  | note | All works have been completed by a registered gas fitter ?
holdpoint | 6e6e5452-7ee5-4ad6-829e-1e8ba0a7ff6f |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | f3317e12-269d-456a-80a4-13b64429f8bb |  | checkpoint | Pipework Pressure Test Report Completed ?
checkpoint-status | 81c263a5-653a-4ab6-b365-f864ce6ae265 |  | checkpoint | As-constructed survey
label | bd6d1095-6d27-5fc3-bb68-e67c7e640bbe |  | note | As-constructed survey must capture the horizontal and vertical locations of all newly constructed or relocated underground trenches and pipework.
checkpoint-status | b4dc20ec-aa59-47ce-a4f7-fc4261ad54b9 |  | checkpoint | As-Builts Completed.
holdpoint | 59d1e029-4656-4fa9-99ab-2651d60b62e9 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | b250d3f5-ae66-4014-bb4e-a32362b20d19 |  | checklist | AECOM Combined Services HDPE Domestic Cold Water Pipework Installation V2 |  |  |  |  | Yes | AECOM Combined Services HDPE Domestic Cold Water Pipework Installation V2 | 70628704-73d6-4a11-91aa-a5b015b276f8
checkpoint-status | d7bf4be1-99a0-4ff0-9b5e-48ad38c0634d |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | dd7e9a09-6b97-4f78-93f6-cee30133549d |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | e510e773-1b51-4181-ab73-cfd8b268cadd |  | checkpoint | Inspect trench depth, width and pipe alignment
label | b674d392-5e7c-5ca3-9202-ceaf3137ff8c |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | 0a151677-2db2-5b35-8db2-09ccf9bd2cab |  | note | QA documents to be provided prior to installing pipework in trenches . CPB to provide to AE Smith.
checkpoint-status | 763d1c15-ba11-4dd2-b87a-f438dd45e987 |  | checkpoint | Number of pipes and dimensions of pipes shall be shown on the drawing
checkpoint-status | 1de6bb3e-dad8-45e2-95ef-1ee9e254b51f |  | checkpoint | Location of pipes shall be shown on the drawing
checkpoint-status | fa064245-31c9-462c-86ea-ad4ec534b709 |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
holdpoint | 205b7165-e006-4b86-8db7-221d4e98981a |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 0b9799ea-f95d-400a-9d87-f3fac0f37a9a |  | checkpoint | Joining of pipework only to be done by Rotable steel flanges and EF Coupling.
checkpoint-status | 2ce115ee-1544-4a18-ac41-ee2fe9b236cc |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | cf3d1a8d-33cb-4033-a900-150f6a1c0482 |  | checkpoint | Install , valves , tees and bends
label | 0b3a6b15-268b-578a-9ff2-65381cf2bbbf |  | note | Connections are installed as per construction drawings ?
label | 3f4274cc-c568-5a08-a7b9-2514acc27342 |  | note | All valves 100mm and above have a 1050 manhole ?
checkpoint-status | c2b63369-e0e5-452f-a3b9-5826d7793c5f |  | checkpoint | Install Thrust and Anchor Blocks
label | 74530e5d-7e8b-5183-bfd2-9f93486db4f4 |  | note | Minimum dimensions as per IFC Drawing
label | 4865529d-49b1-539c-84b9-b4ba36f28be0 |  | note | A protective Denso or black coating membrane has been installed around the pipe and the concrete anchor / thrust block to prevent abrasive damage ?
holdpoint | 748c9329-41d6-4df7-9205-f19d1b70369d |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | fc0af7fb-dc33-461c-a7fd-6c7a4e2bd4e3 |  | checkpoint | Installation of Trace Wire
label | b1b06abf-d879-5ef3-8db7-66fbde7d5a60 |  | note | Install Tracer wire as per Specification 5.21 of the Hydraulic Services Specification and ensure tracer wire is continuous between valves and any excess coiled.
label | d6f51b12-5ac2-50d6-a801-9e4fee2251a2 |  | note | Test Trace Wire as per Specification 5.20.4
holdpoint | dcd029ed-a94a-464a-a536-00813d9e7bea |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 7dfb14f2-d548-46b2-962d-1bef45ae0ff1 |  | checkpoint | Completed Construction Pressure Testing with Air
checkpoint-status | beb04b19-a970-43bb-8faf-3c7bdccc5145 |  | checkpoint | Pre-Pipework Pressure Testing Inspection
label | fcabd6bc-61c9-500d-8683-708a7ea510fc |  | note | Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | b5897680-bcca-503c-a270-bf7fb10c0328 |  | note | Ensure all valves in the system are in the correct position and tagged �DO NOT OPEN� or �DO NOT CLOSE�
label | de2c1291-a448-5e48-9cf1-0492fe39d05e |  | note | All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing.
checkpoint-status | 14b85604-6deb-487b-a6bd-18bf2d78f64c |  | checkpoint | Introduction of Air to 300 kPa
label | 5d28d9e9-e916-59eb-98ef-7b672194a7b7 |  | note | Gradually introduce air into the system to a pressure of 300 kPa and hold for 1 hour.
label | 79c6ceba-e456-5097-abd3-9fd8698866d4 |  | note | Monitor for any drop-in pressure.
label | 9c6da1da-d2ff-5df1-bfcc-e85547f0e631 |  | note | If a leak is identified discharge the air prior to rectifying any leaks.
checkpoint-status | 47f60e36-11ad-48a7-bd62-12423df319a2 |  | checkpoint | Increasing Test Pressure
label | 866f542e-d67e-5f10-9ffb-c2c22ae77676 |  | note | If no leaks are identified Increase pressure by 10% increments until test pressure is achieved.
checkpoint-status | d7d1a254-ac11-41dc-8f2c-b0a2c907c820 |  | checkpoint | Pipework Pressure Test Report Completed
checkpoint-status | bf653005-f8af-4adb-a2dc-a68b083accca |  | checkpoint | As-Builts Completed.
holdpoint | 530f0406-82c3-4cd6-96b9-2928734ca105 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat |  |  | checklist | Cleaning Agent Removal |  |  |  |  | Yes | Flushing - Cleaning Agent Removal | 759932d8-e147-44ea-9415-566d434c7dc7
checkpoint-status |  |  | checkpoint | All sections' valves are opened.
text | daf231f4-7faf-5148-9405-b2582b1c0923 |  | textbox | Make-up valve is opened.
text | 56e67f72-752d-51ea-9ef8-25b90c6a9982 |  | textbox | Date
text | 6e379067-4b55-5305-9eea-fadf1642db65 |  | textbox | Main drain valve at the pump is open.
text | 461a8b11-0034-59ef-8b42-b64fd1324967 |  | textbox | Drain waterflow (l/s)
text | edd774a1-ea8b-54ba-819b-94f893b55fa4 |  | textbox | Drain location
text | 662ddb16-73d4-5444-b82f-20976b1a6b1b |  | textbox | Drain duration (minutes)
text | 73b58ad9-a1e5-5faf-b1c2-de934513145e |  | textbox | Calculated drain water volume (L)
text | 1ee54d61-d023-5122-b7c0-1fbc7afc7491 |  | textbox | Special trade waste water permit obtained.
checkpoint-status |  |  | checkpoint | Adequate make-up water available. System's static pressure is not decreasing.
checkpoint-status |  |  | checkpoint | Clean strainers as required. Upload dirt and clean strainer photos here.
checkpoint-status |  |  | checkpoint | Circulate and replace water until the water runs clear.
checkpoint-status |  |  | checkpoint | Water sample is taken, and labeled as "End of Cleaning" and dates.
text | f732980f-38f7-5f19-a4b0-c0d2783f9553 |  | textbox | Date
checkpoint-status |  |  | checkpoint | Sulphate
text | 736ef1c4-d5c1-523b-b963-eb692c113a78 |  | textbox | Site measurement
text | 64c0c47c-666b-541e-9c17-91e108f78215 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Chloride
text | cacac921-4812-51eb-bfba-b233fa8851a3 |  | textbox | Site measurement
text | 45726c7f-8aeb-53d1-9cc0-7b10c6ef3754 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | pH
text | e8cb8a63-9554-5988-a11b-1df206d551d9 |  | textbox | Site measurement
text | ef28236e-9180-5608-b225-29631ff6cd6b |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Conductivity
text | 557b6f4b-2b3f-5ed2-af54-71577aa3086b |  | textbox | Site measurement
text | c9f5161f-59d5-5afe-84f1-29218f125c91 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | a061317d-f849-5406-8f59-e324a2024dd5 |  | textbox | Site measurement
text | e7272bdf-1ae5-56bf-8452-3cfe66521ceb |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TVC (Total viable count: the total numbers of microorganisms, such as bacteria, yeast or mould species)
text | 36d8f2ee-a9ad-5ee2-bacb-0a7c69c0302c |  | textbox | Site measurement
text | 980cc1ba-1720-5117-a935-b1965e66ba16 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Pseudomonads (microorganism that can create biofilm)
text | 2ecdc3dd-1bbb-5732-84b3-e2e7649b91b1 |  | textbox | Site measurement
text | eb8c7330-99ab-5f84-908b-7229fbeaf9ac |  | textbox | Lab test results
checklist-flat |  |  | checklist | Passivisation |  |  |  |  | Yes | Flushing - Passivisation | 78eb78c6-f986-4151-a1d9-9fd340091ab5
checkpoint-status |  |  | checkpoint | Confirmed all terminals backward & forward flushed
checkpoint-status |  |  | checkpoint | Confirmed the system water quality is as close to the make-up water quality as possible.
checkpoint-status |  |  | checkpoint | Test make-up and system water to compare
checkpoint-status |  |  | checkpoint | pH
text | 9015b3ee-49bb-57cc-bb11-236eae330607 |  | textbox | Make-up Water
text | 2ec935e3-255a-543f-829e-6d9ecf267939 |  | textbox | System Water
checkpoint-status |  |  | checkpoint | Conductivity
text | cf9c6bd3-866a-5823-8271-e12361e046b8 |  | textbox | Make-up Water
text | c6fdbe0a-e2d5-5c84-b43e-d3eb2feb9da7 |  | textbox | System Water
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | 9634d41b-b1e8-5658-970e-91d097eed4d6 |  | textbox | Make-up Water
text | 170f3613-8fe6-5374-87b0-4a082aea92b1 |  | textbox | System Water
checkpoint-status |  |  | checkpoint | Inhibitor chemical(s) added.
text | 7a2c0e76-6a7a-5e83-9a13-4622bf12c682 |  | textbox | Enter Date & Time
text | 8ad3c87b-8306-5780-80e4-003e9efba452 |  | textbox | Name of chemical and SDS
text | 90059b62-2ef6-5b03-a84b-a09168f21bc9 |  | textbox | Name of chemical and SDS
checkpoint-status |  |  | checkpoint | Biocide chemical(s) added.
text | 21bcc1ed-83fa-568d-bbe5-7e2c6ef60e93 |  | textbox | Enter Date & Time
text | 7bf4e880-e518-506c-b490-3d8bd7a0efcc |  | textbox | Name of chemical and SDS
text | 3c22053b-2fb7-534a-98af-93de8b3a1f78 |  | textbox | Name of chemical and SDS
checkpoint-status |  |  | checkpoint | Circulate water 2 - 4 hours
select | eaa21601-450d-5d83-a948-5c1e9a0997df |  | dropdown | Is there any neutralisation chemical added as per chemical specialist advise? | Yes,No
text | b662c954-9960-54dc-bba2-724f46912cf0 |  | textbox | If Yes, enter name and quantiy
checkpoint-status |  |  | checkpoint | Test the water conditions at the completion of the circulation.
checkpoint-status |  |  | checkpoint | Water sample is taken, and labeled as "End of Flushing" and dates.
text | 52973bee-1973-5aa2-a730-4c9e72666a69 |  | textbox | Enter Date & Time
checkpoint-status |  |  | checkpoint | Sulphate
text | 41e5b02b-0578-5daa-8f6d-b0ffff96cc9c |  | textbox | Site measurement
text | 4b0274f2-9cb0-53a2-82e0-e46b84208ae7 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Chloride
text | e38846f7-9236-58ba-ba00-a9625d274a7a |  | textbox | Site measurement
text | e574bfa0-af43-5051-a146-29f32a699f1b |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | pH
text | 399264b2-0a5f-520e-ab97-fbcbbf1440af |  | textbox | Site measurement
text | ddb30371-437e-5156-9124-7be03eff08a6 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Conductivity
text | 0398f88f-0c8b-5344-8660-1f8f0521ed48 |  | textbox | Site measurement
text | bb47ccb2-89c8-5f4a-a71d-7c323b289981 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | 482a9d57-627b-5991-8348-6dba1db0287e |  | textbox | Site measurement
text | 9bcedf1f-fb4e-5eb8-9325-ba46ae185cb4 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TVC (Total viable count: the total numbers of microorganisms, such as bacteria, yeast or mould species)
text | 734e441d-d581-5b86-80e1-1db8add6601a |  | textbox | Site measurement
text | 0358fb07-19f9-523f-a938-7eb45c15d9dc |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Pseudomonads (microorganism that can create biofilm)
text | 0b49e7cf-4d6e-555b-9746-b4b05772eb46 |  | textbox | Site measurement
text | dfcee5d5-b006-5a09-b305-91902cf08fac |  | textbox | Lab test results
checklist-flat | 5e84437d-70fd-4c97-8ded-886705d6182d |  | checklist | Mechanical Services HHW and CHW Water Reticulation |  |  |  |  | Yes | Mechanical Services HHW and CHW Water Reticulation | 7cf706b0-95ed-4830-b2f2-5bfd644f5435
checkpoint-status | 037fb15b-7545-4ed5-b38a-b489084ff84e |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 022f9188-428d-48f8-ad63-73250c555d5b |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | ae72e5c6-ec24-4d46-9ddb-f4faaeb46a85 |  | checkpoint | Confirm trench depth, width and pipe alignment.
label | c25f20c8-ec2e-52b3-aeb6-513d360edc70 |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | b151d6d8-768f-54bd-bee8-2e530404fa3a |  | note | QA documents to be provided prior to installing pipework in trenches. CPB to provide to AE Smith.
checkpoint-status | 9f6cb27c-719b-4b63-a680-9a7ad397c23f |  | checkpoint | Heat Shrink Weld
checkpoint-status | 8fae5aab-4b4c-48f7-b7cc-48131b5f2fef |  | checkpoint | Number of pipe dimensions shown on the drawings.
checkpoint-status | 453a7a67-a625-44c3-8d6f-4a6fe2b938b9 |  | checkpoint | Location of pipes shall be shown on the drawings.
checkpoint-status | 432da7fa-4d1a-4f3d-ab0c-f5bee7747db5 |  | checkpoint | Welding of pipework
label | a663fd0e-27f8-566d-8397-efa1666feac4 |  | note | Joining of steel pipework to be welded as per approved Welding Procedure Specifications (WSP)
checkpoint-status | 2a2e6ed5-6bb1-43bb-b295-8be068cd6f63 |  | checkpoint | Installation of valves
label | 19971166-4a3c-5cc4-8f94-3e87c0f197e2 |  | note | Install valves as per construction drawings
label | 9d1190e9-4de2-5d2d-8caa-6d836bc91e1a |  | note | Lockable toby boxes installed for in-ground valves.
label | d063aec4-bc77-577b-a43a-f892864df3dc |  | note | Correct gaskets installed
label | 37e457a0-6db5-568d-a8d9-daaf607af52e |  | note | Flange bolts tightened in correct tightening sequence.
checkpoint-status | f4f09402-dddf-4f27-bfd2-33d1ad32d0d6 |  | checkpoint | Install Thrust and Anchor Blocks
label | d47e3c17-67a6-5a98-bcc5-d62d3b7913ff |  | note | Minimum dimensions as per IFC drawings.
label | 4ed2b514-fbd7-5e97-a114-e87227bf3050 |  | note | A protective Denso or black coating membrane is to be installed around the pipe and the concrete anchor/thrust blocks to prevent abrasive damage.
checkpoint-status | c4af72b7-c82e-4c22-a9ae-0573ce278049 |  | checkpoint | Installation of Expansion Loops
label | 10f76f8a-fab2-558d-8178-4360f4dbf503 |  | note | Expansion Loops installed as per IFC drawings.
label | aeaed531-b633-5357-b098-f092aec87680 |  | note | Correct dimensions for inner smaller loop as per IFC drawing.
checkpoint-status | 622bcb6f-97d2-44fd-b8f4-bacfca000a6b |  | checkpoint | Inspection of Insulation
label | 976e243b-9583-5cb3-a1eb-f9619036336a |  | note | Inspect insulation for damage
label | e167b5d7-dbe3-5c9e-9411-8687acdd0c2a |  | note | Confirm Insulation is 50mm as per IFC drawings.
checkpoint-status | 9e095f0b-ba89-4d03-9128-a98decdeacbe |  | checkpoint | Installation of Pipework Marking Tape.
label | 6a629d64-6d83-506a-9b1e-37c6d92b7cb7 |  | note | Flow and Return direction arrows installed on all pipework.
label | 75688fa1-c21c-5bc7-ae64-fff0f2a7009e |  | note | Install detector tape 200mm below existing ground level
checkpoint-status | 0b5602c7-4932-4c75-a097-597179637a73 |  | checkpoint | Protection of In-ground bolted flange connections.
label | 559bfa31-b46f-5728-b477-9d307ee6e3b3 |  | note | All in-ground bolted flange connections are to be cladded and foam filled.
checkpoint-status | 947255da-a542-4703-bb14-6fd7ce9a93f5 |  | checkpoint | Completed Construction Pressure Testing with Air at 750 kPa for 4 hours.
checkpoint-status | 9dfb0389-ca3f-41d3-9e23-531ed48f72fe |  | checkpoint | Pre-Pipework Pressure Testing Inspection
label | f2cd7b67-de1d-5396-8d83-bd20ff6b1991 |  | note | Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | 90bb3284-9e41-551a-8b2a-88825dad8c14 |  | note | Ensure each test length is capped and ball valve installed.
label | a46c0cbb-e3fa-56c9-9519-f826233ed6a3 |  | note | Ensure all valves in the system are in the correct position and tagged “DO NOT OPEN” or “DO NOT CLOSE”
label | 67719617-bf11-5890-a9c4-648c6e93d63b |  | note | All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing.
checkpoint-status | 97aa2d84-8517-4d52-b830-30b59bdfd448 |  | checkpoint | Introduction of Air to 300 kPa
label | 297b1b2f-8585-56ba-adf2-8114f20a21ce |  | note | Gradually introduce air into the system to a pressure of 300 kPa and hold for 1 hour.
label | cc4c8556-c9ba-5376-8af2-a7b28b6b7742 |  | note | Monitor for any drop-in pressure.
label | 092f719a-35e7-5b5c-a92a-6e2c721ed40f |  | note | If a leak is identified discharge the air prior to rectifying any leaks.
checkpoint-status | 9ccfaec6-99ef-4394-8171-f8f077009f11 |  | checkpoint | Increasing Test Pressure
label | 2aa63c59-44e2-596c-9f98-725044d652a7 |  | note | If no leaks are identified Increase pressure by 10% increments until test pressure is achieved. Test will begin when pressure reaches 750kPa
checkpoint-status | db77eabc-c134-4bc1-878d-f809bc6dd9ab |  | checkpoint | Pipework Pressure Test Report Completed
checkpoint-status | b7ae5824-0dee-424a-88a3-1c7dd9379ca2 |  | checkpoint | HDPE Jacketing
label | 74142863-9e3b-58ca-854d-93ff91c9f181 |  | note | In situ HDPE jacketing at pipe joints to be completed only after pressure testing is completed and the welds have been checked.
checkpoint-status | c04eac8d-029f-448e-89ec-e289470a8974 |  | checkpoint | As-Builts Completed.
holdpoint | da24fd63-2a6e-4a3a-8596-2024d0f305d5 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 280402e9-0cf3-421d-83a9-a5c1ef65eb7a |  | checklist | Combined Services HDPE Natural Gas Installation V2 |  |  |  |  | Yes | Combined Services HDPE Natural Gas Installation V2 | 8e1d7484-6efb-45c6-bced-9ea574003ae5
checkpoint-status | 5ccc71ca-afef-42c4-84fc-e5652c0c0f08 |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | e3801910-4468-435d-8875-51a676904d81 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | 5938c1be-7848-4b6a-bbef-2d50141ab746 |  | checkpoint | Confirm trench depth, width and pipe alignment.
label | 7ce130fe-dcc6-5d8c-946a-66734c5efcd9 |  | note | QA documents to be received from sub-contractor prior to installation of conduit in trench.
checkpoint-status | 8b897e5b-55ba-450c-8744-bd65348bf275 |  | checkpoint | Number of pipe dimensions shown on the drawings.
checkpoint-status | 25612ac6-ed5e-4a80-87c0-ae3aa0c69a06 |  | checkpoint | Location of pipes shall be shown on the drawings.
checkpoint-status | 42f8b78e-bba8-406b-bcb5-6f243a987534 |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
holdpoint | 542e0144-2661-4753-b07e-136fc26c9df6 |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 613c3028-b1d1-4067-b736-bb6a5201effc |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | a6b5cd37-0e79-424c-870a-5ca17db8d528 |  | checkpoint | Installation of Valves
label | 137e25a4-5153-5f0e-8eb6-41ff1d402454 |  | note | Valves Installed as per approved drawings
label | 9eb75998-efe2-5776-93b1-8dd127338e46 |  | note | All works have been completed by a registered gas fitter ?
holdpoint | 50aa917e-a657-4f19-b102-6866ecd21833 |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 1b7782c1-77b8-4894-94a6-36d9f31e0824 |  | checkpoint | Pipework Pressure Test Report Completed ?
checkpoint-status | 4d752403-1d7c-4b54-9e41-a0dccab6ce11 |  | checkpoint | As-Builts Completed.
holdpoint | 95bf28d5-0c49-4e4b-a95b-da1086faf027 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 7a5d6761-6022-48ab-bc58-643bd116f718 |  | checklist | Seismic Joint Building Connection |  |  |  |  | Yes | Seismic Joint Building Connection | 99f90d07-659f-4092-ae8a-73f7205fe565
checkpoint-status | 051b447e-9569-4ed7-85dc-5cb07aa62dc3 |  | checkpoint | Waterproofing
checkpoint-status | 8094a051-a210-4548-a9c0-0404aac2be84 |  | checkpoint | Insulation
checkpoint-status | b2eed668-0df7-4902-b2a3-56f89abd8a76 |  | checkpoint | Victaulic Coupler
checkpoint-status | c76eecf7-a159-4973-a332-d63ccca65c3a |  | checkpoint | Installed Correctly
holdpoint | 34241939-5483-43b5-bc23-11034c43aa30 |  | signoff | CPB signoff
checklist-sectioned |  |  | checklist | Communications Underground Fiber Micro Duct |  |  |  |  | Yes | Communications Underground Fiber Micro Duct | 9b4b7f65-d129-4870-8259-ac81eded35c9
checkpoint-group |  |  | section | Approval
checkpoint-status |  |  | checkpoint | RDM & Consent Approval received by the client and approved?
checkpoint-status |  |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-group |  |  | section | Location
checkpoint-status |  |  | checkpoint | As shown on the drawings
checkpoint-status |  |  | checkpoint | Instructed by CPB Rep. as to best suit the conditions on the Site at the time of construction
checkpoint-status |  |  | checkpoint | Confirm trench depth, width and micro duct alignment, QA documents to be received from sub-contractor prior to installation of conduit in trench
checkpoint-status |  |  | checkpoint | Bottom of the trench shall be compacted to form a firm uniform surface free from loose material.
checkpoint-status |  |  | checkpoint | Number of micro duct dimensions shall be shown on drawings.
checkpoint-status |  |  | checkpoint | Location of micro shall be shown on the drawings.
checkpoint-group |  |  | section | Bedding of Microduct
checkpoint-status |  |  | checkpoint | Duct shall be bedded on approved bedding material
checkpoint-status |  |  | checkpoint | Bedding material shall be 150mm above top of duct
checkpoint-status |  |  | checkpoint | White marker tape installed with the words
checkpoint-status |  |  | checkpoint | WARNING - Communications cable buried below laid in the trench 150mm below ground level.
checkpoint-status |  |  | checkpoint | As-built drawings completed
checklist-flat | b9105d1f-37c2-4236-8a70-70e4feb899b7 |  | checklist | AECOM Combined Services HDPE Domestic Cold Water Pipework Installation |  |  |  |  | Yes | AECOM Combined Services HDPE Domestic Cold Water Pipework Installation | a8dd93c2-9fa5-4ff0-929a-0f9801d67e39
checkpoint-status | e4e64b97-52cf-45bc-869e-c57ec8ed8771 |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 8b8d8a6b-74a4-4c28-b0b8-c4642fe3e978 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | 0fca93a8-84dc-4ec1-9fb1-2b50a1344bd7 |  | checkpoint | Inspect trench depth, width and pipe alignment
label | edb6e2ab-ad29-5a75-8148-30348da1c006 |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | 9f237b1b-16b0-5c9c-a9bf-2c67dee60fa3 |  | note | QA documents to be provided prior to installing pipework in trenches . CPB to provide to AE Smith.
checkpoint-status | 55c4b252-44cc-4bca-b1c7-1cea09dc6797 |  | checkpoint | Number of pipes and dimensions of pipes shall be shown on the drawing
checkpoint-status | 53478528-8355-4e59-81ac-5d32b6eebd62 |  | checkpoint | Location of pipes shall be shown on the drawing
checkpoint-status | cbf97e7f-17e1-4ca7-a775-d9b4a3c04d87 |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
checkpoint-status | fcf6181a-61c0-451b-9776-790567cbc483 |  | checkpoint | Joining of pipework only to be done by Rotable steel flanges and EF Coupling.
checkpoint-status | 7d421d9b-af0f-4380-8491-580abe44550e |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | b73c79e4-a1af-49fc-97e7-ebfed4925ad0 |  | checkpoint | Install , valves , tees and bends
label | 953a6533-c63d-5d81-ad26-5349ee70a3e3 |  | note | Connections are installed as per construction drawings ?
label | d277ee34-1275-5944-a96d-abbf6eb0609f |  | note | All valves 100mm and above have a 1050 manhole ?
checkpoint-status | 355775f1-5c02-4bc8-aa0b-519d14cbe3af |  | checkpoint | Install Thrust and Anchor Blocks
label | 52aef6fe-31a9-5cd7-9a6f-de54041e88d3 |  | note | Minimum dimensions as per IFC Drawing
label | 4e070d35-b635-5e8c-9ae8-7cfd4801b39f |  | note | A protective Denso or black coating membrane has been installed around the pipe and the concrete anchor / thrust block to prevent abrasive damage ?
checkpoint-status | 6360c5f7-541d-44d2-a082-e912bb31dbcb |  | checkpoint | Installation of Trace Wire
label | 135a1e63-0e25-58c0-8c2a-62fbba11412d |  | note | Install Tracer wire as per Specification 5.21 of the Hydraulic Services Specification and ensure tracer wire is continuous between valves and any excess coiled.
label | e768983c-da82-5038-82a5-75334ae81ff2 |  | note | Test Trace Wire as per Specification 5.20.4
checkpoint-status | fa9d7ce6-a539-4472-9b7f-8ebba00dafb7 |  | checkpoint | Completed Construction Pressure Testing with Air
checkpoint-status | 9bb315da-14cd-4d8d-a4e3-1149b37f515a |  | checkpoint | Pre-Pipework Pressure Testing Inspection
label | 5ccfc376-0079-5abb-9050-2063c1abe3af |  | note | Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | a82dfe3b-b17b-512f-a3c5-5bf67ef0ac53 |  | note | Ensure all valves in the system are in the correct position and tagged “DO NOT OPEN” or “DO NOT CLOSE”
label | 05ded2ac-d02d-563a-98a4-91fdc520b3b5 |  | note | All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing.
checkpoint-status | d51cde8d-f9a2-419b-b0ea-38fff916f20a |  | checkpoint | Introduction of Air to 300 kPa
label | 11da5df0-9bd1-5bbf-a09f-05d9f29e8b18 |  | note | Gradually introduce air into the system to a pressure of 300 kPa and hold for 1 hour.
label | 3b7a3c9f-7244-5232-8367-faf552e02b29 |  | note | Monitor for any drop-in pressure.
label | 4bb5bfa3-6b6b-56c3-928b-0ec794005189 |  | note | If a leak is identified discharge the air prior to rectifying any leaks.
checkpoint-status | b45e64dd-0a51-4fdf-b3e0-fbf7014271f0 |  | checkpoint | Increasing Test Pressure
label | d8157463-5d4c-553e-9c33-0622b9e56fff |  | note | If no leaks are identified Increase pressure by 10% increments until test pressure is achieved.
checkpoint-status | 56eaa2ce-7f14-42d1-a2c4-cc5b980d0fd2 |  | checkpoint | Pipework Pressure Test Report Completed
checkpoint-status | c195a4d7-c1cd-4f46-aae3-317f0aea54ed |  | checkpoint | As-Builts Completed.
holdpoint | 20dc41e7-669f-4440-84a0-74de6e6d4be2 |  | signoff | Request Signoff/ Raise Remedial
checklist-sectioned |  |  | checklist | Ductwork Leakage Test Certificate |  |  |  |  | Yes | Ductwork Leakage Test Certificate | b736f61b-1b40-42c2-8c76-903a9a5321f9
checkpoint-group |  |  | section | Part 1- Physical details
checkpoint-status |  |  | checkpoint | Physical details captured correctly
label | c95af755-cc38-5396-8aaa-12ca63dfc783 |  | note | The issue of this certificate is notification that this sytem has passed and ready for witnessing. Its is to be witnessed within 7 days following the test.
text | 5d020693-ab62-5478-868d-15de08c441a8 |  | textbox | Section of Ductwork Tested
text | 701dec88-9ec7-5724-9712-556fc6258e27 |  | textbox | Test Standard, Class & Pressurisation
text | 698f5e22-b1bd-5322-ad2b-7610fa7a4c21 |  | textbox | Test Static Pressure (Pa)
text | d545571d-0274-56c3-9cf7-3859199d3248 |  | textbox | Leakage Factor (l/s/m²)
text | 4d596cd4-5373-53db-b3d9-ec4efaae4fb2 |  | textbox | Surface area of duct under test (m²)
text | 6d36a571-b43d-53ac-932c-a837f6f62e6d |  | textbox | Maximum permitted leage (l/s)
checkpoint-group |  |  | section | Part 2 - Results
checkpoint-status |  |  | checkpoint | Part 2 Completed
text | fdb87a2f-633e-5f72-9636-70a466965f93 |  | textbox | Test Rig Details
text | 38f3d419-3b62-5210-a8c6-7fb60579a32f |  | textbox | Test Instrument Manufacturer / Model
text | d5977c1d-01df-5508-9446-f82370680a92 |  | textbox | Serial number / Calibration date
text | 75b2f916-c1a3-5774-8b8f-7000774b1f8a |  | textbox | Actual Duct Static Pressure (Pa)
text | c4b55c7c-88d6-583a-ac70-654f970edb65 |  | textbox | Actual Airflow Leakage Rate (l/s)
text | 04e42a95-145d-5201-a5c7-f0b0f445468e |  | textbox | Calculated Leakage rate per m2 (l/s/m²)
text | 29aa2958-d3de-567b-b87e-30b5d314522f |  | textbox | Duration of test ( Airflow reading taken at end of test duration )
text | 97745ebd-8cd2-5d2c-87f3-7b07a0f13688 |  | textbox | Test Outcome
checkpoint-group |  |  | section | Sign Off
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
checkpoint-status |  |  | checkpoint | Signed off By Witness
text | 2828bbc7-e437-504a-9810-320f616133a0 |  | textbox | Witness Name
checkpoint-status |  |  | checkpoint | Signed off by Consultant
text | 523942f7-068d-5f72-bc72-14c484d70b23 |  | textbox | Consultant Name
checkpoint-group |  |  | section | Photos
checkpoint-status |  |  | checkpoint | Start of Pressure test
checkpoint-status |  |  | checkpoint | Pressure test after recorded Duration
checkpoint-status |  |  | checkpoint | Photos Attached
checklist-sectioned |  |  | checklist | AES-NZ1005-STE-ITP-PMT-0012 - Natural Gas & LPG Gastight Air Pressure Test |  |  |  |  | Yes | AES-NZ1005-STE-ITP-PMT-0012 - Natural Gas & LPG Gastight Air Pressure Test | c5c46ab4-d1d9-47c4-a073-acae3381f04c
checkpoint-group |  |  | section | PRE-COMMENCEMENT CHECKS FOR NATURAL GAS GASTIGHT AIR PRESSURE TEST
checkpoint-status |  |  | checkpoint | Natural Gas Reticulation (AECOM Specifications – NZT5007-STE-HSSP-0001) - CPB Hold Point
label | bb086dd1-63f2-5dc3-9790-073a258d1958 |  | note | Resp. - SUP
label | 91c5ebc5-85fb-599b-897d-a6d5bae385f8 |  | note | Referenced Documentation - AES-NZ1005-STE-ITP-PMT-003
label | 9dbcb065-2a0d-56d7-8a50-2ff5fe3ca4fa |  | note | Conformance Criteria - Ensure Combined Services HDPE Natural Gas Pipework Installation Inspection and Testing Plan has been signed off prior to commencing Gastight Air Pressure Test.
label | fb3aea9e-595a-5442-82ad-535139198282 |  | note | Method - Document Review
label | b994eb2d-ceb8-54ec-982a-8bcc42cb7ff5 |  | note | Frequency - Before each Test
label | 46febd96-4a67-54b5-ac11-6907117ec7db |  | note | Hold Point - CPB
label | 55e6478b-d769-5055-b67f-91e8648918e1 |  | note | Records - Signed off ITP
checkpoint-status |  |  | checkpoint | General - CPB Hold Point
label | d29bb16a-3172-511b-9950-fc9115595ffb |  | note | Resp. - SE
label | 91875f99-f1b3-5f74-a29a-ce58f17487d9 |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001 REV 4
label | 3bcf2298-6ddb-5aa1-ada1-1acd324fed00 |  | note | Conformance Criteria - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
label | 105790d4-5bc6-50c0-aecc-f12786249afc |  | note | • Specifications & QA Documents Approved
label | 4965c60d-c90f-5b5f-b536-a7921431a182 |  | note | • Drawings are confirmed
label | 7df03538-7b00-55cb-ad0c-664cf4bd91a5 |  | note | • Equipment fit for purpose
label | 0b0d73ac-714b-5951-a472-8969449c6a63 |  | note | Method - DR
label | 5a2d9a50-b913-5a23-94ec-d7552abe40b7 |  | note | Frequency - Each material
label | c7bcbe54-62b2-5ca1-8ac5-342d100b152f |  | note | Hold Point - CPB
label | 54109d9a-4771-5708-a524-d18bb40907d2 |  | note | Records - Aconex approval
label | 802ce0b5-a734-5c8b-ae33-b72f1d1fa1d6 |  | note | • Incoming Inspection Checklists
label | 869a6bdd-f9f1-5814-9483-8d273ceee1b8 |  | note | • Drawing Register
checkpoint-group |  |  | section | NATURAL GAS GASTIGHT AIR PRESSURE TEST – AS/NZ5601 Appendix E.4 Pipework Test Procedure
checkpoint-status |  |  | checkpoint | Natural Gas Gastight Air Pressure Test - CPB/AECOM/IR Hold Point
label | f60c41a1-8901-5218-b9b4-c07292c67e19 |  | note | Resp. - SUP
label | 92e10b39-ca80-5097-9b61-3b2812f9c1f2 |  | note | Referenced Documentation - AE Smith – Waikeria Prison Development Pressure Testing Procedure V1 Appendix D Schedule 11 WCT62
label | 7a6668da-cab1-559f-acb5-4c7af3a47838 |  | note | Conformance Criteria - 1. SYSTEM IS DISCONNECTED AT THE METER OR THE CYLINDER.
label | 5dc2cc80-ce83-5d02-a41b-fd9efdc27ada |  | note | 2. ALL OPEN-END CAPS ARE CAPPED OR PLUGGED?
label | 0d966dbf-e4ea-5a36-97a6-79009fc5f4e2 |  | note | 3. ALL GAS APPLIANCES ARE ISOLATED?
label | b72696c2-1307-5f00-a9a7-9afa789d1227 |  | note | 4. SUITABLE TESTING INSTRUMENT CONNECTED. SERIAL No…………………….
label | d0df873e-e8fa-5820-bef9-2c64eceffdb1 |  | note | 5. RAISE PRESSURE TO 1.5 TIMES THE OPERATING PRESSURE
label | 342bc97d-31e8-52d2-9678-4cb161bea244 |  | note | • Section 1 – NG – Area 23 to UT1 @ 210kPa =315kPa
label | f2f0f502-77d3-579d-9ec8-dcce4c6c4e51 |  | note | • Section 2 -NG- UT1 to FM1 @ 70kPa= 105 kPa
label | f6a50220-b8d8-5a81-8b4f-18f80372b5db |  | note | • Section 3 - NG- UT1 to FM3 , IND & SPO - @ 70kPa = 105 kPa
label | e087e8dd-d789-557a-a97b-50f5842af512 |  | note | • Section 4 LPG - FM1 TO LAU @ 70kPa= 105kPa
label | 7369b875-565c-50d3-ba7a-185852ace789 |  | note | 6. ISOLATE PRESSURE SOURCE AND ALLOW 2 MINUTES FOR THE TEMPERATURE OF THE TESTING MEDUIM TO STABILISE.
label | 5f282f4a-0ba3-5753-83de-67d92ff6b12e |  | note | 7. RECORD TEST START TIME AND GAUGE READING AND PHOTOGRAPH FOR:
label | 9dc45ff9-a0ad-58f4-b9d7-cda90416d4ee |  | note | • Section 1
label | c00b5e96-8859-5b72-9d43-4a170fd63d72 |  | note | • Section 2
label | eb8a76e3-632d-537e-a48b-1ee5e9b4f313 |  | note | • Section 3
label | 91607518-7e02-5e3b-94b9-645d81e5b99b |  | note | • Section 4
label | 0e02b964-3ad2-5040-816c-e3f073b68bc5 |  | note | 8. TEST DURATIONS AND TEST PRESSUREs
label | 71fda93f-fbe7-50fd-b5d0-e41a5809fca6 |  | note | • Section 1 – NG – Area 23 to UT1 - 50.52 HOURS at 315 kPa
label | a493b2b8-84cb-5084-95d2-18a46186accd |  | note | • Section 2 - NG - UT1 to FM1: 1.13 HOURS at 105 kPa
label | 998997f8-7b2d-539c-8630-48396db02a3e |  | note | • Section 3 - NG - UT1 to FM3: 15.27 HOURS at 105 kPa
label | 710e1619-306b-5374-b416-8d60a83761b5 |  | note | • Section 4 LPG FM1 to LAU: 10 hours at 105 kPa
label | d1383509-a43a-5a99-a0ec-3f6e67e353e5 |  | note | 9. RECORD TEST END TIME AND GAUGE READING AND PHOTOGRAPH FOR
label | 68c98005-2ada-5972-986d-6a7681fefe0e |  | note | • Section 1
label | 0def0c17-e99f-54df-9bca-cb3fd3a3e549 |  | note | • Section 2
label | 73cc56e0-d478-53f7-8eeb-2b0fb360cdd9 |  | note | • Section 3
label | 11ace230-b81d-5fb6-8a35-c3ca1bc46491 |  | note | • Section 4
label | 5b8a4193-ddf5-5f9f-9f0e-5a756670be02 |  | note | 10. CALCULATE ADJUSTED TEST END PRESSURE. AND ANY PRESSURE LOSS
label | 541acc1a-6f9e-5b76-a14a-c790086099de |  | note | • Section 1
label | 61fc89b6-6574-5ad9-a244-4a428c8f2ef9 |  | note | • Section 2
label | 76e948bc-9c74-5fd3-9427-bf69d09fd5f5 |  | note | • Section 3
label | 0005c4b7-2421-5e2a-8853-d9edf57c9e0b |  | note | • Section 4
label | aa0b5d45-d78f-5a74-b9da-4cc87a533c12 |  | note | IF NO PRESSURE LOSS DURING THE PERIOD THE PIPEWORK CAN BE CONSIDERED GASTIGHT.
label | 752c6307-923f-5d6a-b1b2-7f4463943eef |  | note | 11. RECORD PASS/FAIL
label | 7912a8cc-c2b5-5f21-aabd-0a94712caa23 |  | note | • Section 1
label | d1bf79b2-34bb-5357-b16d-7d3cabf73771 |  | note | • Section 2
label | d6c72a4b-2fce-5d69-8861-a0b194e03466 |  | note | • Section 3
label | 8782ccc0-bcad-59d7-97cd-ca0e683a3557 |  | note | • Section 4
label | c2ae0dbc-f2ae-53cc-af33-2ca5a03f874c |  | note | 12. WCT 62 (a)(i)(H) IR to witness gas start test pressure.
label | 54e65fe9-dba6-50f0-80db-101e99da5df2 |  | note | 13. WCT 62 (a)(i)(H) IR to witness gas end test pressure.
label | 3c96c333-fc86-5d88-9ec9-d8c0a0bba336 |  | note | Method - DR
label | 83a77787-0202-5f54-bf5f-d71dda30c0db |  | note | Frequency - Before each test
label | 2fd828b7-e806-5598-8e46-dab367bc2cc1 |  | note | Hold Point - CPB/AECOM/IR
label | 22fb9335-0d51-5d2d-8cdb-6f44df7b3fad |  | note | Records - Gastight Air Pressure Test Report / CONQA
checkpoint-group |  |  | section | COMPLETION RECORDS
checkpoint-status |  |  | checkpoint | Test results - CPB/AECOM/IR Hold Point
label | 9784c747-b142-59d5-a750-ab804ab2f56b |  | note | Resp. - SE
label | 9b40653c-41c9-5c7e-92e1-d00bf18ac63d |  | note | Referenced Documentation - AE Smith – Waikeria Prison Development Pressure Testing Procedure V1 Schedule 11 WCT 62
label | c4980601-258d-5bd9-9ed7-b308117539cd |  | note | Conformance Criteria - WCT 62 (a)(iii)
label | 28add46d-22a4-5c77-ac76-4dc9bc5ef87f |  | note | • All pipework pressure test reports shall be provided to the Independent reviewer.
label | c2f13037-93f0-5e2c-b5bd-129408ff0dcd |  | note | Method - DR
label | eac30d74-353f-5237-af08-67a909ba327a |  | note | Frequency - Witness
label | f2fc641c-02a6-54bb-acb8-3b71993f5fff |  | note | Hold Point - CPB/AECOM/IR
label | 944f48be-7009-55ff-bf47-b73d8eafbf83 |  | note | Records - FTR Gastight Air Pressure Test Report
checkpoint-status |  |  | checkpoint | Gas Certificate of compliance - CPB/AECOM/IR Hold Point
label | f9681af3-f5e7-508b-aa52-6cd15bd041c5 |  | note | Resp. - SE
label | ff639672-5cf4-5a45-ac99-51926e203371 |  | note | Referenced Documentation - Schedule 11 WCT 62
label | 4f0f6215-d9a1-53d3-8e93-bc96df63419f |  | note | Conformance Criteria - WCT 62 (c)
label | 425a2c60-4d35-5252-acb9-05d0d1edd794 |  | note | • GAS COC shall be provided to the Independent reviewer
label | 9575a0ed-3618-5584-800f-c362b531a104 |  | note | Method - DR
label | 43a92095-86d9-5edf-9408-d8241cea7a41 |  | note | Frequency - Receive and review
label | 41038836-187b-5553-bb13-8a104e06c655 |  | note | Hold Point - CPB/AECOM/IR
label | 09d8d37c-14db-5a57-86ff-2127bfb6f641 |  | note | Records - GAS COC
checklist-flat |  |  | checklist | Flushing Preparation Checklist |  |  |  |  | Yes | Flushing - Flushing Preparation Checklist | d209a62f-4c72-431d-94a9-dbfe367d2598
checkpoint-status |  |  | checkpoint | Differential pressure manometer
text | 9c8f765a-8c56-5430-814f-e7829c40f7ec |  | textbox | Model Number
text | 37abac2c-3bad-5887-b1ad-72348facb843 |  | textbox | Serial Number
checkpoint-status |  |  | checkpoint | HydROtwist Portable Digital PH Test Meter
checkpoint-status |  |  | checkpoint | HM Digital Hand Held TDS Temperature Water Test Meter TDS-3
checkpoint-status |  |  | checkpoint | Hm Digital Hand Held Conductivity & Temperature Meter EC-3
checkpoint-status |  |  | checkpoint | 0-14 pH test strips
checkpoint-status |  |  | checkpoint | High level 200 ppm chlorine test strips
checkpoint-status |  |  | checkpoint | Low level 4 ppm chlorine test strips
select | 768cfa8a-a7ff-5f4f-a986-3301f5d356fd |  | dropdown | Flushing pump | Temporary pump,system pump
checkpoint-status |  |  | checkpoint | Pump is available to run under VSD control.
checkpoint-status |  |  | checkpoint | Pump is wired and ready to be turned on.
checkpoint-status |  |  | checkpoint | Strainer basket(s) is installed with commissioning mesh. / skimmers socks installed.
checkpoint-status |  |  | checkpoint | Skimmers sock is installed on the strainers.
checkpoint-status |  |  | checkpoint | Schematic and layout drawings are available and studied.
checkpoint-status |  |  | checkpoint | Isolation valves are installed at each terminal.
checkpoint-status |  |  | checkpoint | Balancing valve is installed at each terminal.
checkpoint-status |  |  | checkpoint | Balancing valves are used to measure waterflows
select | ff27bd34-3774-55a2-b4c2-cd7427cee4e6 |  | dropdown | Any additional method to measure /confirm flushing waterflows. (flushing velocities) | Pump curve,Ultrasonic flow meter,Main Branch valve
checkpoint-status |  |  | checkpoint | Chemicals available on site as detailed in the
checkpoint-status |  |  | checkpoint | Piping system has been pressure tested and passed.
checkpoint-status |  |  | checkpoint | System has been installed as per drawing and schematic. If not mark-up the drawing and upload here.
checkpoint-status |  |  | checkpoint | All high points have air vents installed
checkpoint-status |  |  | checkpoint | All low points have drain cocks installed.
checkpoint-status |  |  | checkpoint | Mains water / make-up water supply pipe is connected at the suction side of the pump downstream of the drain port.
checkpoint-status |  |  | checkpoint | Mains water pipe connection size is 40 mm or bigger.
checkpoint-status |  |  | checkpoint | Mains water pressure is minimum 1.3 Bar at flow.
checkpoint-status |  |  | checkpoint | A backflow prevention valve (check valve) is installed at the mains water supply valve and it is certified.
checkpoint-status |  |  | checkpoint | A local drain is available in the vicinity of the flushing pump.
checkpoint-status |  |  | checkpoint | The drain pipe minimum 40 mm size is connected upstream of the strainer.
checkpoint-status |  |  | checkpoint | A high volume of contaminated water is to be discharged to the sewer drain. A discharge consent is not required and the discharge limits are recorded below in the note sections.
checkpoint-status |  |  | checkpoint | A special council discharge (trade waste water) consent is required and obtained. A copy of permit is attached. The discharge limits are recorded below in the note section.
checkpoint-status |  |  | checkpoint | Sensitive equipment as listed below are isolated (by-passes), and not included in the dynamic and chemical flushing processes.
checkpoint-status |  |  | checkpoint | Coils
checkpoint-status |  |  | checkpoint | Control valves
checkpoint-status |  |  | checkpoint | Heat exchangers
checkpoint-status |  |  | checkpoint | Condensers
checkpoint-status |  |  | checkpoint | Evaporators
checkpoint-status |  |  | checkpoint | Cartridges from any auto-flow control valves
checkpoint-status |  |  | checkpoint | 15 L dosing pot is installed and connected
label | 4e8f86a4-55c4-55ff-b5c6-2afa818aa6e0 |  | note | BSRIA BG 29/2012 recommends make up water quality as below. Label the sample bottle as "Make-up water sample" and date it.
checkpoint-status |  |  | checkpoint | Sulphate
label | f9856671-45e5-5462-b582-5caee790f42e |  | note | Recommended: <250 mg/L
text | 69b4174c-befd-5940-8019-308d83847828 |  | textbox | Site measurement
text | cb99fd52-3e5d-5288-ba61-d8ff19f2b1b1 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Chloride
label | df90db93-8f87-5841-8587-d1cb3e21905a |  | note | Recommended: <250 mg/L
text | f8a12740-9eff-5169-9d7a-44db691dd9c0 |  | textbox | Site measurement
text | b3a772b5-a38c-52c0-a358-6485c4e33f93 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | pH
label | 528d9963-812a-5b77-a118-7ce0948c70b0 |  | note | Recommended: 6.0 < x < 8.5
text | 3a479036-efb3-5459-b98e-4af7e2f6cc18 |  | textbox | Site measurement
text | bd3d4034-25a3-503a-9956-88cca4278c10 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Conductivity
text | 73e23c30-1960-541e-bc52-b17c8747bb54 |  | textbox | Site measurement
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | d56a3d80-f1e0-57af-b32c-96b23e1659b9 |  | textbox | Site measurement
checkpoint-status |  |  | checkpoint | TVC (Total viable count: the total numbers of microorganisms, such as bacteria, yeast or mould species)
label | b04808f0-882c-59d3-8509-01d5075d0a8f |  | note | Recommended: <10000 per ml
text | f5c0f427-028b-5c15-b279-7c04babe5654 |  | textbox | Site measurement
text | 30d7e6f3-32f1-5abf-b84d-674c565d51cb |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Pseudomonads (microorganism that can create biofilm)
label | e180c9f5-9f5a-565f-9df5-2686d149e6b7 |  | note | Recommended: <10 per ml
text | 4b8444ad-923f-570f-a58b-0321532a6322 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | System filled with make-up water
checkpoint-status |  |  | checkpoint | Date
checkpoint-status |  |  | checkpoint | Make-up water connection location
checkpoint-status |  |  | checkpoint | Mains water pressure (kPa)
checkpoint-status |  |  | checkpoint | Water drained from furthest terminal until clear water is visible.
text | 69a66e97-1352-5bd1-bc72-dbd5a6e80ef5 |  | textbox | Drain waterflow (l/s)
text | 7d2bddd2-2b77-5196-be0e-e279a30b019c |  | textbox | Drain location
text | 8dbef6a8-2f8a-54c3-a848-c8c1a3d44d0c |  | textbox | Drain duration (minutes)
text | d30131dc-095f-5061-a74f-e281c3374d55 |  | textbox | Calculated drain water volume (L)
checkpoint-status |  |  | checkpoint | Special trade waste water permit obtained.
checkpoint-status |  |  | checkpoint | Water drained from all other location same as above
checkpoint-status |  |  | checkpoint | Air vent from all high points.
checklist-flat |  |  | checklist | Chemical Flushing Checklist |  |  |  |  | Yes | Flushing - Chemical Flushing Checklist | db610477-7cd1-4b8f-aac4-c233de373004
checkpoint-status |  |  | checkpoint | Uploaded highlighted drawing.
text | d8057836-2670-505f-8dbc-0e210d3da21c |  | textbox | List the zones / terminals / branches flushed during this step.
checkpoint-status |  |  | checkpoint | Confirm all other terminals isolated
checkpoint-status |  |  | checkpoint | Test the water conditions prior adding chemical
checkpoint-status |  |  | checkpoint | pH
text | 1291fd88-4b0c-5216-9cfb-da2bcd3e1d5b |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Conductivity
text | 553c851b-9f54-5c5a-b7ec-5f4b1e14f43f |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | 73397227-eb48-5f6a-b09a-f0ce4e04e37c |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Chloride
text | b3230d25-d131-57fe-b696-0d7298a2b9b9 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Pump is operating at 50 Hz.
checkpoint-status |  |  | checkpoint | Required cleaning chemical (L)
text | 10cee463-0fe7-5558-b3a1-f5ad68c1d257 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Cleaning chemical(s) added.
checkpoint-status |  |  | checkpoint | Name of chemical and SDS
text | deb5eafd-14d4-540e-8466-f9575f18e7fc |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Name of chemical and SDS
text | d4a93df9-11e5-5ee9-a48d-9a1af64cc92c |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Name of chemical and SDS
text | 75fe36a3-2301-5b1d-a519-61e760904595 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Circulate water 2 - 4 hours
checkpoint-status |  |  | checkpoint | Test the water conditions at the completion of the circulation.
checkpoint-status |  |  | checkpoint | pH
text | e56fe2e1-1097-500f-9f3c-8f829d8f6ff7 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Conductivity
text | b50191df-08ff-58cd-a929-e60f36574b2d |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | c14ba298-9b3f-5b92-ac21-ca7c8d8cfc6b |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Chloride
checkpoint-status |  |  | checkpoint | Photo of water sample at the end of the circulation before draining water.
checkpoint-status |  |  | checkpoint | Is there any neutralisation chemical added as per chemical specialist advise? If yes enter name and quantity
checkpoint-status |  |  | checkpoint | Record total and terminal waterflows on the "Flushing Water Flows" test sheet and upload here.
checkpoint-status |  |  | checkpoint | Clean strainers as required. Upload dirt and clean strainer photos here.
checkpoint-status |  |  | checkpoint | If this is last section to be flushed, then continue draining process.
checklist-flat |  |  | checklist | B5B - Line Valve Assemblies – Closure and Zoning Tests |  |  |  |  | Yes | B5B - Line Valve Assemblies – Closure and Zoning Tests | de6797db-b8b9-4930-af6e-8fdf943f800f
checkpoint-status |  |  | checkpoint | B5B - Line Valve Assemblies – Closure and Zoning Tests complete
text | 0b865fd8-807a-56fd-9c7d-9df1383f1a6d |  | textbox | Plant ref
text | 50591040-1290-5110-bc76-31a6cbb5f171 |  | textbox | Test by
text | bdd49dc8-7b4e-5665-905f-488027441404 |  | textbox | Test date
text | 72edb006-aad7-5b69-b6f4-4fed24ba72a6 |  | textbox | Revision
checkpoint-status |  |  | checkpoint | This is to certify that CLOSURE and ZONING of the LVAs was tested in accordance with paragraphs 15.63–15.65 on the pipeline system as follows:
text | 13613164-7825-573b-9290-2a2e1e24bf55 |  | textbox | LVA number
text | 42e6b72a-79db-5b0f-8c75-c44b259f68c3 |  | textbox | Test pressure (kPa)
text | 2bbf2656-8ffc-5975-b49a-dedf6a36d5e0 |  | textbox | Downstream/upstream pressure change after 15 min (kPa)
text | 74c5fe4f-4ad7-5626-999a-a29ee802107b |  | textbox | Terminal units controlled (total no)
text | ae79a404-c3c0-5e33-8051-77c18dcff3b6 |  | textbox | Terminal unit labelling
text | f261024d-2894-5679-a44f-ac73fba94266 |  | textbox | Contractors representative:
checkpoint-status |  |  | checkpoint | Sign Off Complete
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
checkpoint-status |  |  | checkpoint | Signed off By Witness
text | 480b0d8a-bfc8-511c-b940-e63fc17b41f4 |  | textbox | Witness Name
checkpoint-status |  |  | checkpoint | Signed off by Consultant
text | 4646063c-f8c9-5817-9f04-76aeb98e8073 |  | textbox | Consultant Name
checklist-sectioned |  |  | checklist | Combined Services - Heating Hot Water and Chilled Water Pipework Hydrostatic Pressure Test |  |  |  |  | Yes | Combined Services - Heating Hot Water and Chilled Water Pipework Hydrostatic Pressure Test | dedbefcb-af6f-4179-b62f-093e5a81a285
checkpoint-group |  |  | section | Details
checkpoint-no-status |  |  | checkpoint | Reference Documentation:
label | 22a27c7d-17cc-527f-9eaf-0fa66f268745 |  | note | Medium duty black steel to AS 1074
label | 35f9c70a-06c7-59a7-b138-29c8409e515b |  | note | Welded: To ANSI/API Spec 5L grade B.
label | e2ebbb2e-7220-5f46-820c-34879c6316c8 |  | note | Seamless: To ANSI/API Spec 5L grade B or ASTM A106 grade B.
label | 0e5e2b85-1d1f-5f74-8dbe-c72df6c4c605 |  | note | Standard: To AS 4041.
checkpoint-no-status |  |  | checkpoint | Project Specifications:
label | 063bed06-b857-5556-81ff-32213bfb4ef3 |  | note | NZT5007-STE-MSSP-0001
checkpoint-no-status |  |  | checkpoint | Drawings:
label | 27102b56-a06c-5d91-9c2a-fa63f81dca9e |  | note | AES-NZ1005-STE-SHD-MEC-1101-in sequence up to- AES-NZ1005-STE-SHD-MEC-1142
checkpoint-status |  |  | checkpoint | Prepared by:
text | 1d3fe4cc-4a1c-5da0-bfd9-bb100f262feb |  | textbox | Name:
text | 034c38fb-2e78-5c27-8f88-cf4224f53fc8 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Reviewed by: CPB Engineer
text | 021acdc9-f9f7-5bd4-8afc-2bafde4d25f9 |  | textbox | Name:
text | 0964ba3a-8680-59fb-841e-d00d9032d395 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Reviewed by: CPB QA Rep
text | ade30544-5833-5bcf-820e-b72f01b89e23 |  | textbox | Name:
text | d38332ae-c892-56bf-9dc8-70d50bda1bc8 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Reviewed by: CPB Completions Rep
text | 2c16a104-3c5c-5036-8463-f5b1c01d5ae9 |  | textbox | Name:
text | 36b56dfd-6a9e-5d60-8297-f90ab44c520a |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Reviewed by: Consultant (If applicable. N/A for Architects)
text | af3f5244-fc2d-51cf-bcfe-84221d69588a |  | textbox | Name:
text | fccf2193-5360-5055-962f-397742c10880 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Approved by: CPB SPE or higher
text | e3125728-8285-5af9-bfa1-090134ca12fa |  | textbox | Name:
text | 87c6c70a-e701-5b10-bff5-745f566b2adc |  | textbox | Date:
checkpoint-group |  |  | section | Preliminary Inspections and Tests
checkpoint-status |  |  | checkpoint | 1 - RDM & Consent Approval
label | 7bb975b5-8046-5eda-837e-e35e74c83193 |  | note | Responsibility - CPB
label | 2d8bdab6-17c7-5d42-811b-721b44101c81 |  | note | Specification Reference - RDM Tracker Consent Tracker
label | 9a62a6b2-44d4-554f-90d7-eb16b8a0e6a9 |  | note | Conformance Criteria - RDM approval tracker
label | e49db500-6631-5788-99bb-9f77c8a28ad5 |  | note | Consent approval tracker
label | 3639f811-dde8-5cee-969d-7e806f94ede4 |  | note | Method - Document Review
label | 9732e7c0-e266-5275-aae9-7130ab83189c |  | note | Frequency - By Building/Area
label | 49a3c978-a83d-5579-9250-0009c7523a40 |  | note | CPB - HP
label | 621ff52b-d925-542f-a063-f72d815281f8 |  | note | Records - Receipt of Approval by Client
holdpoint |  |  | signoff | CPB - HP
checkpoint-status |  |  | checkpoint | 2 - Define LOT Area
label | 7da66f88-28fd-5c15-83ba-ea18f441d493 |  | note | Specification Reference - IFC Drawings
label | a920cd7d-8ecc-5c24-befe-ada00dfe8ce3 |  | note | Conformance Criteria - Lot areas clearly defined
label | 407aaf4d-9eaf-58d8-bad8-beef069b43df |  | note | Records - LOT Map / Register
checkpoint-group |  |  | section | Quality Control Checklists
checkpoint-status |  |  | checkpoint | QUALITY CONTROL CHECKLIST – ATTACH ALL CHECKLIST TEMPLATES USED FOR THIS ITP
label | f69f4d90-37c6-57d8-af39-0dc01f8eba0d |  | note | *NAME OF CHECKLIST MUST BE INCLUDED ON ITP PART 1 LAST COLUMN (RECORDS OR CHECKLIST REFERENCE)
checkpoint-group |  |  | section | Lot Verification Checklist
checkpoint-status |  |  | checkpoint | Lot Verification
text | ed032731-6e17-50d2-a234-7742c29f7729 |  | textbox | Lot Number:
text | 4549b2fb-43a6-5cbf-aef3-08f0447a429e |  | textbox | Lot Description:
label | 2c15c791-de33-5b11-a03f-d6f466dc8158 |  | note | Note: Item / # records to be filled out by CPB Engineer - minimum is to match ITP, extra documents can be added
checkpoint-status |  |  | checkpoint | 1.0 - ITP / Quality Control Checklists
text | ca6e65b3-7c6d-5cc7-a967-5fb6e270f413 |  | textbox | Item
text | 9ecb1ad4-878f-5770-b3c1-75cc8693851f |  | textbox | Number of Records Required
text | da0ac52d-3110-5d91-90e9-3530b0ad1285 |  | textbox | LOT Subfolder No:
text | fb0326ce-10b0-5157-a970-bbb4af1794a3 |  | textbox | Remarks (initial / date)
checkpoint-status |  |  | checkpoint | 1.1 - ITP / Quality Control Checklists
text | bac63303-cc11-5bc0-b244-88ce8ce34827 |  | textbox | Item
text | 48b58649-2852-54cb-9f34-1123e37a5aeb |  | textbox | Number of Records Required
text | 54f289fe-8d23-5bf5-9702-5653de29904c |  | textbox | LOT Subfolder No:
text | 57ff40db-784a-549e-80c2-d8e8b4161402 |  | textbox | Remarks (initial / date)
checkpoint-status |  |  | checkpoint | 2.0 - Survey Results
text | 6bd40811-0129-5d93-b3fc-d2762addb505 |  | textbox | Item
text | f7d18893-8e29-5ae7-a064-a83fc418682e |  | textbox | Number of Records Required
text | 02b5bdaf-c7e6-50ed-9d81-cbae78113312 |  | textbox | LOT Subfolder No:
text | 5c165c1f-2bce-5264-b5b1-078caa919241 |  | textbox | Remarks (initial / date)
checkpoint-status |  |  | checkpoint | 2.1 - Survey Results
text | bbf0f8b7-1277-5b9d-8150-74bc2c259c65 |  | textbox | Item
text | 36178a5a-d0e2-55ee-94ed-56b15ea3668c |  | textbox | Number of Records Required
text | bdc733b4-3de5-50f0-bfe7-a51a2e5c22ae |  | textbox | LOT Subfolder No:
text | 36f1caed-45c4-5147-ba59-88b8e6e877ac |  | textbox | Remarks (initial / date)
checkpoint-status |  |  | checkpoint | 3.0 - Test Results
text | 20df3581-7bd1-5fbb-9eac-5ef900717b4a |  | textbox | Item
text | 143eb4ca-edc2-5115-b907-b50b111c810b |  | textbox | Number of Records Required
text | 0c0fe370-e5a3-5232-a5dd-07da3cddf09d |  | textbox | LOT Subfolder No:
text | 6a44f676-e740-51d5-b66a-c0dcd413e749 |  | textbox | Remarks (initial / date)
checkpoint-status |  |  | checkpoint | Conformance of Work Statement (if required ie if some docs not signed):
label | eeb45b55-54c5-5087-b857-81e483a5cbe9 |  | note | The works for this construction lot conforms in respects to the ITP.
text | bfb331a1-5632-5576-8cfc-ff500488f172 |  | textbox | Name:
text | 8935c577-c787-524f-a873-5ca2b5a88213 |  | textbox | Subcontractor:
text | 195ba56a-e4a5-5c27-a972-75bd400df5a4 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Conformance of Work Statement:
label | 9975f30c-630c-5290-ac48-f34dfa172331 |  | note | The works for this construction lot conforms in respects to the ITP.
text | c3658552-2753-5b4c-9e89-548deae9afed |  | textbox | Name:
text | 210c207e-1d7e-5626-a1f6-0b310682b7ae |  | textbox | Subcontractor:
text | 8761f1ed-e489-5353-ab5f-c64f0aa19054 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Conformance / Verification of Construction Lot Statement:
label | 49f71d63-db38-55e9-bcbf-262758e41a1e |  | note | This closed lot conforms in all respects with the standards and requirements specified in the Contract Documents. The lot verification records are complete and attached. Any non-conformances have been dispositioned in accordance with the contract requirements.
text | 146ea390-e7b3-5970-88dc-7ded82319c15 |  | textbox | Name:
text | 79303fa7-0100-5d15-b8b2-9502a8ed73c9 |  | textbox | Subcontractor:
text | 3efff00b-f872-593e-ba95-550026187079 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Quality Review:
text | 418d80dc-0e88-5356-a7b0-78d374c0ed8e |  | textbox | Name:
text | 97e7e928-0d85-5697-b962-cd30af1b4ed2 |  | textbox | Subcontractor:
text | 5061896c-719d-5e75-950a-6db10a284839 |  | textbox | Date:
checklist-flat | 1ff1eda9-e246-49ea-a63d-3f7a003a5cf1 |  | checklist | Electrofusion Welding |  |  |  |  | Yes | Electrofusion Welding | e00c3fcb-b742-46a8-a0d3-4bd7bb54b706
checkpoint-status | d12c9200-3934-4fd5-affd-13103cb9a054 |  | checkpoint | Welding details
select | e77830ce-f45a-55a8-8a52-5f6d69e4ba95 |  | dropdown | EF Coupler completed by and recorded. | Benjamin Habon, EB Lindayao, Jefferson Calla, Redennis Teves, Steve Reeves, William Sabino, Calvin Cheyne, Mark Bateman, John Chingkaw
label | 5fd56b78-e9f7-5af6-a50a-a60b0b6e3bcb |  | note | Fusion Machine Used - SR No 402-1348 Caldertech EF welder
text | 3fa48e41-db68-52ab-81c9-804fc5e2807e |  | textbox | Record EF Coupler Used (Size)
checkpoint-status | 1b9c4532-8cf6-4ea3-8480-c96ebb6cfb55 |  | checkpoint | Pipe surface free from scratches, deeper than 10% of the wall thickness ?
checkpoint-status | 7858b33b-4783-4870-b4ea-aed0845ff578 |  | checkpoint | Pipe scraped and marked ?
checkpoint-status | fa06c62f-e8b1-412f-9c43-6714ed83820c |  | checkpoint | Pipe surface cleaned with Isopropyl alcohol?
checkpoint-status | e4e0cca8-6df2-4a79-b3df-d2fd3da92938 |  | checkpoint | Barcode scanned by machine?
checkpoint-status | 2973a4d7-4cbd-4427-b90d-a928bb1181f2 |  | checkpoint | Record cooling time achieved?
checkpoint-status | 053000d2-41d2-4afd-b182-92257266546c |  | checkpoint | Details of E.F Coupler Operator
select | 25ea69af-78dd-5a8e-bc52-08898dcaa0f7 |  | dropdown | Name | Benjamin Habon, EB Lindayao, Jefferson Calla, Redennis Teves, Steve Reeves, William Sabino, Calvin Cheyne, Mark Bateman, John Chingkaw
holdpoint | c555ef4d-303c-46cb-954b-57b8228b5e25 |  | signoff | Signature
checkpoint-status | c2efb854-1674-40de-9085-fa6ab7efb7f1 |  | checkpoint | Post weld checks completed
holdpoint | c62849b8-1925-4dce-a8a5-ea4583b835af |  | signoff | Post weld checks by Client and AE Smith - Request Signoff
checklist-flat | 10ed7224-c711-4507-9897-7f27ab667212 |  | checklist | Combined Services HDPE Fire Pipework Installation |  |  |  |  | Yes | Combined Services HDPE Fire Pipework Installation | e09c19c4-f149-42ee-a51e-24c713d97a1c
checkpoint-status | 8022e9fd-0aa8-40e4-b447-451b1340c5ab |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 697497df-c6fd-4c50-a7ba-01daccadcc52 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | b7edc8b5-9cd9-4ab6-badb-3ce5419219ce |  | checkpoint | Inspect trench depth, width and pipe alignment
label | ba51a8d2-8504-5e37-b3ba-d1d60c9f3349 |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | b066f345-ca72-5060-aa63-a1d2218c4aad |  | note | QA documents to be provided prior to installing pipework in trenches . CPB to provide to AE Smith.
checkpoint-status | 8821beff-0771-4f4b-b472-80a336648a61 |  | checkpoint | Number of pipes and dimensions of pipes shall be shown on the drawing
checkpoint-status | 83f5d64d-2c67-449d-804e-409f76640c0f |  | checkpoint | Location of pipes shall be shown on the drawing
checkpoint-status | 19a7d8c9-46b4-45f7-8a92-80b7fba56b53 |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
checkpoint-status | 43e9ca16-c620-463b-a4e6-31ff9c21c8e2 |  | checkpoint | Joining of pipework only to be done by Rotable steel flanges and EF Coupling.
checkpoint-status | 675a37db-f46f-4999-844b-a19492446763 |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | 2e7c517a-6630-4d4c-9f35-c39b71dc9d99 |  | checkpoint | Installation of tees and bends
label | 5829e92a-c37e-5b9c-b12c-9750e2b9ec8a |  | note | Install all connection tees as per construction drawings
label | 6b3eea05-4075-56c7-94ff-341987301bca |  | note | Ductile iron bends to be installed on pipework above 300ND
checkpoint-status | bb98b517-ae47-44dd-9126-61d2f259c681 |  | checkpoint | Installation of Hydrants and Hydrant Valves
label | f3b2e1c5-8ef0-5303-9483-9a983e177ad6 |  | note | Mount hydrants on approved types of hydrant tees with risers if necessary so that the top of each hydrant is within 100mm of the finished ground surface level
label | 81829216-8aa1-5604-8fe9-c0a077d8703d |  | note | In-ground hydrants and hydrant valves are installed in secure toby boxes and on isolation spurs.
checkpoint-status | 4fd587cb-7603-4b00-83e1-e114d3ac1749 |  | checkpoint | Install Thrust and Anchor Blocks
label | dd6e72d1-065c-55b8-93e0-97ea38ddba0e |  | note | Minimum dimensions as per IFC drawings.
label | 9645f101-c57a-5f3b-bf48-2e5cbc987eda |  | note | A protective Denso or black coating membrane is to be installed around the pipe and the concrete anchor/thrust blocks to prevent abrasive damage.
checkpoint-status | 33bc3bce-aa56-4bb5-9420-3d899912c43d |  | checkpoint | Installation of Trace Wire
label | 5eeda8b3-da8c-5a3e-9923-82b712c44fd6 |  | note | Install Trace Wire and ensure tracer wire is continuous between valves and any excess coiled in valve box.
label | 2f79e2d4-5294-58e3-8f5e-b7d3b92ad862 |  | note | Test Trace Wire following installation.
checkpoint-status | 3c335720-2666-47ab-8c1e-0937e7627ff3 |  | checkpoint | Completed Construction Pressure Testing with Air
checkpoint-status | 737feebe-f37b-4742-8fbd-ad0653cea5f2 |  | checkpoint | Pre-Pipework Pressure Testing Inspection
label | 439a9998-c367-5685-8e62-fd18afcd4b86 |  | note | Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | 1d153018-38ac-5852-ae19-c7ec6607660b |  | note | Ensure each test length is capped and ball valve installed.
label | beff4f06-94da-5d94-83db-ef98f6d4004d |  | note | Ensure all valves in the system are in the correct position and tagged “DO NOT OPEN” or “DO NOT CLOSE”
label | 057e71b5-c379-52e2-8b62-bf8d89f736b6 |  | note | All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing.
checkpoint-status | 393f7ca7-7580-424b-acad-adf968ac53c5 |  | checkpoint | Introduction of Air to 300 kPa
label | 3815b57e-a832-56b4-9683-0ff70760e3cc |  | note | Gradually introduce air into the system to a pressure of 300 kPa and hold for 1 hour.
label | 269a0052-2d5a-5769-865d-5cdbb745c26c |  | note | Monitor for any drop-in pressure.
label | ffb241e8-2908-5f9f-b29e-e700fdf574b0 |  | note | If a leak is identified discharge the air prior to rectifying any leaks.
checkpoint-status | 30df5c34-da48-446e-be8d-a9f8b5337ebe |  | checkpoint | Increasing Test Pressure
label | 34bba2a1-fc69-5d6a-8b65-f2b4d5467462 |  | note | If no leaks are identified Increase pressure by 10% increments until test pressure is achieved.
checkpoint-status | 2c204f13-a04c-4849-a220-22c6afbe940c |  | checkpoint | Pipework Pressure Test Report Completed
checkpoint-status | cd4c256c-d202-4b65-b743-1cad32ad3393 |  | checkpoint | As-Builts Completed.
holdpoint | b5d480b0-8354-4f62-a3ba-04b22a6d7f1f |  | signoff | Request Signoff/ Raise Remedial
checklist-flat |  |  | checklist | Flushing Site Details |  |  |  |  | Yes | Flushing Site Details | e7978756-5687-4d53-acde-f3a59d7ceb67
checkpoint-status |  |  | checkpoint | Flushing Information collected correctly
text | bced8f71-be22-5b90-ad95-23be884c4a22 |  | textbox | Job number
text | 58d42d1b-3125-52f0-b0d5-95438dd39a11 |  | textbox | Job name
text | 734c6279-9958-533e-8802-4e9ee5c88429 |  | textbox | Builder
select | 20c7f828-b67c-52bb-822a-cf6c69a8f951 |  | dropdown | System Type | Domestic Cold Water, Chilled Water, Heating Hot Water, Low Temperature Heating Hot Water, High Temperature Heating Hot Water, Fire Hydrant
text | 4bfd2d78-679a-5962-9290-ec8077784b32 |  | textbox | System Volume (Litre)
text | e7434e49-60c3-5054-8408-0d50704d955a |  | textbox | Location
text | 504ade3c-3097-59bd-9eea-519b78be4477 |  | textbox | Drawing
boolean | 00a94e86-2473-5471-908c-940ccda162f7 |  | tickbox | CIBSE Commissioning Code W
boolean | c3616dd9-3cd7-51dd-a5df-43cd96225f5e |  | tickbox | BSRIA BG 29/2012
checklist-sectioned |  |  | checklist | AES-NZ1005-STE-ITP-PMT-0024 - DCW Pipework Hydrostatic Pressure Test |  |  |  |  | Yes | AES-NZ1005-STE-ITP-PMT-0024 - DCW Pipework Hydrostatic Pressure Test | f6c728bb-5846-40fb-87c0-a65a5f72c860
checkpoint-group |  |  | section | MATERIAL COMPLIANCE
checkpoint-status |  |  | checkpoint | RDM & Consent Approval - CPB Hold Point
label | 5478e124-cf1e-55ba-bc86-7f5eee17e109 |  | note | CRITERIA - RDM approval tracker Consent approval tracker
checkpoint-status |  |  | checkpoint | General - CPB Hold Point
label | 5a491135-34fc-5ea1-8d81-f8cb6a38b89c |  | note | CRITERIA - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
label | 44025ba1-7a0e-59cf-b21a-a8d7b869d9ad |  | note | • Specifications & QA Documents Approved
label | f956f66f-c7d1-5e7a-85b8-334368bb4f07 |  | note | • Drawings are confirmed
label | e0d21305-5a99-58b1-b386-959dd7350b87 |  | note | • Equipment fit for purpose
checkpoint-group |  |  | section | CONNECT PRESSURE PUMP TO DCW RING MAINS
checkpoint-status |  |  | checkpoint | Confirm Flushing & Disinfection of Pipework - CPB Hold Point
label | a0249970-5137-58d0-9c36-abbd8c42c69e |  | note | CRITERIA - 1. Air should be removed at each building prior to the DCW water supply water entry assembly to prevent debris from entering building.
label | faadcc86-88f2-5117-8f78-c452ed3820c5 |  | note | 2. Ensure system sterilization completed.
label | ed709b78-d374-5bf6-8cb4-f021735f0b85 |  | note | 3. Ensure TNK filtration is cleaned/ inspected if not isolated from test.
label | e3b58431-a7c9-5e57-9487-728d000e009c |  | note | 4. Ensure all screens/ strainers are cleaned/ inspected if not isolated from test.
checkpoint-status |  |  | checkpoint | Accept delivery of pump to site
label | 2b06915f-b1a1-58a8-8197-7fcae002eb89 |  | note | CRITERIA - 5. Check pump is rated for pressure test
label | 3037c693-a888-532b-9c6a-3aedd4ca6343 |  | note | 6. Check all supplied attachments are correct and in good order
label | 8a9000e5-0d1d-53cf-b2cf-5480837ce73e |  | note | 7. Check fluid levels & fill as necessary
checkpoint-status |  |  | checkpoint | Isolate: Mains water Storage Tanks
label | e4983d6a-43b8-5304-9937-ffa7b8886515 |  | note | CRITERIA - 1. Check Mains water is isolated
label | 47370c62-c830-5713-ac69-b070e71f7340 |  | note | 2. Check Storage Tank is isolated
label | 3f9baea1-947b-551d-bde7-a67c7a95f1c6 |  | note | 3. Check Filters are isolated (10 Bar max rated)
checkpoint-status |  |  | checkpoint | Connect pump to pipework under test
label | 5a21b3d9-d5f5-5db1-9692-813435cd5d9a |  | note | CRITERIA - Confirm connections are safe and correct, Supervisor to confirm section under test is correct and all other parts of the system not under test correctly isolated
checkpoint-status |  |  | checkpoint | Connect calibrated gauges for pressure test
label | c62bf30f-7fc2-5373-bffe-6a924f29efa3 |  | note | CRITERIA - Confirm position is correct, gauge is in good order for test & calibrated
checkpoint-group |  |  | section | HYDROSTATIC TEST
checkpoint-status |  |  | checkpoint | Fill DWC ring mains with domestic water
label | 4d152ae4-5ff4-51ba-97d6-785d83046349 |  | note | CRITERIA - Completely fill closed loop system with water releasing all air from the Taps at each Building
checkpoint-status |  |  | checkpoint | Gradually increase system pressure to 1550kPa
label | 5284d731-45bf-591e-9be1-d996ef54480d |  | note | CRITERIA - Slowly raise system pressure to 1550kPa
label | 67fb1be6-d0ad-5bad-be3a-269d47c0991a |  | note | • Checking for any signs of leaks or pressure drops
checkpoint-status |  |  | checkpoint | Stabilize 1550kPa pressure (START WITNESSED) - CPB/IR Hold Point
label | 3c69cdc2-6c0a-56ce-bfa4-20b3150d4ea9 |  | note | CRITERIA - Record START time & photograph gauge
label | f4d887b1-12d4-5ec4-b1e3-ee72e280ffdf |  | note | • All relevant parties to witness starting pressure of 1550kPa
label | d410fe94-93c4-5e66-a46f-7fc2a030b80a |  | note | • IR to be invited for witness at the reviewer’s discretion (Aconex hold point mail)
checkpoint-status |  |  | checkpoint | Hold 1550kPa pressure for 35min (END WITNESSED) - CPB/IR Hold Point
label | 16b9b78c-e8d9-5bde-9faf-8c74f4f4a5f5 |  | note | CRITERIA - Record FINISH time & photograph gauge
label | 16df8195-29d6-5949-adcd-527dff973210 |  | note | • All relevant parties to witness pressure of 1550kPa
label | 09eb3ce8-5336-55c3-abb7-dc38c1a850c5 |  | note | • IR to be invited for witness at the reviewer’s discretion (Aconex hold point mail)
checkpoint-status |  |  | checkpoint | Pressure released or reduced for next test
label | 6da4a585-dc90-56a1-bb88-209797d8322f |  | note | CRITERIA - Supervisor to ensure energy (pressure) is only stored while under test
checkpoint-status |  |  | checkpoint | Discharge pressure leave system in a safe state
label | fd6f14a1-5cf4-5f76-a52b-7d5d1a09970c |  | note | CRITERIA - Discharge system pressure, ensure area is left in a safe state meeting site requirement
checkpoint-group |  |  | section | COMPLETION RECORDS
checkpoint-status |  |  | checkpoint | Testing Results - CPB Hold Point
label | 3f506ff8-3e45-5862-a9fb-1527e459017f |  | note | CRITERIA - All pipework pressure test reports shall be provided
checkpoint-status |  |  | checkpoint | Works Completion Test WCT 68 - CPB/IR Hold Point
label | 96504cc1-7921-582f-ad71-28269b93ebfe |  | note | CRITERIA - PDS testing and satisfactory commissioning (including interfaces with other services) has been completed, recorded and compliance results presented to the Independent Reviewer for the pressure test all cold and domestic hot water pipe lines