## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | AES-NZ1005-STE-ITP-PMT-0030 - EV Charging |  |  |  |  | Yes | AES-NZ1005-STE-ITP-PMT-0030 - EV Charging
section | MATERIAL COMPLIANCE
checkpoint | RDM & Consent Approval
label | Resp. - CPB
label | Referenced Documentation - RDM Tracker Consent Tracker
label | Conformance Criteria - RDM approval tracker Consent approval tracker
label | Method - DR
label | Frequency - By Building/ Site Wide
label | WP - AES
label | Records - Receipt of Approval by Client
checkpoint | General
label | Resp. - SE
label | Referenced Documentation - NZT5007-STE-ESSP-0001
label | Conformance Criteria - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
label | • Specifications & QA Documents Approved
label | • Drawings are confirmed.
label | • Equipment fit for purpose
label | Method - DR
label | Frequency - Each material
label | WP - CPB
label | Records - Aconex approval
label | • Incoming Inspection Checklists
label | • Drawing Register
section | MSB 3 Installation
checkpoint | Factory acceptance tests
label | Resp. - SUP
label | Referenced Documentation - AS/NZS 3000:2007
label | Conformance Criteria - Confirm FATs complete
label | Method - DR
label | Frequency - Once
label | WP - AES, CPB
label | Records - Check Sheet + CMR
checkpoint | Location
label | Resp. - SUP
label | Referenced Documentation - AS/NZS 3000:2007
label | Conformance Criteria - Check MSB is located as per the approved drawings.
label | • Complies with standards
label | Method - V + FM
label | Frequency - Once
label | WP - AES
label | Records - Check Sheet + Photo
checkpoint | Fixings
label | Resp. - SUP
label | Conformance Criteria - Check seismic fixings comply with approved submission
label | Method - V
label | Frequency - Once
label | WP - AES
label | Records - Check Sheet
section | Low Voltage Cable & DB Installation
checkpoint | Electrical conduits
label | Resp. - SUP
label | Referenced Documentation - Refer AES-NZ1005-STE-ITP-PMT-0019
label | Conformance Criteria - Complete as per the referred ITP
label | Method - DR
label | Frequency - Once
label | WP - AES
label | Records - Check Sheet + ITP
checkpoint | Mains & submains Installed & terminated to MSB-3
label | Resp. - SUP
label | Referenced Documentation - AEC-NZ1005-STE-SCH-ELE-0002
label | • AEC-NZ1005-STE-SCH-ELE-0004
label | • AES-NZ1005-STE-ITP-PMT-0022
label | • AS/NZS 3000:2007
label | Conformance Criteria - Installed as per cable schedule on cable tray & inground conduits & pull pits.
label | • Installed & terminated.
label | • Pre-livening tests ONLY as per AES-NZ1005-STE-ITP-PMT-0022
label | Method - V + FM
label | Frequency - Once
label | WP - AES
label | Records - Check Sheet + ITP
checkpoint | Carpark DBs Installed
label | • HRO
label | • UT1
label | • STA
label | Resp. - SUP
label | Conformance Criteria - Location as per drawings
label | • Plinths installed & grouted around conduit
label | • Conduits cut down for DB install
label | • DB placed & fixed to plinth
label | Method - V
label | Frequency - Each Location
label | WP - AES
label | Records - Check Sheet + Photo
checkpoint | Submains Terminated to DBs
label | • DB-STE-EV1 (HRO)
label | • DB-STE-EV2 (UT1)
label | • DB-STE-EV3 (STA)
label | Resp. - SUP
label | Referenced Documentation - AEC-NZ1005-STE-SCH-ELE-0004, AES-NZ1005-STE-ITP-PMT-0022, AS/NZS 3000:2007
label | Conformance Criteria - Installed as per cable schedule on cable tray & inground conduits & pull pits.
label | • Installed & Terminated.
label | • Pre-livening tests ONLY as per AES-NZ1005-STE-ITP-PMT-0022
label | Method - V + FM
label | Frequency - Each Location
label | WP - AES
label | Records - Check Sheet
checkpoint | MSB-3 Pre-Livening Checks Complete - LJE/AES/CPB Hold Point
label | Resp. - SUP
label | Referenced Documentation - LJE-UT1 MSB3 AS/NZS 3000:2007
label | Conformance Criteria - As per LJE commissioning Plan
label | • MSB-3 Main Switch & Sub Circuit breakers Isolated
label | • Safe to Liven Mains from TX3 to MSB3
label | Method - V + DR
label | Frequency - Once
label | Hold Point - LJE / AES / CPB
label | Records - Check Sheet + CMP
checkpoint | HV Switching TX3 - AES/CPB Hold Point
label | Resp. - SUP
label | Conformance Criteria - HV Switching confirmed by CPB
label | Method - V
label | Frequency - Once
label | Hold Point - AES / CPB
label | Records - Check Sheet
checkpoint | MSB-3 Energisation & Commissioning - CPB Hold Point
label | Resp. - SUP
label | Referenced Documentation - AES-NZ1005-STE-ITP-PMT-0022, LJE-UT1 MSB3, AS/NZS 3000:2007
label | Conformance Criteria - Live cable testing on MSB-3 as per AES-NZ1005-STE-ITP-PMT-0022
label | • Main Switch Isolation removed.
label | • MSB-3 commissioned as per LJE commissioning plan
label | Method - V + FM + DR
label | Frequency - Once
label | WP - AES
label | Hold Point - CPB
label | Records - Check Sheet + ITP + CMP + COC
checkpoint | Site DBs Pre-Livening Checks Complete - LJE/AES/CPB Hold Point
label | Resp. - SUP
label | Referenced Documentation - LJE-UT1 MSB3 AS/NZS 3000:2007
label | Conformance Criteria - As per LJE commissioning Plan
label | • DB Main Switch & Sub Circuit breakers Isolated
label | • Safe to Liven Mains from MSB-3 to DBs
label | Method - V + DR
label | Frequency - Each Location
label | Hold Point - LJE / AES / CPB
label | Records - Check Sheet + CMP
checkpoint | Site DBs Energised & Commissioned - CPB Hold Point
label | • DB-STE-EV1 (HRO)
label | • DB-STE-EV2 (UT1)
label | • DB-STE-EV3 (STA)
label | Resp. - SUP
label | Referenced Documentation - AES-NZ1005-STE-ITP-PMT-0022 LJE-UT1 MSB3 AS/NZS 3000:2007
label | Conformance Criteria - Live cable testing on DBs as per AES-NZ1005-STE-ITP-PMT-0022
label | • Main Switch Isolation removed.
label | • DBS commissioned as per LJE commissioning plan
label | Method - V + FM + DR
label | Frequency - Each Location
label | WP - AES
label | Hold Point - CPB
label | Records - Check Sheet + ITP + CMP + COC
section | Communication Install
checkpoint | Communications conduits Install
label | Resp. - SUP
label | Referenced Documentation - Refer AES-NZ1005-STE-ITP-PMT-0008
label | Conformance Criteria - Complete as per the referred ITPs
label | Method - DR
label | Frequency - Once
label | WP - AES
label | Records - Check Sheet + ITP
section | EV Charger Plinth Install
checkpoint | Foundations & Plinths Installed
label | Resp. - SUP
label | Referenced Documentation - AES-NZ1005-STE-DSH-ELE-0034
label | Conformance Criteria - Foundations for ABB wall charger pedestals installed to approved specification.
label | • Precast plinths for ABB T54
label | • Chargers installed at HRO & STA carparks
label | Method - Each location
label | Frequency - V
label | WP - AES
label | Records - Check Sheet + Photos
checkpoint | Low Voltage Cables Installed - AES Hold Point
label | Resp. - SUP
label | Referenced Documentation - AEC-NZ1005-STE-SCH-ELE-0004, AES-NZ1005-STE-ITP-PMT-0022, AS/NZS 3000:2007
label | Conformance Criteria - Installed as per cable schedule through inground conduits & pull pits.
label | • Pre-livening tests ONLY as per AES-NZ1005-STE-ITP-PMT-0022
label | • Communication & Charger control cables run to each location from DBs
label | Method - Each location
label | Frequency - V + DR + FM
label | Hold Point - AES
label | Records - Check Sheet + Photos + ITP
section | Completion Test & Record
checkpoint | Works Completion Test WCT 54 - AES/CPB/IR Hold Point
label | Resp. - SUP
label | Referenced Documentation - Schedule 11 WCT 54 (e)(f) AS/NZS 3000:2007
label | Conformance Criteria - The EIS for the New Waikeria Facility have been installed in accordance with the FDD. This includes EIS testing and satisfactory commissioning (including interfaces with other services) has been completed, recorded and compliance results presented to the Independent Reviewer for the following systems:
label | (e) general power;
label | (f) earthing system;
label | Method - FTR + V + DR
label | Frequency - Once
label | WP - AE Smith + LJE
label | Hold Point - AES / CPB / IR
label | Records - Check Sheet + QA documents + COC
checkpoint | Works Completion Test WCT 83 - AES/CPB/IR Hold Point
label | Referenced Documentation - Schedule 11 WCT 83 Cable pull pits
label | Conformance Criteria - Cable Pull pits inside the primary physical barrier are accessible for maintenance and have locking type bolt down metal covers
label | Method - DR
label | Frequency - On completion of installation
label | WP - AES / Downer
label | Hold Point - AES / CPB / IR
label | Records - Check Sheet
checkpoint | Conformance records
label | Resp. - SUP
label | Conformance Criteria - All relevant records will be provided and demonstrate compliance with project requirements
label | Method - DR
label | Frequency - Each Lot
label | WP - AES
label | Records - Check Sheet
checkpoint | As-built Survey
label | Resp. - SUP
label | Referenced Documentation - NZT5007-SSS-CSSP-0001
label | Conformance Criteria - As Built Completed
label | Method - DR
label | Frequency - Each Lot
label | WP - AES
label | Records - Check Sheet