## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | Storage Tanks |  |  |  |  | Yes | Storage Tanks | 303abc28-7941-4575-b09b-5863b6329476
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Latest specifications and standards
checkpoint-status |  |  | checkpoint | Setout & alignment as per latest available drawing (include revision below)
text | 2dac603a-a8ed-576a-b281-bffaee43666a |  | textbox | Drawing & revision number(s)
text | b4c9e30c-4bd0-5eca-9c09-d0a8a1f0a95a |  | textbox | Correct approved materials as per sample register
checkpoint-status |  |  | checkpoint | Manufacturer's quality
checkpoint-status |  |  | checkpoint | Connections and valves properly installed and tested for leaks
checkpoint-status |  |  | checkpoint | Access equipment installed as per AS1657
checkpoint-status |  |  | checkpoint | Level sensor installed and working correctly
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | c71fbcd0-7542-5a12-b54b-5fdad61dab24 |  | note | Passing above includes Builder sign-off
boolean | ba6ac862-5c91-5caa-a031-4d9f1dac0c02 |  | tickbox | Area clean
checklist-flat |  |  | checklist | Sewer AG |  |  |  |  | Yes | Sewer AG | 154115e8-b409-4d89-b5c1-2f348bbb34c9
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | 9f5bfc79-865f-5120-b541-ceffbb8b9085 |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Grades, fittings & joints installed to standards
checkpoint-status |  |  | checkpoint | Fixings & seismic support to standards
checkpoint-status |  |  | checkpoint | Expansion joints per floor installed correctly & clipped
checkpoint-status |  |  | checkpoint | Pipe risers sealed per floor & capped off to prevent damage
checkpoint-status |  |  | checkpoint | Correct invert level (As per Standards)
checkpoint-status |  |  | checkpoint | Vents and AAV installed (As per Standards)
checkpoint-status |  |  | checkpoint | Acoustic lagging installed to acoustic specification
checkpoint-status |  |  | checkpoint | Pipework water tested to 15Kpa
checkpoint-status |  |  | checkpoint | Identifications of services
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | e75379fb-b4d5-5695-844e-519058b24034 |  | note | Passing above includes Builder sign-off
boolean | 7a05bd1e-1c34-5c78-9c01-f1b575d5101c |  | tickbox | Area clean
checklist-flat |  |  | checklist | Trench Grate |  |  |  |  | Yes | Trench Grate | c1cd56d2-8dc4-4c1b-907c-453d74aa6ffa
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Latest specifications and standards nominated in ITP
checkpoint-status |  |  | checkpoint | Setout & alignment as per latest available drawing (include revision below)
text | e9509583-0218-5014-940d-5beb1fcd92d3 |  | textbox | Drawing & revision number(s)
text | f683f79e-d387-52bf-9133-3bd49022f980 |  | textbox | Correct approved materials as per sample register
checkpoint-status |  |  | checkpoint | Manufacturer's Quality
checkpoint-status |  |  | checkpoint | Trench Grate Installation & correct invert levels
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 9670b777-0d89-53a6-a5c2-d3edca2dd1b8 |  | note | Passing above includes Builder sign-off
boolean | 30e1982f-6f8b-55a7-8df5-a53b9d200067 |  | tickbox | Area clean
checklist-flat |  |  | checklist | Pump / Macerator Station |  |  |  |  | Yes | Pump / Macerator Station | a8f5e0fa-912d-4fd6-89b3-a43cb2eff59f
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Latest specifications and standards
checkpoint-status |  |  | checkpoint | Setout & alignment as per latest available drawing (include revision below)
text | c2639861-086f-53a6-bc31-62e4087b0cb8 |  | textbox | Drawing & revision number(s)
text | 1543b2a0-c741-5feb-b71d-346c19e936b0 |  | textbox | Correct approved materials as per sample register
checkpoint-status |  |  | checkpoint | Manufacturer's quality
checkpoint-status |  |  | checkpoint | Pit excavation
checkpoint-status |  |  | checkpoint | Pit installation & correct invert levels
checkpoint-status |  |  | checkpoint | Pump installed correctly
checkpoint-status |  |  | checkpoint | Guide rails installed correctly
checkpoint-status |  |  | checkpoint | All valves installed correctly
checkpoint-status |  |  | checkpoint | Pressure transducer installed correctly
checkpoint-status |  |  | checkpoint | Builder sign off prior concealment
checkpoint-status |  |  | checkpoint | Backfilling (as per specification / geotechnical report)
checkpoint-status |  |  | checkpoint | Compaction of material (as per specification / geotechnical report)
checkpoint-status |  |  | checkpoint | Clean and flush
checkpoint-status |  |  | checkpoint | Inspection and photos prior to closure
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 0071f320-09a8-5d33-93e3-78d460538855 |  | note | Passing above includes Builder sign-off
checklist-flat |  |  | checklist | Pipework Flushing Procedure |  |  |  |  | Yes | Pipework Flushing Procedure | 69f0dea4-88bb-4efb-9568-eda4a879b36a
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Pipework Flushing Date & Time
text | ec67aac4-0279-5d4e-bd95-82dffd555873 |  | textbox | Date & time
checkpoint-status |  |  | checkpoint | All "Flush Out Points" on the floor requires warning signage
checkpoint-status |  |  | checkpoint | Check Required volume to be flushed from each system - hot & cold - calculations can be found in "WPD Pipework Flushing Folder" for time durations per area
checkpoint-status |  |  | checkpoint | Cold Water System - Start by opening tap located furthest from the meters, open others on the way back & observe time to ensure system has been sufficiently drained. Open outside taps for enough time to empty volume of the main line, then flush each toilet the required amount to empty each branch.
checkpoint-status |  |  | checkpoint | Hot Water System - Start by opening tap located closest to end of the return line, open others on the way back & observe time to ensure system has been sufficiently drained.
checkpoint-status |  |  | checkpoint | Flushing showerheads & hoses - let the shower hang down (without touching the ground) it will let the water drain out afterwards. The water in a showerhead & hose when it sits there inside can become a risk and also causes scale buildup.
label | a51b9e4c-79d7-57ab-bf92-cac9806e8c3c |  | note | Faucets/taps with an aerator on it, should be removed during flushing, to allow the outlet to flush at high volume.
checkpoint-status |  |  | checkpoint | All taps turned off & area made safe
checkpoint-status |  |  | checkpoint | Complete register & attach photos
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 5814df4f-a6c4-5a18-a8f8-bf6a3279b93f |  | note | Passing above includes Builder sign-off
boolean | 2eb62fa0-968a-5907-9e4c-b6a0a4611eba |  | tickbox | Area clean
checklist-flat |  |  | checklist | Inspection Chamber |  |  |  |  | Yes | Inspection Chamber | 9b88b206-d8d9-400a-8e84-e015a2b771fa
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Latest specifications and standards nominated in ITP
checkpoint-status |  |  | checkpoint | Setout & alignment as per latest available drawing (include revision below)
text | 74b286b3-b05a-5aad-934f-f09b92983298 |  | textbox | Drawing & revision number(s)
text | ed781823-b922-5b22-bf4a-304071d811fa |  | textbox | Correct approved materials as per sample register
checkpoint-status |  |  | checkpoint | Manufacturer's Quality
checkpoint-status |  |  | checkpoint | Inspection Chamber Excavation
checkpoint-status |  |  | checkpoint | Inspection Chamber Installation & correct invert levels (as per AS 3500.2 Section 4.8)
checkpoint-status |  |  | checkpoint | Builder sign off prior concealment
checkpoint-status |  |  | checkpoint | Backfilling (as per AS 3500.2 Section 5.5)
checkpoint-status |  |  | checkpoint | Compaction of Material (As per Specification / Geotechnical report)
checkpoint-status |  |  | checkpoint | Clean and Flush
checkpoint-status |  |  | checkpoint | Inspection Prior to Closure
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | ff1454ea-5fff-5d36-ac54-8ac8bcf522fa |  | note | Passing above includes Builder sign-off
boolean | 20c637af-9351-59b0-befc-4f06e5d9fc97 |  | tickbox | Area clean
checklist-flat |  |  | checklist | Rainwater |  |  |  |  | Yes | Rainwater | ae7e669c-ec76-4cb0-95c8-e5e068411579
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | 556e3567-020d-57e0-83c0-8c9b89b907f0 |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Material type as per approved sample submission
checkpoint-status |  |  | checkpoint | Pipework fittings, bends, joints etc (as per AS 3500.1 section 2.6)
checkpoint-status |  |  | checkpoint | Welding / pressfit / push fit (as per AS 3500.1)
checkpoint-status |  |  | checkpoint | Support & fixings (acoustic / seismic / water hammer)
checkpoint-status |  |  | checkpoint | Pipework Installation (as per AS 3500.1)
checkpoint-status |  |  | checkpoint | Check no cross connection
checkpoint-status |  |  | checkpoint | Pressure test (1500kpa pressure test)
checkpoint-status |  |  | checkpoint | Identifications of services
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | d598042d-9beb-5581-bea6-d241ce09f4c9 |  | note | Passing above includes Builder sign-off
boolean | 99cf2a97-f2d5-5de0-a106-f9b0e532ef2b |  | tickbox | Area clean
checklist-flat |  |  | checklist | Commissioning Pump / Macerator Station |  |  |  |  | Yes | Commissioning Pump / Macerator Station | d1e3acad-6417-44b8-a1a1-5b66584c74e7
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Condition as when it was installed (report any changes)
checkpoint-status |  |  | checkpoint | Control panel installed
checkpoint-status |  |  | checkpoint | Electrical wiring connected between pumps, controller & level sensing system installed correctly
checkpoint-status |  |  | checkpoint | Connected to BMS
checkpoint-status |  |  | checkpoint | Connected to power supply
checkpoint-status |  |  | checkpoint | BMS faults in working order (specify faults)
checkpoint-status |  |  | checkpoint | High level alarm in working order
checkpoint-status |  |  | checkpoint | Supplier commissioning sheet
boolean | 80fe671d-0832-5009-bb04-b99e13b5cf53 |  | tickbox | Area clean
checklist-sectioned |  |  | checklist | Corridor Template |  |  |  |  | Yes | Corridor Template | 8a643e99-1421-48af-b83d-7ed37c34a799
checkpoint-group |  |  | section | High Level Services
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | cb99b1be-acc6-5dfd-81a1-2d67ec8c7ddc |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Material type as per approved sample submission with AGA or watermarks
checkpoint-status |  |  | checkpoint | Welding , press fittings, witness marks visually checked
checkpoint-status |  |  | checkpoint | Fixings & seismic support to standards
checkpoint-status |  |  | checkpoint | Pipework installations to code requirements
checkpoint-status |  |  | checkpoint | Water meters installed to authority standards
checkpoint-status |  |  | checkpoint | Gas 25mm separation achieved from other services as per AS 5601.1
checkpoint-status |  |  | checkpoint | Penetrations, fire protection, wall sealant installed to the BCA requirements
checkpoint-status |  |  | checkpoint | Identifications of services, valves & meters to standards
checkpoint-status |  |  | checkpoint | Pressure test to code requirements
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 9199fe7b-71b2-5f07-8e25-387163764a22 |  | note | Passing above includes Builder sign-off
boolean | 76bbce7c-5bf3-51d3-925f-78724a646f60 |  | tickbox | Area clean
checkpoint-group |  |  | section | Drainage
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual) and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Stormwater riser
checkpoint-status |  |  | checkpoint | Syfon drainage
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
boolean | 4c3c4be5-d7ec-5d65-a679-489be32d2fb3 |  | tickbox | Area clean
checkpoint-group |  |  | section | Sewer AG
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | 30735e82-8533-5bac-a2ec-f7cfd2ae63d5 |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Grades, fittings & joints installed to standards
checkpoint-status |  |  | checkpoint | Fixings & seismic support to standards
checkpoint-status |  |  | checkpoint | Expansion joints per floor installed correctly & clipped
checkpoint-status |  |  | checkpoint | Pipe risers sealed per floor & capped off to prevent damage
checkpoint-status |  |  | checkpoint | Correct invert level (As per Standards)
checkpoint-status |  |  | checkpoint | Vents and AAV installed (As per Standards)
checkpoint-status |  |  | checkpoint | Acoustic lagging installed to acoustic specification
checkpoint-status |  |  | checkpoint | Pipework water tested to 15Kpa
checkpoint-status |  |  | checkpoint | Identifications of services
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | a915df0a-ea40-5466-b505-8901c92623c0 |  | note | Passing above includes Builder sign-off
boolean | 53b71f03-d600-58bf-bb1b-ce89cc38c824 |  | tickbox | Area clean
checklist-flat |  |  | checklist | Greywater |  |  |  |  | Yes | Greywater | 3294944a-a96e-48d0-b2c1-c18a54a66121
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout and alignment as per drawing (include revision in comments)
text | 33bca168-8d58-59d2-b4b1-527c2a9eaab6 |  | textbox | Grades, fittings & joints
checkpoint-status |  |  | checkpoint | Fixings and seismic
checkpoint-status |  |  | checkpoint | Expansion joints per floor installed correctly and clipped
checkpoint-status |  |  | checkpoint | Pipe risers sealed per floor and capped off to prevent damage
checkpoint-status |  |  | checkpoint | Correct invert level
checkpoint-status |  |  | checkpoint | Check for no cross connections with waste drainage
checkpoint-status |  |  | checkpoint | AAV installed
checkpoint-status |  |  | checkpoint | Acoustic lagging installed to acoustic specification
checkpoint-status |  |  | checkpoint | Testing to 15KPA
checkpoint-status |  |  | checkpoint | Identifications of services
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 2a06649d-fc15-588f-8c26-c4570321d1f4 |  | note | Passing above includes Builder sign-off
boolean | 29c7248b-cac0-5980-b343-4fd2810f02a2 |  | tickbox | Area clean
checklist-flat |  |  | checklist | Greasy AG |  |  |  |  | Yes | Greasy AG | 009fe4cc-0e38-48c2-bba4-87979055d8e8
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | 8217a15e-af2a-55c7-8455-07e2c78caae4 |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Correct material as per sample register
checkpoint-status |  |  | checkpoint | Grades, fittings & joints installed to standards including witness marks
checkpoint-status |  |  | checkpoint | Fixings & seismic support to code requirements
checkpoint-status |  |  | checkpoint | Expansion joints per floor installed correctly & clipped
checkpoint-status |  |  | checkpoint | Pipe risers sealed per floor & capped off to prevent damage
checkpoint-status |  |  | checkpoint | Correct ventilation installed including AAV
checkpoint-status |  |  | checkpoint | Acoustic lagging installed to acoustic specification
checkpoint-status |  |  | checkpoint | Testing to 15KPA with air or full water test
checkpoint-status |  |  | checkpoint | Identifications of services
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 322ffad7-0247-5d67-a8fd-1d9302e87c2c |  | note | Passing above includes Builder sign-off
boolean | 2dcbc319-62e0-5f73-bac8-0f7be9274de8 |  | tickbox | Area clean
checklist-sectioned |  |  | checklist | Fix 2 checklist |  |  |  |  | Yes | Fix 2 checklist | cb5f8455-e511-4a46-a43c-3cc12b47b642
checkpoint-group |  |  | section | Fixtures
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Correct product (samples provided)
checkpoint-status |  |  | checkpoint | Check products for imperfections
checkpoint-status |  |  | checkpoint | Location & fixings (as per drawings & manufacturer guidelines)
checkpoint-status |  |  | checkpoint | Silicone seals are acceptable standard (as applicable)
checkpoint-status |  |  | checkpoint | Operation of all fixtures, taps & points of demand
checkpoint-status |  |  | checkpoint | Final fit off inspection on all items
text | 46d9f226-f5af-5ddd-8010-253a4c69a164 |  | textbox | Inspection date
checkpoint-status |  |  | checkpoint | Items protected until commissioning (Attach photos below)
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 69810024-33d2-5272-aae3-f313c17231cb |  | note | Passing above includes Builder sign-off
boolean | df7ff3fe-0757-5f6d-be88-bab6d62f7c2a |  | tickbox | Area clean
checkpoint-group |  |  | section | Commissioning
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Check products for imperfections
checkpoint-status |  |  | checkpoint | Fixtures location & fixings all correct (as per drawings & samples)
checkpoint-status |  |  | checkpoint | Clean out all strainers / aerators
checkpoint-status |  |  | checkpoint | Check for no cross connections / leaks / access to isolation valves
checkpoint-status |  |  | checkpoint | Floor wastes (clear of debris & draining correctly)
checkpoint-status |  |  | checkpoint | Quality of silicone seals to fixtures acceptable
checkpoint-status |  |  | checkpoint | Hot water tempering valve set to 50c (+/- 5c) & DDA thermostatic mixing valve set to 42 degrees.
checkpoint-status |  |  | checkpoint | Water pressure acceptable 350Kpa to 500 Kpa
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 6044ab76-416f-5ca3-8755-f45c75921fe0 |  | note | Passing above includes Builder sign-off
boolean | c09a24d8-f6a7-5b98-b7eb-b202c261c4a4 |  | tickbox | Area clean
checklist-flat |  |  | checklist | Rough In Checklist |  |  |  |  | Yes | Rough In Checklist | f381badb-6e20-45ea-9958-9252a1b62900
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | 727a45f5-271f-5b07-9faa-77440e511108 |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Material type (as per sample submission)
checkpoint-status |  |  | checkpoint | Welding / pressfit / push fit / witness marks (as per AS 3500.1)
checkpoint-status |  |  | checkpoint | Support & fixings checked (acoustic / seismic / water hammer/ silicone) - Add Photos below
checkpoint-status |  |  | checkpoint | Pipework installation checked against standards (as per AS 3500.1)
checkpoint-status |  |  | checkpoint | Check no cross connection
checkpoint-status |  |  | checkpoint | Heights double checked before room sign off as per sample submission
checkpoint-status |  |  | checkpoint | Pipe risers water sealed per floor & capped off to prevent damage
checkpoint-status |  |  | checkpoint | Correct sewer ventilation installed
checkpoint-status |  |  | checkpoint | Pressure test water lines to (1500kpa)
checkpoint-status |  |  | checkpoint | Identification of services
text | 57c060f6-fbee-549c-a65d-8c07b4dcd4cd |  | textbox | Services
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | a2a56273-3d2e-5b45-a8ae-3d078cd41d88 |  | note | Passing above includes Builder sign-off
boolean | 0d339bcb-3e1e-5402-a9ab-e7c9dba9ee31 |  | tickbox | Area clean
checklist-flat |  |  | checklist | In Ground Tank |  |  |  |  | Yes | In Ground Tank | bc6175e8-b5b1-4bf3-8925-efabb2a21053
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Latest specifications and standards nominated in ITP
checkpoint-status |  |  | checkpoint | Setout & alignment as per latest available drawing (include revision below)
text | 87cbc86b-5a2e-5cf4-9085-469a113bfdd9 |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Correct approved materials as per sample register
checkpoint-status |  |  | checkpoint | Manufacturer's Quality
checkpoint-status |  |  | checkpoint | Tank Excavation
checkpoint-status |  |  | checkpoint | Tank Installation & correct invert levels (as per AS 3500.1 Section 8)
checkpoint-status |  |  | checkpoint | Builder sign off prior concealment
checkpoint-status |  |  | checkpoint | Backfilling (as per AS 3500.3 Section 6.2.11)
checkpoint-status |  |  | checkpoint | Compaction of Material (As per Specification / Geotechnical report)
checkpoint-status |  |  | checkpoint | Clean and Flush
checkpoint-status |  |  | checkpoint | Inspection Prior to Closure
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 8712cf5b-89b7-5a8f-b885-1728beb51b74 |  | note | Passing above includes Builder sign-off
boolean | dbeae28b-1d7b-5fd4-bfd4-bf499920e669 |  | tickbox | Area clean
checklist-flat |  |  | checklist | Stormwater BG |  |  |  |  | Yes | Stormwater BG | b9e0c86c-7443-4f7e-bb8f-6d28c320c06b
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Latest specifications and standards nominated in ITP
checkpoint-status |  |  | checkpoint | Setout & alignment as per latest available drawing (include revision below)
text | 8ca56149-6b29-57d8-8293-31db936a7304 |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Correct approved materials as per sample register
checkpoint-status |  |  | checkpoint | Excavation undertaken & no issues (Any issues comment below)
checkpoint-status |  |  | checkpoint | Pipe bedding material (as per AS 500)
checkpoint-status |  |  | checkpoint | Grades, fittings & joints installed to standards
checkpoint-status |  |  | checkpoint | Pipe clean out via water flush
checkpoint-status |  |  | checkpoint | Inspection and Testing Prior to Concealment to AS 3500.2 section 13
checkpoint-status |  |  | checkpoint | Builder sign off prior concealment
checkpoint-status |  |  | checkpoint | Seal open ends with caps & high light to avoid damage
checkpoint-status |  |  | checkpoint | Backfill & Compaction of Material (As per Specification / Geotechnical report)
checkpoint-status |  |  | checkpoint | CCTV on completion & record results (If applicable)
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | e4bf5831-c911-5182-b503-b026a2e04767 |  | note | Passing above includes Builder sign-off
boolean | adaf729f-81d1-54b9-80e1-562f8a57570b |  | tickbox | Area clean
checklist-flat |  |  | checklist | Slab Penetrations Template |  |  |  |  | Yes | Slab Penetrations Template | b588dd52-9ddd-4fd9-b51d-b06effd22ff2
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | e6f76ed5-abc6-535e-9c95-de1488eb4ebc |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Approved fire protection material installed (as per approved samples)
checkpoint-status |  |  | checkpoint | Fire protection material installed as per Manufacturer's Instructions
checkpoint-status |  |  | checkpoint | Fire protection material installed in correct locations
checkpoint-status |  |  | checkpoint | Penetration secured down for concrete pour
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photo's below)
label | ad9dfa2b-3d19-5504-97f1-4553ab23ebfc |  | note | Passing above includes Builder sign-off
boolean | 49c38675-82eb-590a-8de4-44c8e82f86be |  | tickbox | Area clean
checklist-flat |  |  | checklist | Cold Water BG |  |  |  |  | Yes | Cold Water BG | 4e6f2a3a-0f48-407a-8262-a67e5483b1b9
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | ce333f36-f37e-5e65-b1f5-f7f3229b11bb |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Correct material as per sample register
checkpoint-status |  |  | checkpoint | Bedding material installed correctly
checkpoint-status |  |  | checkpoint | Fittings & joints correctly installed to manufacturer's requirements
checkpoint-status |  |  | checkpoint | Satisfactory welding/pressing of copper pipe
checkpoint-status |  |  | checkpoint | Witness marks visible
checkpoint-status |  |  | checkpoint | Pipework layed correctly and to AS 3500
checkpoint-status |  |  | checkpoint | Inspection and Testing Prior to Concealment to AS 3500
checkpoint-status |  |  | checkpoint | Seal open ends with caps & high light to avoid damage
checkpoint-status |  |  | checkpoint | Identification of services via I.D tape
checkpoint-status |  |  | checkpoint | Backfill & compaction to specification in 300mm layers
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 443b740b-a999-55c1-a5ed-a4cde8615a57 |  | note | Passing above includes Builder sign-off
boolean | eeda2b32-33f4-5119-a576-6570c6bc1e56 |  | tickbox | Area clean
checklist-flat |  |  | checklist | Vacuum Drainage |  |  |  |  | Yes | Vacuum Drainage | 0de3e743-241b-4043-b45f-db8a98dac905
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | 85277292-5428-5892-a2f2-cb3a2a3ec152 |  | textbox | Drawing & revision number(s)
text | 56f59781-8bcf-5301-9f6a-8f17e9abf65f |  | textbox | Material type (as per sample submission)
checkpoint-status |  |  | checkpoint | Correct invert level (as per AS 3500.2 Section 16)
checkpoint-status |  |  | checkpoint | Pipework fittings, bends, joints etc (as per AS 3500.2 Section 16)
checkpoint-status |  |  | checkpoint | Support & fixings (acoustic / seismic)
checkpoint-status |  |  | checkpoint | Pipework installation checked against standards (as per AS 3500.2)
checkpoint-status |  |  | checkpoint | Check no cross connection
checkpoint-status |  |  | checkpoint | Pipework water tested to 35-70Kpa
checkpoint-status |  |  | checkpoint | Identifications of services
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 1d2aabb2-1ee4-5476-a52c-2ce16c3dcd8f |  | note | Passing above includes Builder sign-off
boolean | 60bd5bbc-5d64-5970-be86-316abddf0fc5 |  | tickbox | Area clean
checklist-flat |  |  | checklist | Greasy BG |  |  |  |  | Yes | Greasy BG | 93a3c3d2-d387-4dd8-bf8f-588dd56b7ae0
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Latest specifications and standards nominated in ITP
checkpoint-status |  |  | checkpoint | Setout & alignment as per latest available drawing (include revision below)
text | ed7f1990-d9b9-5ee0-8d2f-23fd62d7d0e5 |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Correct approved materials as per sample register
checkpoint-status |  |  | checkpoint | Excavation undertaken & no issues (Any issues comment below)
checkpoint-status |  |  | checkpoint | Pipe bedding material comply (as per AS 3500)
checkpoint-status |  |  | checkpoint | Grades, fittings & joints installed to standards
checkpoint-status |  |  | checkpoint | Pipe clean out via water flush
checkpoint-status |  |  | checkpoint | Inspection & Testing Prior to Concealment to AS 3500.2 section 13
checkpoint-status |  |  | checkpoint | Builder sign off prior concealment
checkpoint-status |  |  | checkpoint | Seal open ends with caps & high light to avoid damage
checkpoint-status |  |  | checkpoint | Backfill & Compaction of Material (As per Specification / Geotechnical report)
checkpoint-status |  |  | checkpoint | CCTV on completion & record results
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | d445b355-0c12-5154-ae8f-b7e9ca7451ab |  | note | Passing above includes Builder sign-off
boolean | ab98eebd-6a8f-5f80-bf18-b33f5a7ed932 |  | tickbox | Area clean
checklist-flat |  |  | checklist | Gas BG |  |  |  |  | Yes | Gas BG | 7700a1a3-9ae2-43f6-a406-7952b7e2b05c
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | 45f3c097-1ccc-5c81-92ee-921ec480f5bc |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Correct material as per sample register
checkpoint-status |  |  | checkpoint | Bedding material installed correctly
checkpoint-status |  |  | checkpoint | Fittings & joints correctly installed to manufacturer's requirements
checkpoint-status |  |  | checkpoint | Witness marks visible
checkpoint-status |  |  | checkpoint | Pipework layed correctly and to AS 5601.1
checkpoint-status |  |  | checkpoint | Inspection and Testing Prior to Concealment to AS 5601.1 (ESV start works notice)
checkpoint-status |  |  | checkpoint | Seal open ends with caps & high light to avoid damage
checkpoint-status |  |  | checkpoint | Identification of services via I.D tape
checkpoint-status |  |  | checkpoint | Backfill & compaction to specification in 300mm layers
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 08ac5835-bbd8-5da6-bd48-b62b63d9f7b8 |  | note | Passing above includes Builder sign-off
boolean | ef1be147-c0b5-5122-9a64-7f1f4b34ef70 |  | tickbox | Area clean and As-Built Markup
checklist-flat |  |  | checklist | Stormwater AG |  |  |  |  | Yes | Stormwater AG | 776dd442-d329-49d9-9215-7fd8b113dbea
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | 23e2b1dc-2644-555b-bfa2-5bf65a72adcf |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Grades (as per AS:3500)
checkpoint-status |  |  | checkpoint | Location (as per hydraulic drawing)
text | 4c56132b-0f66-55b1-9162-f1b783bdeeec |  | textbox | Location
checkpoint-status |  |  | checkpoint | Fixings - Securely fixed (As per Standards)
checkpoint-status |  |  | checkpoint | Fittings Joints ETC (as per AS 3500)
checkpoint-status |  |  | checkpoint | Inspection prior to closure
checkpoint-status |  |  | checkpoint | Operation of pumps (Commissioning report) if Applicable
checkpoint-status |  |  | checkpoint | Test water and discharge requirements are met
checkpoint-status |  |  | checkpoint | Correct invert level AS per AS 3500
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 6cac5e8d-0697-5691-b230-9932953a7a99 |  | note | Passing above includes Builder sign-off
boolean | 6223520b-dffa-5cf0-b3f8-2c5e11ece80a |  | tickbox | Area clean
checklist-flat |  |  | checklist | Pit |  |  |  |  | Yes | Pit | 819cd8c8-f917-4f2c-a000-6df2ad699cea
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Latest specifications and standards nominated in ITP
checkpoint-status |  |  | checkpoint | Setout & alignment as per latest available drawing (include revision below)
text | f4070de4-8412-52a5-919f-02529508b1a0 |  | textbox | Drawing & revision number(s)
text | c84052a2-32fc-5b62-b215-6f941ab26799 |  | textbox | Correct approved materials as per sample register
checkpoint-status |  |  | checkpoint | Manufacturer's Quality
checkpoint-status |  |  | checkpoint | Pit Excavation
checkpoint-status |  |  | checkpoint | Pit Installation & correct invert levels (as per AS 3500.3 Section 7.5)
checkpoint-status |  |  | checkpoint | Builder sign off prior concealment
checkpoint-status |  |  | checkpoint | Backfilling (as per AS 3500.3 Section 6.2.11)
checkpoint-status |  |  | checkpoint | Compaction of Material (As per Specification / Geotechnical report)
checkpoint-status |  |  | checkpoint | Clean and Flush
checkpoint-status |  |  | checkpoint | Inspection Prior to Closure
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | b6de496b-efa9-5201-aa86-b50086f8a583 |  | note | Passing above includes Builder sign-off
boolean | fef867d3-bbd1-5a89-a505-925acfe089d0 |  | tickbox | Area clean
checklist-flat |  |  | checklist | CCTV Checksheet |  |  |  |  | Yes | CCTV Checksheet | ef9c72ca-d734-4295-83be-b9fd0195dc71
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | CCTV Completed & Attached
button | 9b71e5b7-6bf9-5b62-bb73-b0f95b3a1904 |  | button | Drains clear, free of obstructions & in acceptable condition | Yes, No
text | 08ae1480-199c-5ac4-9db1-910c1effe443 |  | textbox | If No the above explain why
checkpoint-status |  |  | checkpoint | Final sign off - CCTV completed, Pass when satisfied to proceed (Any issues please comment & Add photos below)
checklist-flat |  |  | checklist | Cold Water Checklist |  |  |  |  | Yes | Cold Water Checklist | 96bb2fc5-a1de-427d-adf5-cbadba4e8ad8
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | 0b5356a3-f3b0-580a-b8e6-1d15171d6bc9 |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Material type (as per sample submission)
checkpoint-status |  |  | checkpoint | Pipework fittings, bends, joints etc (as per AS 3500.1 section 2.6)
checkpoint-status |  |  | checkpoint | Welding / pressfit / push fit (as per AS 3500.1)
checkpoint-status |  |  | checkpoint | Support & fixings (acoustic / seismic / water hammer)
checkpoint-status |  |  | checkpoint | Pipework installation (as per AS 3500.1)
checkpoint-status |  |  | checkpoint | Check no cross connection
checkpoint-status |  |  | checkpoint | Pressure test (1500kpa pressure test)
checkpoint-status |  |  | checkpoint | 3rd Party Inspection (Including the below as applicable)
text | 29c85837-6c12-5e06-a4cf-4eb4f57e8ff7 |  | textbox | Name
text | eabe51d2-55e2-5835-9627-39eb2eec7190 |  | textbox | Company
holdpoint |  |  | signoff | Click to Add 3rd party signature(s) & any documentation
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 115a44e7-adc7-503e-a3ed-41433fb24a64 |  | note | Passing above includes Builder sign-off
boolean | 3af74322-d85f-521b-a189-2c4fa9aed469 |  | tickbox | Area clean
checklist-flat |  |  | checklist | Hot Water |  |  |  |  | Yes | Hot Water | 8231491e-2676-45ea-a4d9-b1bac2c067f7
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | 30cef90b-df11-5324-9591-bf618cec368f |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Material type (as per sample submission)
checkpoint-status |  |  | checkpoint | Pipework fittings, bends, joints etc (as per AS 3500.1 section 2.6)
checkpoint-status |  |  | checkpoint | Welding / pressfit / push fit (as per AS 3500.1)
checkpoint-status |  |  | checkpoint | Support & fixings (acoustic / seismic / water hammer)
checkpoint-status |  |  | checkpoint | Pipework installation (as per AS 3500.1)
checkpoint-status |  |  | checkpoint | Check no cross connection
checkpoint-status |  |  | checkpoint | Pressure test (1500kpa pressure test)
checkpoint-status |  |  | checkpoint | 3rd Party Inspection (Including the below as applicable)
text | 610b5f60-6943-52f7-bbc5-225d2a2d7151 |  | textbox | Name
text | 037d41be-24d1-5d1b-9815-346b9645f3ad |  | textbox | Company
holdpoint |  |  | signoff | Click to Add 3rd party signature(s) & any documentation
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 32f69748-89fc-55d5-a0aa-bc742fe2dcd7 |  | note | Passing above includes Builder sign-off
boolean | 6d68e0b8-9bbf-5dd1-8720-94d41ad35dfa |  | tickbox | Area clean
checklist-flat |  |  | checklist | Recycled Water |  |  |  |  | Yes | Recycled Water | 8fa6c34d-f1de-4f8e-9f46-f2da84cb45af
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout and alignment as per drawing (include revision in comments)
text | 2fe65b73-6428-55ec-9a8f-558c40ad9459 |  | textbox | Material type (as per sample submission)
checkpoint-status |  |  | checkpoint | Pipework fittings, bends, joints etc (as per AS 3500.1 section 2.6)
checkpoint-status |  |  | checkpoint | Welding / pressfit / push fit (as per AS 3500.1)
checkpoint-status |  |  | checkpoint | Support & fixings (acoustic / seismic / water hammer)
checkpoint-status |  |  | checkpoint | Pipework installation (as per AS 3500.1)
checkpoint-status |  |  | checkpoint | Check no cross connection with domestic water supply
checkpoint-status |  |  | checkpoint | Pressure test (1500kpa pressure test)
checkpoint-status |  |  | checkpoint | Identifications of services
checkpoint-status |  |  | checkpoint | Final inspection (3rd Party)
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 11e0e3be-7263-5e10-9820-dd61574dd136 |  | note | Passing above includes Builder sign-off
boolean | 4e5df4e9-aa31-5f66-9b07-3a377aa3aab4 |  | tickbox | Area clean
checklist-flat |  |  | checklist | Prefab Checklist |  |  |  |  | Yes | Prefab Checklist | d88140aa-f2c5-4cce-90d5-f5f376dc6c05
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Check materials products for imperfections
checkpoint-status |  |  | checkpoint | Site sample, diagrams, & materials list clear to understand
button | 63dbc8cd-6a30-5321-ab94-4d4653c8c674 |  | button | Order complete | Yes, No
button | b2f48885-623d-5430-9087-ef14ce33e06a |  | button | Delivery booked with site team | Yes, No
checkpoint-status |  |  | checkpoint | Completed stillage or pallet weighed & materials do not exceed SWL of stillage or pallet
button | 9fc16094-8168-58ee-9a6e-90a36c291c18 |  | button | Factory paperwork attached to package including weight stamp | Yes, No
button | 23aa40a7-fa34-5403-b237-37f3a3ab2185 |  | button | Delivery weight total does not exceed SWL of delivery truck | Yes, No
checkpoint-status |  |  | checkpoint | Delivery sent to site
checkpoint-status |  |  | checkpoint | Order complete
checklist-flat |  |  | checklist | Sanitary |  |  |  |  | Yes | Sanitary | 41e4e287-72f8-4b0d-b1d5-18f0598d8198
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout and alignment as per drawing (include revision in comments)
text | 1baae0ce-27d1-5881-9405-b0799354ec67 |  | textbox | Materials Type (as per sample submission)
checkpoint-status |  |  | checkpoint | Fittings & fixings (as per AS 2032)
checkpoint-status |  |  | checkpoint | Identification of services
checkpoint-status |  |  | checkpoint | Heights double checked before room sign off off fixture approvals tech data
checkpoint-status |  |  | checkpoint | Pipe risers sealed per floor and capped off to prevent damage
checkpoint-status |  |  | checkpoint | Correct ventilation
checkpoint-status |  |  | checkpoint | CCTV drainage
checkpoint-status |  |  | checkpoint | Testing (air testing to 15kpa)
checkpoint-status |  |  | checkpoint | Identifications of services
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 9254d17f-36fd-51ca-a44f-a7cc624590d8 |  | note | Passing above includes Builder sign-off
boolean | e8daf5e3-05f5-5fec-90e1-fcabca0966ac |  | tickbox | Area clean
checklist-flat |  |  | checklist | Backfill & Compaction |  |  |  |  | Yes | Backfill & Compaction | 279076c7-2ecd-469c-bd89-632cb277502c
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Latest specifications and standards
checkpoint-status |  |  | checkpoint | Location surface type as per approved drawings
text | 1a96c87f-e00d-50c2-b376-e3c6d473458b |  | textbox | Specify surface type
checkpoint-status |  |  | checkpoint | Minimum compaction requirement (%)
text | 2aec21d3-1ed3-520b-bab6-2e449a9fc71c |  | textbox | %
checkpoint-status |  |  | checkpoint | Compaction of Material (As per Specification / Geotechnical report)
checkpoint-status |  |  | checkpoint | Compaction layer thickness (mm)
text | 1ea3d031-79c2-511d-8c41-b53064c923d4 |  | textbox
checkpoint-status |  |  | checkpoint | Backfilling (as per AS 3500.3 Section 6.2.11)
checkpoint-status |  |  | checkpoint | Compaction test
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 98d992c7-63b0-5abd-9d42-3f7a09685b65 |  | note | Passing above includes Builder sign-off
boolean | 512847a4-ebcd-5206-9bd3-965588596c4d |  | tickbox | Area clean
checklist-flat |  |  | checklist | Gas |  |  |  |  | Yes | Gas | c3cc4de5-c4ef-4120-b2a7-42bb93d299d5
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | 7cbb92cf-204f-5a14-bce1-f8a80d91234f |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Material type as per approved sample submission
checkpoint-status |  |  | checkpoint | Welding, press fittings, witness marks visually checked
checkpoint-status |  |  | checkpoint | Supports & fixings to ESV and WPD standards
checkpoint-status |  |  | checkpoint | Pipework installations to ESV standards
checkpoint-status |  |  | checkpoint | Penetrations, fire protection, wall sealant installed to the BCA requirements
checkpoint-status |  |  | checkpoint | Witness marks / labels / tiger tape / kpa signage
checkpoint-status |  |  | checkpoint | Pressure test (as per AS/NZS 5601.1)
checkpoint-status |  |  | checkpoint | Test appliances (as per AS/NZS 5601.1)
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | b0ef75ce-c8cb-55a3-8bb8-8edf2de4dc76 |  | note | Passing above includes Builder sign-off
boolean | db3b3603-b255-5b48-b35b-104e67c3aa88 |  | tickbox | Area clean
checklist-flat |  |  | checklist | Sewer BG |  |  |  |  | Yes | Sewer BG | 159bdd7d-60aa-4f40-b899-73a8d7b99578
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Latest specifications and standards nominated in ITP
checkpoint-status |  |  | checkpoint | Setout & alignment as per latest available drawing (include revision below)
text | b70c799f-2066-56d8-b665-37b35cd695e4 |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Correct approved materials as per sample register
checkpoint-status |  |  | checkpoint | Excavation undertaken & no issues (Any issues comment below)
checkpoint-status |  |  | checkpoint | Pipe bedding material comply (as per AS 3500)
checkpoint-status |  |  | checkpoint | Grades, fittings & joints installed to standards
checkpoint-status |  |  | checkpoint | Pipe clean out via water flush
checkpoint-status |  |  | checkpoint | Inspection & Testing Prior to Concealment to AS 3500.2 section 13
checkpoint-status |  |  | checkpoint | Builder sign off prior concealment
checkpoint-status |  |  | checkpoint | Seal open ends with caps & high light to avoid damage
checkpoint-status |  |  | checkpoint | Backfill & Compaction of Material (As per Specification / Geotechnical report)
checkpoint-status |  |  | checkpoint | CCTV on completion & record results
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 97dd0b2e-a83d-519f-8182-117ea05afb34 |  | note | Passing above includes Builder sign-off
boolean | 8bf65035-b551-5f28-900a-e71621ef0e25 |  | tickbox | Area clean
checklist-flat |  |  | checklist | Fire Service BG |  |  |  |  | Yes | Fire Service BG | df4909e7-1613-4bca-b9d8-e8bbb4a9c281
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | 773e22ae-338e-5c21-acf6-79181698c09e |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Correct material as per sample register
checkpoint-status |  |  | checkpoint | Bedding material installed correctly
checkpoint-status |  |  | checkpoint | Fittings & joints correctly installed to manufacturer's requirements
checkpoint-status |  |  | checkpoint | Satisfactory welding/pressing of copper pipe
checkpoint-status |  |  | checkpoint | Witness marks visible
checkpoint-status |  |  | checkpoint | Pipework layed correctly & to AS 3500
checkpoint-status |  |  | checkpoint | Concrete anchor thrust blocks installed as per engineers report
checkpoint-status |  |  | checkpoint | Testing to 1700 kPa with no leaks for 120 minutes
checkpoint-status |  |  | checkpoint | Identification of services via I.D tape
checkpoint-status |  |  | checkpoint | Backfill & compaction to specification in 300mm layers
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 3d867dea-2eb3-53a0-b65c-5385813173a7 |  | note | Passing above includes Builder sign-off
boolean | 7844d696-5542-5006-b1e1-3ca8caf379a1 |  | tickbox | Area clean
checklist-flat |  |  | checklist | Water Meter Validation |  |  |  |  | Yes | Water Meter Validation | c055b4fa-3c78-4311-b282-a3e26c618aed
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Correct meter installed as per sample register (Attach photo below)
checkpoint-status |  |  | checkpoint | Clean out all strainers & flush water before validation starts
checkpoint-status |  |  | checkpoint | Check BMS is connected
checkpoint-status |  |  | checkpoint | Check meter has correct labelling tag as per the meter matrix
checkpoint-status |  |  | checkpoint | Check right pulse rate to be recorded
text | ca103616-30f2-58b1-90e6-b5abe2fc8dbe |  | textbox | Pulse rate
checkpoint-status |  |  | checkpoint | Turn on test point & fill test bucket with water to marked litre level
checkpoint-status |  |  | checkpoint | Record reading is the same with BMS contractor
text | 52596dad-3129-5b59-9b6d-546daa99e646 |  | textbox | Record reading(s)
checkpoint-status |  |  | checkpoint | Remove test lines & insert plug, test for leaks
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 3658dcca-7e48-53af-872c-3f33df1b582e |  | note | Passing above includes Builder sign-off
boolean | a2ffb3fe-15bc-5a50-9fd6-473df18f5f87 |  | tickbox | Area clean
checklist-sectioned |  |  | checklist | Fix 1 Checklist |  |  |  |  | Yes | Fix 1 Checklist | 02133698-ed36-4a4f-b888-698a465a9251
checkpoint-group |  |  | section | Sewer AG
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | 72276118-d3d9-5547-be32-01e122894e62 |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Grades, fittings & joints installed to standards
checkpoint-status |  |  | checkpoint | Fixings & seismic support to standards
checkpoint-status |  |  | checkpoint | Expansion joints per floor installed correctly & clipped
checkpoint-status |  |  | checkpoint | Pipe risers sealed per floor & capped off to prevent damage
checkpoint-status |  |  | checkpoint | Correct invert level (As per Standards)
checkpoint-status |  |  | checkpoint | Vents and AAV installed (As per Standards)
checkpoint-status |  |  | checkpoint | Acoustic lagging installed to acoustic specification
checkpoint-status |  |  | checkpoint | Pipework water tested to 15Kpa
checkpoint-status |  |  | checkpoint | Identifications of services
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | e101fc39-e2df-57dc-ba78-13b0627bc7d3 |  | note | Passing above includes Builder sign-off
boolean | b7d7749f-dff4-5731-9568-de08012a748e |  | tickbox | Area clean
checkpoint-group |  |  | section | Stormwater AG
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | 731c34a3-433b-5d6e-9e0e-eacdba234e7d |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Grades (as per AS:3500)
checkpoint-status |  |  | checkpoint | Location (as per hydraulic drawing)
text | 182d568a-531b-5324-9c27-38eb42b6ef9c |  | textbox | Location
checkpoint-status |  |  | checkpoint | Fixings - Securely fixed (As per Standards)
checkpoint-status |  |  | checkpoint | Fittings Joints ETC (as per AS 3500)
checkpoint-status |  |  | checkpoint | Inspection prior to closure
checkpoint-status |  |  | checkpoint | Operation of pumps (Commissioning report) if Applicable
checkpoint-status |  |  | checkpoint | Test water and discharge requirements are met
checkpoint-status |  |  | checkpoint | Correct invert level AS per AS 3500
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 9744e09c-39de-5a84-965f-c82542d952f0 |  | note | Passing above includes Builder sign-off
boolean | d22d4cc5-aca1-5312-9ca8-70e30408a433 |  | tickbox | Area clean
checkpoint-group |  |  | section | Rough In
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | 158b76e3-be91-5355-a271-0090670d56aa |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Material type (as per sample submission)
checkpoint-status |  |  | checkpoint | Pipework installation checked against standards (as per AS 3500.1)
checkpoint-status |  |  | checkpoint | Welding / pressfit / push fit / witness marks (as per AS 3500.1)
checkpoint-status |  |  | checkpoint | Support & fixings checked (acoustic / seismic / water hammer/ silicone)
checkpoint-status |  |  | checkpoint | Check for no cross connection
checkpoint-status |  |  | checkpoint | Heights double checked before room sign off as per sample submission
checkpoint-status |  |  | checkpoint | Pipe risers water sealed per floor and capped off to prevent damage
checkpoint-status |  |  | checkpoint | Correct sewer ventilation
checkpoint-status |  |  | checkpoint | Pressure test water lines to (1500kpa)
checkpoint-status |  |  | checkpoint | Identification of services
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 63f584c4-8979-5870-ab9b-e43d94b38c87 |  | note | Passing above includes Builder sign-off
boolean | 316ad6c9-7a3f-5e27-a836-f32b1c15abfa |  | tickbox | Area clean
checkpoint-group |  |  | section | Rainwater
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | 39bcf99b-c78d-52af-8afa-4bb7486f2bcc |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Material type as per approved sample submission
checkpoint-status |  |  | checkpoint | Pipework fittings, bends, joints etc (as per AS 3500.1 section 2.6)
checkpoint-status |  |  | checkpoint | Welding / pressfit / push fit (as per AS 3500.1)
checkpoint-status |  |  | checkpoint | Support & fixings (acoustic / seismic / water hammer)
checkpoint-status |  |  | checkpoint | Pipework Installation (as per AS 3500.1)
checkpoint-status |  |  | checkpoint | Check no cross connection
checkpoint-status |  |  | checkpoint | Pressure test (1500kpa pressure test)
checkpoint-status |  |  | checkpoint | Identifications of services
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 77f9838d-58b2-57b6-bc60-9aad782ae6e4 |  | note | Passing above includes Builder sign-off
boolean | 645c65ef-478d-566b-b14d-6582608fcd2f |  | tickbox | Area clean
checklist-flat | 9b4b9b84-84b6-49c8-9af9-298a07794a79 |  | checklist | Project Shutdown Protocol Checklist |  |  |  |  | Yes | Project Shutdown Protocol Checklist | 67264145-5949-4376-bf0d-fae6e62f342e
checkpoint-status | fd9069c7-bb03-44e6-b3cf-bb4f2c1389f0 |  | checkpoint | Project Shutdown Details
label | 8021266e-6b28-5e5b-9b33-c2084a2d489a |  | note | Complete/Comment/Photo ALL aspects below to insure site is shut down correctly
label | 32a6c768-b122-5117-922d-b04b7ede627f |  | note | *** Add photos for each aspect as applicable ***
checkpoint-status | 9719ae5e-79ac-47f9-9ce7-7b18c1f0ee68 |  | checkpoint | Check Roof areas
boolean | 27f4fcd1-43ab-5392-9ef2-7f2d8a8f6214 |  | tickbox | Area Clean/Tidy
checkpoint-status | b7283350-4839-4b5e-b032-d2470d21b5c5 |  | checkpoint | Check downpipes are connected with mechanical fixings not duct tape
checkpoint-status | bb84a1e5-3eb2-4099-8f95-353053805f35 |  | checkpoint | Turn OFF water supply to all temporary lines
checkpoint-status | 54055b7d-ad1b-4a27-a027-63817b9f3b63 |  | checkpoint | Check Stormwater/Sewer Pumpwells are all working
button | a0dd8afa-a1f4-53e7-9950-497eb7bc734c |  | button | Pumpwell is in good order | No,Yes
label | 0b2fa59b-43f8-595a-b323-7ad6cdce1587 |  | note | If No comment/photo issues/solutions below
checkpoint-status | 1a82ffb1-a679-4367-acf2-188139dc53cb |  | checkpoint | Wilson open penetrations on all floors covered & sealed
label | 2e70496f-d771-52ae-9cb7-eead4d1b2f6e |  | note | Photos attached below
checkpoint-status | 5f3ab802-0212-4741-bbe5-675ba280ccaf |  | checkpoint | Shut down Main Water Pumps
button | 331bbe1d-f731-5696-a6c7-6f292ac52c35 |  | button | Pumps Made safe | No,Yes
checkpoint-status | df411c30-1e55-4468-8bbb-6c4f3a2813ab |  | checkpoint | Turn OFF Hot Water Plants
button | de7e22e0-1e0c-52c9-886d-79654654ec74 |  | button | HW Plants Made safe | No,Yes
checkpoint-status | 0b66a989-61c7-4454-a7c9-e32ae2b78d24 |  | checkpoint | Make sure all loose material is secure
label | d552cb69-521b-5712-aca2-34333b4fe058 |  | note | Including deck work
checkpoint-status | 219557cd-3547-4e5a-ad7e-55f4d942f681 |  | checkpoint | TOTAL clean up of all materials
label | 1bdda025-3494-5653-abf5-8289ce13209e |  | note | Stacked/Stored adequately for duration of shut down
checkpoint-status | c0a2c9db-7aba-4e6a-ba0f-a843306bc409 |  | checkpoint | Copper pipe not installed to be placed in secure location
label | 22967b3c-ea6e-5622-9caf-5ced5dfe693b |  | note | Attach photos of secured copper pipe below
checkpoint-status | 88ec993d-8e63-4dab-9b15-12f4ba74870a |  | checkpoint | All IT items to be taken home
label | 09d0743f-423e-5c62-8293-50b0c1a99239 |  | note | Printers can remain on site
checkpoint-status | fb1914e5-3799-476f-a50a-675f29b44796 |  | checkpoint | All Tools stored in secure location OR removed from site
button | 1095c688-29e7-557f-92ef-9100e4f861e3 |  | button | Tools stored securely and photos attached | No,Yes
text | 7c67f5bb-d406-505e-bce1-1ede7c227771 |  | textbox | If NO list Tools removed from site
checkpoint-status | 3d054c9c-5adc-42db-b1b0-8694220cc86b |  | checkpoint | OXY hoses totally removed from bottles and placed in secure location
label | 1f40ab3b-a49b-5538-9a6f-5ef360b237e1 |  | note | Attach photos of secured OXY hoses below
checkpoint-status | 4be08a37-5183-4ca7-9f8e-ad65a76cfe3b |  | checkpoint | All Machinery shut down
button | 82e65e82-ed31-5285-b90d-19f1c0157785 |  | button | Keys removed from Machinery | No,Yes
button | a853c7f1-f1e1-5055-8ec8-16a61b26ac87 |  | button | Machinery stored in a safe/secure location | No,Yes
label | cb218817-f9cb-51f7-90b5-de4abef8443a |  | note | Attach photos of secured Machinery below
checkpoint-status | dd0080cd-d702-49b4-bb3b-d76863066d0b |  | checkpoint | FINAL - Site adequately shutdown, All WPD items secured/removed or Made safe & Photos attached
label | c183aa39-2cdb-5b3a-a852-a4749293427c |  | note | By passing acceptance the site is ready to be shutdown
checklist-flat |  |  | checklist | Fire Collars |  |  |  |  | Yes | Fire Collars | aa241013-8b90-4cfe-8831-0747ffa45ca3
checkpoint-status |  |  | checkpoint | Employee trained for task and reviewed installation instructions (product QR code / manufacturer's website / instruction manual)
checkpoint-status |  |  | checkpoint | Setout & alignment as per drawing (include revision below)
text | 4d79d0d2-0fd5-5330-8996-726106b44dbe |  | textbox | Drawing & revision number(s)
checkpoint-status |  |  | checkpoint | Installation as per manufacturer's requirements
checkpoint-status |  |  | checkpoint | Correct fire collar location (as per drawing)
text | 1763043a-a68d-5bf3-ace8-e5777e13b589 |  | textbox | Location
checkpoint-status |  |  | checkpoint | Fire tags as per fire matrix installed
checkpoint-status |  |  | checkpoint | Structurally correct (Engineers Approval required)
boolean | 02392771-70eb-56c6-9fb3-4c62464bd81c |  | tickbox | Engineers Approval attached
checkpoint-status |  |  | checkpoint | Fire sealant installed correctly
checkpoint-status |  |  | checkpoint | Final Inspection - 3rd Party (Including the below as applicable)
text | 6783f43e-b6a0-5396-a72b-b8161d707c53 |  | textbox | Name
text | cbc222d0-0091-535e-9ece-eb4ecad99a1a |  | textbox | Company
holdpoint |  |  | signoff | Click to Add 3rd party signature(s)
checkpoint-status |  |  | checkpoint | Final sign off - Pass when satisfied to proceed (Any issues please comment & Add photos below)
label | 61720622-49d4-5002-ae36-bf2394cf2696 |  | note | Passing above includes Builder sign-off