## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | GM-ITPS-002 Fire Alarm and EWIS Design | itp |  |  |  |  | GM-ITPS-002 Fire Alarm and EWIS Design
section | Details
checkpoint | 1 - REVIEW CLIENTS DRAWING REGISTER
label | ACCEPTANCE CRITERIA SPECIFIED - IN HOUSE
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 2 - NOTATE INTERNAL DRAWING REGISTER
label | ACCEPTANCE CRITERIA SPECIFIED - IN HOUSE
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 3 - REVIEW TENDER/CONSTRUCTION DRAWINGS
label | ACCEPTANCE CRITERIA SPECIFIED - IN HOUSE
textbox | DRAWING REFERENCE NUMBER - Construction Issued Drawings Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 4 - REVIEW SPECIFICATION
label | ACCEPTANCE CRITERIA SPECIFIED - NCC2019 FIRE SPECIFICATION
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 5 - PREPARE SHOP DRAWINGS/ LAYOUTS
label | ACCEPTANCE CRITERIA SPECIFIED - IN HOUSE NCC2019 FIRE SPECIFICATION
label | QUALITY CONTROL - A & I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6 - REVIEW SUPPLIERS SHOP DRAWINGS
label | ACCEPTANCE CRITERIA SPECIFIED - NCC2019
textbox | DRAWING REFERENCE NUMBER - Issued Drawings Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 7 - DESIGNING FIRE ALARM SCHEMATIC
label | ACCEPTANCE CRITERIA SPECIFIED - In House Design 1670.1-2018 – Must specify size/type of cable to be installed, transmission paths, type of devices to be installed and End of Line Devices
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 7 - PREPARE SCHEMATIC DRAWINGS
label | ACCEPTANCE CRITERIA SPECIFIED - Prepared to as installed drawings.
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 7 - SUBMIT SHOP DRAWINGS FOR APPROVAL
label | ACCEPTANCE CRITERIA SPECIFIED - In house design Referenced to PC specifications
textbox | DRAWING REFERENCE NUMBER - For Approval Issued Drawing No:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 10 - REVIEW RETURNED SHOP DRAWINGS
label | ACCEPTANCE CRITERIA SPECIFIED - In House QA
textbox | DRAWING REFERENCE NUMBER - For Approval Issued Drawing No:
label | QUALITY CONTROL - W & I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 11 - DISTRIBUTE "FOR CONSTRUCTION" DRAWINGS
label | ACCEPTANCE CRITERIA SPECIFIED - Referenced to PC specifications. Updated and superseded as needed
textbox | DRAWING REFERENCE NUMBER - Construction Issued Drawing No:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
holdpoint | Signatures
checklist | GM-ITPS-003 Purchasing and Procurement | itp |  |  |  |  | GM-ITPS-003 Purchasing and Procurement
section | Details
checkpoint | 1 - EQUIPMENT PURCHASES TO SPECIFICATION
label | ACCEPTANCE CRITERIA SPECIFIED - In House QA Samples approved by PC/ CL
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Issued Drawings Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 2 - CHECK SPECIFICATION SAMPLES HAVE BEEN APPROVED.
label | ACCEPTANCE CRITERIA SPECIFIED - Approval by PC/ CL
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 3 - MATERIALS APPROVED FOR INSTALLATION
label | ACCEPTANCE CRITERIA SPECIFIED - CL Specification
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Issued Drawings Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 4 - PURCHASE ORDERS SPECIFIC AND PRICED
label | ACCEPTANCE CRITERIA SPECIFIED - Orders from approved suppliers
label | ○ In House QA – Equipment ordered > Equipment Supplied
label | ○ POs referenced and invoices approved
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Construction Issued Drawings Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 5 - FIRE PANEL DELIVERED – AS ORDERED
label | ACCEPTANCE CRITERIA SPECIFIED - In House QA Reference Design Invoice from Supplier
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6 - FIRE PANEL Q.A. CERTIFIED
label | ACCEPTANCE CRITERIA SPECIFIED - In House QA To system Design requirements Supplier QA referenced
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | QUALITY CONTROL - C
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 7 - SMOKE DETECTORS DELIVERED AS ORDERED
label | ACCEPTANCE CRITERIA SPECIFIED - Samples approved by PC/ CL.
label | ○ Quantities as required.
label | ○ Invoices checked.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Issued Drawings Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 8 - FABRICATED PIPE & VALVES DELIVERED AS ORDERED
label | ACCEPTANCE CRITERIA SPECIFIED - SPRINKLERS: AS2118.1-2017 – Section 7.1; All pipes, valves and fittings shall be supplied new
label | ○ HYDRANTS: AS2419.2-2005 – Section 8.1.1; Pipe, valve and fittings provided shall be new and comply with fitting specification.
label | ○ In House QA
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Issued Drawings Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 9 - SPRINKLER HEADS DELIVERED AS ORDERED
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Section 9 & 10; Shall be new and meet the demands of the system they are installed on (Light/Ordinary Hazard)
label | ○ In House QA
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Issued Drawings Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
holdpoint | Signatures
checklist | GM-ITPS-004 Fire Alarm and EWIS Installation | itp |  |  |  |  | GM-ITPS-004 Fire Alarm and EWIS Installation
section | Details
checkpoint | 1 - CABLE TYPE & SIZE TO DESIGN CRITERIA
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018 Have a cross sectional area of no less than 0.75mm2 AS3000
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | C5.4.0 Wiring | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 2 - CABLE HEIGHTS & LOCATION ADEQUATE FOR FIT OFF
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: internal domestic and office situations where cabling is mounted on walls at heights above 1.5m AS3000
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | C5.2.5 Control Loops | Pass
radio | C5.4.0 Wiring | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 3 - CABLE FIXED TO SPECIFIED REQUIREMENTS
label | ACCEPTANCE CRITERIA SPECIFIED - AS3000-2018: Where a wiring system is not resting on a continuous surface it shall be supported by suitable means in accordance with Clause 3.3.9
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | C5.2.5 Control Loops | Pass
radio | C5.4.0 Wiring | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 4 - DETECTOR BASES FITTED OFF
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670, AS1668: Detectors that can be contaminated by construction works should not be fitted unless suitably protected until the construction works are completed.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 5 - DETECTOR HEADS INSTALLED & TYPE CHECKED
label | ACCEPTANCE CRITERIA SPECIFIED - Detector type to appropriate location. Installed to Latest RCP
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | C5.6.0 Sensors/Detectors | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6 - MANUAL CALL POINTS INSTALLED
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: An MCP shall be mounted between 750 mm and 1100 mm above floor level and a clear space of 600 mm shall be provided in a semi-circle in front of the MCP.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | C5.10.0 Manual Call Points | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 7 - STROBES FITTED OFF
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: Check with Design Drawing and/or RCP
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | C5.2.2 Set Points | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 8 - SPEAKERS INSTALLED
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670: Check with Design Drawing and/or RCP
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 9 - WARDEN INTERCOM PHONES
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.4-2018: The WIP handset shall be mounted at a height of not less than 1200 mm and not more than 1800 mm above finished floor level.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | C6.2.8 Warden Intercom Phones | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 10 - SPRINKLER INTERFACES FITTED OFF
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: The ‘end-to-end’ test should include the activation of associated detection devices to confirm that all required functions operate correctly in accordance with the system interface matrix.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | C5.2.2 Set Points | Pass
radio | C5.8.0 Modules Input/Output | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 11 - FIRE RATING TO PENETRATIONS CORRECT
label | ACCEPTANCE CRITERIA SPECIFIED - AS4072.1-2018: Ensure correct Test Report is used – refer to FRL requirements on wall selection
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 12 - LABELS AFFIXED
label | ACCEPTANCE CRITERIA SPECIFIED - AS4072.1-2018: The label should be positioned close to the service penetration
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 13 - ACOUSTIC PENETRATION SEALING
label | ACCEPTANCE CRITERIA SPECIFIED - AS4072.1-2018: Sound proofing sealant may be used depending on dB Level requirements
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 14 - CABLE TRAY BRACKET SPACING
label | ACCEPTANCE CRITERIA SPECIFIED - AS3000-2018: Where a wiring system is not resting on a continuous surface it shall be supported by suitable means in accordance with Clause 3.3.9
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 15 - INSTALLED IN ACCORDANCE APPROVED WORKING DRAWING AND LATEST ARCHITECTURAL
label | ACCEPTANCE CRITERIA SPECIFIED - In House QA
label | ○ Up to Date drawing register
label | ○ Drawings updated with MPX approved references
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
holdpoint | Signatures
checklist | GM-ITPS-005 Fire Alarm and EWIS Commissioning | itp |  |  |  |  | GM-ITPS-005 Fire Alarm and EWIS Commissioning
section | Details
checkpoint | 1 - CONDUCT 100% TESTING OF ZONING
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: Ensure Detectors are activated when tested and correctly indicates on the detectors and at the FDCIE
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | GMF-COMDRY-001 - Fire Detection Zone Commissioning | Pass
radio | C5.2.6 Sequencing | Pass
radio | C5.2.9 Alarm Functions | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 2 - CONDUCT 100% TESTING OF SMOKE AND THERMALS
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: Aspirating detectors measure and record the transport time (TT) from the most disadvantaged sampling point for each sampling pipe or branch.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | GMF-COMDRY-002 - Fire Detection and Alarms (Smokes, Thermals, Duct Probes) | Pass
radio | C5.6.0 Sensors/Detectors | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 3 - CONDUCT 100% TESTING OF MCPS
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018:
label | (i) the correct operation of each manual call point;
label | (ii) that the activation of manual call points on the same circuit as other actuating devices does not cause existing detector alarm indications to be extinguished; and
label | (iii) that manual call points are not subjected to alarm dependency.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | GMF-COMDRY-003 - Manual Call Points | Pass
radio | C5.10.0 Manual Call Points | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 4 - CONDUCT 100% TESTING OF DOOR DEVICES
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: Check the operation of each device/door release once installed
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | GMF-COMDRY-004 - M.D.H / Auto Door Commissioning | Pass
radio | C5.8.0 Modules Input/Output | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 5 - CONDUCT 100% TESTING CASCADE AND EWIS ZONING
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.4-2018: Audible signals, visual and tactile signals to be checked – automatic operation.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | GMF-COMDRY-005 - Emergency Warning Cascade and Matrix | Pass
radio | C6.2.5 Cascade Sequence | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6 - CONDUCT 100% TESTING SPEAKERS AND ZONES
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: Ensure Detectors are activated when tested and correctly indicates on the detectors and at the FDCIE
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | C5.6.0 Sensors/Detectors | Pass
radio | GMF-COMDRY-006 - Emergency Warning Commissioning | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 7 - CONDUCT 100% TESTING WARDEN INTERCOM PHONES
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.4-2018: The WIP audible call signal shall have a SPL of not less than 80 dB(A) when measured at a distance of 1 m from the WIP. The SPL of the WIP handset audible call signal shall also be met when the WIP handset is mounted within a security enclosure.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | C6.2.8 Warden Intercom Phones | Pass
radio | GMF-COMDRY-007 - Warden Intercom Point | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 8 - CONDUCT FIRE MATRIX TESTING
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: The ‘end-to-end’ test should include the activation of associated detection devices to confirm that all required functions operate correctly in accordance with the system interface matrix
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | C5.2.2 Set Points | Pass
radio | GMF-COMDRY-005 - Emergency Warning Cascade and Matrix | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 9 - CONDUCT FIRE FAN CONTROL PANEL AND BRIGADE INTERFACE TESTING
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018: The FFCP shall be incorporated into or located adjacent to the FBP and constructed in accordance with the FDCIE requirements in Clause 2.1
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | C6.6.0 Brigade Interface – FFCP | Pass
radio | GMF-COMDRY-001 Fire Detection Zone Commissioning | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 11 - CONDUCT FULL FUCNTIONAL FIRE TESTING AND WITNESSING
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.4-2018 – 100% test of installed devices, Interface testing to Trades:
label | ○ Mech Shutdowns
label | ○ Security trips
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | C7.0.0 Full Function Fire Test – Witnessing | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - T/W
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 12 - SPRINKLER INTERFACES FITTED OFF
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2015: Systems interface testing Prior to any interface testing check that all systems listed in the system interface schedule are complete and operable. This will involve checking that all systems interfaces to the FDAS
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | C5.2.2 Set Points | Pass
radio | C5.8.0 Modules Input/Output | Pass
radio | GMF-COMWET-001 - Sprinkler Zone Commissioning | Pass
radio | GMF-COMWET-002 - Flow Switch, Valve, Pump and Tank Indication | Pass
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 13 - OPERATORS MANUAL, INSTALLERS STATEMENTS, AS- INSTALLED DRAWINGS, LOGBOOK AVAILABLE TO SPECIFICATION REQUIREMENTS
label | ACCEPTANCE CRITERIA SPECIFIED - In House QA
label | ○ Correct documentation
label | ○ Referenced and submitted to PC
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
holdpoint | Signatures
checklist | GM-ITPS-006 Fire Brigade Inspection | itp |  |  |  |  | GM-ITPS-006 Fire Brigade Inspection
section | Details
checkpoint | 1 - FIRE INDICATOR PANEL LOCATION ACCEPTABLE
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018 Section 3.9 – FDCIE to be installed with .5m clearance either side of panel and 1.0m clearance in front of Panel.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 2 - HEAT DETECTORS TESTED
label | ACCEPTANCE CRITERIA SPECIFIED - 100% Test of installed devices.
label | ○ Correct location and spacings
label | ○ Correct zoning and description at FDCIE
label | ○ Correct interfaces triggered
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | GMF-ITP-005 | Pass,Reviewed
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 3 - SMOKE DETECTORS TESTED
label | ACCEPTANCE CRITERIA SPECIFIED - 100% Test of installed devices.
label | ○ Correct location and spacings
label | ○ Correct zoning and description at FDCIE
label | ○ Correct interfaces triggered
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | GMF-ITP-005 | Pass,Reviewed
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 4 - A / C INTERFACE TESTED
label | ACCEPTANCE CRITERIA SPECIFIED - GFAs triggered from correct zones/devices
label | ○ Interface Matrix referenced
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | GMF-ITP-005 | Pass,Reviewed
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 5 - MANUAL CALL POINTS TESTED
label | ACCEPTANCE CRITERIA SPECIFIED - 100% Test of installed devices.
label | ○ Correct location and spacings
label | ○ Correct zoning and description at FDCIE
label | ○ Correct interfaces triggered
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | GMF-ITP-005 | Pass,Reviewed
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6 - DOOR INTERFACES. BMS INDICATION
label | ACCEPTANCE CRITERIA SPECIFIED - GFAs triggered from correct zones/devices
label | ○ BMS correct to descriptions provided from trades
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | GMF-ITP-005 | Pass,Reviewed
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 7 - CERTIFICATES PROVIDED
label | ACCEPTANCE CRITERIA SPECIFIED - GMF-COMDOC-001, GMF-COMDOC-002, GMF-COMDOC-003, GMF-COMDOC-004
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - n/a
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - C
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
holdpoint | Signatures
checklist | GM-ITPS-007 Warranty Period | itp |  |  |  |  | GM-ITPS-007 Warranty Period
section | Details
checkpoint | 1 - PROVIDE CLIENT OPERATOR INSTRUCTIONS
label | ACCEPTANCE CRITERIA SPECIFIED - As and when required
label | QUALITY CONTROL - G/W
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 2 - TRAINING
label | ACCEPTANCE CRITERIA SPECIFIED - As and when required
label | QUALITY CONTROL - G/W/H
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 3 - MAINTENANCE PLAN
label | ACCEPTANCE CRITERIA SPECIFIED - As per spec. and quoted offer.
label | QUALITY CONTROL - G
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
holdpoint | Signatures
checklist | GM-ITPS-008 Sprinkler and Hydrant Design | itp |  |  |  |  | GM-ITPS-008 Sprinkler and Hydrant Design
section | Details
checkpoint | 1 - REVIEW CLIENTS DRAWING REGISTER
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 2 - REVIEW TENDER/CONSTRUCTION DRAWINGS
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 3 - REVIEW SPECIFICATION
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Construction Issued Drawings Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 4 - PREPARE SHOP DRAWINGS/LAYOUTS TO LATEST ARCHITECTURAL DRAWINGS
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 5 - DESIGNING PIPING LAYOUT
label | ACCEPTANCE CRITERIA SPECIFIED - SPRINKLERS: AS2118.1-2017 – Section 2; All new sprinkler systems shall be hydraulically designed in accordance with the requirements of Section 14 (hydraulic calculation of Sprinkler Systems)
label | ○ HYDRANTS: AS2419.1-2005 – Section 2; Fire Hydrant systems shall be compatible with the equipment and procedures employed by the attending Fire Brigade
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6 - PREPARE SPRINKLER VALVE DRAWINGS
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Section 8.2.3(b); All sprinkler stop valves shall be clearly labelled on this Sprinkler Block Plan
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Issued Drawings Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 7 - SUBMIT SHOP DRAWINGS FOR APPROVAL
label | ACCEPTANCE CRITERIA SPECIFIED - Clients Specifications In House QA
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Issued Drawings Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 8 - REVIEW RETURNED SHOP DRAWINGS
label | ACCEPTANCE CRITERIA SPECIFIED - In House QA
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Issued Drawings Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 9 - DISTRIBUTE "FOR CONSTRUCTION" DRAWINGS
label | ACCEPTANCE CRITERIA SPECIFIED - Per clients Specification
label | QUALITY CONTROL - G
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
holdpoint | Signatures
checklist | GM-ITPS-010 Fire Sprinkler Installation | itp |  |  |  |  | GM-ITPS-010 Fire Sprinkler Installation
section | Details
checkpoint | 1 - PIPING, DRAWING & CUTTING SHEETS CROSS CHECKED
label | ACCEPTANCE CRITERIA SPECIFIED - IN HOUSE
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Cut Sheet Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 2 - UNDERGROUND PIPING TO PUMP HOUSE FROM BOOSTER TO APPROVED LAYOUT & DETAIL
label | ACCEPTANCE CRITERIA SPECIFIED - IN HOUSE QA
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | DRAWING REFERENCE NUMBER - By others.
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 3 - PIPING & SIZE TO DESIGN CRITERIA
label | ACCEPTANCE CRITERIA SPECIFIED - SPRINKLERS: AS2118.1-2017 – Section 7.1; All pipes shall be supplied new and conform to the standards and relevant requirements.
label | ○ Latest Design Drawings
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.5 Pre – Commissioning | Pass
textbox | DRAWING REFERENCE NUMBER - Construction Issued Drawings Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 4 - MANUFACTURED FITTINGS TO DESIGN DETAILS
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118-2017 – Section 7.1; All fittings shall be supplied new and conform to the standards and relevant requirements.
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 5 - PIPEWORK SUPPORTED BY SEISMIC BRACING
label | ACCEPTANCE CRITERIA SPECIFIED - AS1170.4-2007 (R2018), clause 5.4.6 and section 8. AS1170.0-2002, AS5216-2018 & ETAG 001 PART 6, ANNEX 1.
textbox | DRAWING REFERENCE NUMBER - Seismic Design Drawings as supplied by Seismic Engineer.
label | ○ Construction Issued Drawings Number:
label | QUALITY CONTROL - A & I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6 - PIPING FIXED TO SPECIFIED REQUIREMENTS
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 - Section 7.8; Sprinkler supports shall be of the correct type installed in the correct locations and meet required load ratings for the pipe they are supporting.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.5 Pre – Commissioning | Pass
radio | W5.6 System Checks | Pass
textbox | DRAWING REFERENCE NUMBER - Construction Issued Drawings Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 7 - VALVES TO DESIGN DETAILS
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Section 8.2 – each installation shall have a main stop valve fitted, have clear identification and be shown on the Block plan.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.5 Pre – Commissioning | Pass
radio | W5.6 System Checks | Pass
label | DRAWING REFERENCE NUMBER - Construction Issued Drawings
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 8 - SPRINKLER INTERFACES FITTED OFF
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Appendix H – check to ensure alarm interfaces are fit off and tested prior to sign off
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.5 Pre – Commissioning | Pass
radio | W5.6 System Checks | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 9 - WITNESS DRY FIRE TESTING OF VALVE SETS AND MONITORING EQUIPMENT
label | ACCEPTANCE CRITERIA SPECIFIED - AS1670.1-2018, AS2118.1-2017 – Appendix H6 – system tested in accordance to the standard prior to witness testing with client or QFES.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W8.2.2 Witness Requirements | Pass
label | QUALITY CONTROL - W & I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 10 - SPRINKLER HEADS FITTED OFF
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Section 5 Approved and up to date Reflected Ceiling Plan (RCP)
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.6 System Checks | Pass
textbox | DRAWING REFERENCE NUMBER - Construction Issued Drawings
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 11 - OMISSION OF SPRINKLERS
label | ACCEPTANCE CRITERIA SPECIFIED - Fire Engineers Report (FER)
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.6 System Checks | Pass
textbox | DRAWING REFERENCE NUMBER - Fire Engineering Report.
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 12 - SPARE SPRINKLERS & KEY INSTALLED & TYPE CHECKED
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Section 6.7 – spare sprinklers of each type used in the installation shall be provided and located in a spares box.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.6 System Checks | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 13a - LABELS & BLOCK PLAN INSTALLED
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Section 8.3 – Block plans shall be provided, be of permanent design, water and fade resistant
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY:
date | DATE:
checkpoint | 13a - CONTROL ASSEMBLIES
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 - Section 8.1 – shall be located in a secure location and readily accessible to the fire brigade.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.6.2 Mechanical Checks: Automatic Control Valves | Pass
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 13b - LABELING OF CONTROL EQUIPMENT
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 - Section 3 (3.3.4) – shall be permanently affixed fade- resistant and water resistant
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 14 - FIRE RATING TO PENETRATIONS CORRECT AND LABELS AFFIXED
label | ACCEPTANCE CRITERIA SPECIFIED - BCA
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 15 - ACOUSTIC PENETRATION SEALED
label | ACCEPTANCE CRITERIA SPECIFIED - AS4072
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
holdpoint | Signatures
checklist | GM-ITPS-011 Fire Sprinkler System Commissioning | itp |  |  |  |  | GM-ITPS-011 Fire Sprinkler System Commissioning
section | Details
checkpoint | 1 - CHECK SPRINKLER HEADS ARE INSTALLED IN AN ENVIRONMENT IN WHICH THEY ARE SUITED
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Section 2.2 – heads installed to correct classification and spacing
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 2 - CHECK HYDRANTS ARE INSTALLED TO CODE AND HAVE REQUIRED CLEARENCES
label | ACCEPTANCE CRITERIA SPECIFIED - AS2419.1-2005 – Section 3.2 – Clearances differ when related to internal or external hydrants, ensure correct standards are implemented
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.2 State of the System | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 3 - AIR TEST INSTALLATION BEFORE WATER FILL
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Section 7.9.4 – hold 300 kPa for 30 minutes without a 10% loss.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | Hold Point Required: | Yes
radio | W5.4 System Filling and Venting | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
holdpoint | HOLD POINT
checkpoint | 4 - STATIC TEST INSTALLATION WITH WATER TO 1600KPA
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Section 7 (7.9.3) – system tested to 1.6MPa and holds pressure for 2 hours
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | Hold Point Required: | Yes
radio | W5.4 System Filling and Venting | Pass
radio | W5.4.1 Pressure Testing | Pass
radio | W5.5.2 Flushing Procedure | Pass
radio | W5.7 Static Completion Records | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 5 - CHECK & TEST WATER SUPPLY CAPACITY TO MEET SYSTEM DEMAND
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 - section 4.2.2.1 – capable of supplying the flow and pressure requirements of the sprinkler system.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W7.2 Flow Rate Measurement Tolerances | Pass
radio | W7.5 Preliminary Flow Rate Check | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6 - CHECK OPERATION OF PRESSURE SWITCHES TO DBS
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 - Appendix H4 – Test via 15mm test valve and record time taken to operate. Confirm with ASE monitoring service that alarm was received.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.6 System Checks | Pass
radio | W5.6.2 Mechanical Checks: Automatic Control Valves | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 6 - CHECK OPERATION OF PRESSURE SWITCHES FOR PUMP START
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Appendix H5.4 – P/Sw to be tested via dropping system pressure via test valve or remote test point.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.6 System Checks | Pass
radio | W5.6.2 Mechanical Checks: Automatic Control Valves | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY:
date | DATE:
checkpoint | 7 - CONDUCT 100% TESTING OF PRESSURE SWITCH, FLOW SWITCH & VALVE MONITOR
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 Appendix H6 – equipment to be tested to procedure set out in standard and in conjunction with Fire alarm workers.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W5.6 System Checks | Pass
radio | W5.6.2 Mechanical Checks: Automatic Control Valves | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 8 - CHECK PUMP PRESSURE AND FLOW REQUIREMENTS
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 - Section 14.9 – shall be capable of satisfying the flow and pressure requirements of the design +50kPa.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W7.2 Flow Rate Measurement Tolerances | Pass
radio | W7.5 Preliminary Flow Rate Check | Pass
label | QUALITY CONTROL - T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 9 - WITNESS TEST HOLD POINTS
label | ACCEPTANCE CRITERIA SPECIFIED - PIPE TESTING PROCEDURE
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | Hold Point Required: | Yes
radio | W5.7 Static Completion Records | Pass
label | QUALITY CONTROL - T & W
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
holdpoint | HOLD POINT
checkpoint | 10 - HYDROSTATIC SPRINKLER PIPE TEST
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 Appendix H & Section 7.9.3
label | ○ All new installations, trunk mains and water supply connections shall be capable of withstanding for a period of 2 h, without loss of pressure, a hydrostatic test pressure of 1600 kPa.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | Hold Point Required: | Yes
radio | W5.7 Static Completion Records | Pass
label | As per GM Fire ITPS-013 Sprinkler Pipe Testing.
label | QUALITY CONTROL - I & T
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
holdpoint | HOLD POINT
checkpoint | 11 - COMPLETE FORM 71 SPRINKLERS
label | ACCEPTANCE CRITERIA SPECIFIED - NCC 2019, AS2118
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W7.10 Commissioning Certification | Pass
label | QUALITY CONTROL - C
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 12 - COMPLETE FORM 71 HYDRANTS
label | ACCEPTANCE CRITERIA SPECIFIED - NCC 2019, AS2419
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION -
radio | W7.10 Commissioning Certification | Pass
label | QUALITY CONTROL - C
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 13 - OPERATORS MANUAL, INSTALLERS STATEMENT, AS- INSTALLED DRAWINGS, LOGBOOK AVAILABLE TO SPECIFICATION REQUIREMENTS
label | ACCEPTANCE CRITERIA SPECIFIED - In House QA
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | QUALITY CONTROL - C
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
holdpoint | Signatures
checklist | GM-ITPS-012 Fire Brigade Inspection Sprinklers and Hydrants | itp |  |  |  |  | GM-ITPS-012 Fire Brigade Inspection Sprinklers and Hydrants
section | Details
checkpoint | 1 - CHECK SPRINKLER HEADS ARE INSTALLED IN AN ENVIRONMENT IN WHICH THEY ARE SUITED
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Section 2.2 – heads installed to correct classification and spacing
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 2 - CHECK HYDRANTS ARE INSTALLED TO CODE AND HAVE REQUIRED CLEARENCES
label | ACCEPTANCE CRITERIA SPECIFIED - AS2419.1-2005 – Section 3.2 – Clearances differ when related to internal or external hydrants, ensure correct standards are implemented
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 3 - CHECK & TEST WATER SUPPLY CAPACITY TO MEET SYSTEM DEMAND
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 - section 4.2.2.1 – capable of supplying the flow and pressure requirements of the sprinkler system.
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 4 - CHECK OPERATION OF PRESSURE SWITCHES TO DBS
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 - Appendix H4 – Test via 15mm test valve and record time taken to operate. Confirm with ASE monitoring service that alarm was received.
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 5 - CHECK OPERATION OF PRESSURE SWITCHES FOR PUMP START
label | ACCEPTANCE CRITERIA SPECIFIED - AS2118.1-2017 – Appendix H5.4 – P/Sw to be tested via dropping system pressure via test valve or remote test point.
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
holdpoint | Signatures
checklist | GM-ITPS-013 Pressure Testing of Pipework | [5 empty] | GM-ITPS-013 Pressure Testing of Pipework
section | Details
checkpoint | Test Information
textbox | Maximum System design pressure:
textbox | Required test pressure:
label | STOP TEST IMMEDIATELY IF PRESSURE GAUGE REACHES 1650 kPa
radio | Hold Point Required: | Yes
textbox | Holding time:
textbox | Description of test configuration (attach sketch or piping and instrument diagram):
textbox | Test fluid:
textbox | Test Fluid Volume:
checkpoint | Test Equipment
textbox | Pressure Gauge:
textbox | Pressure Relief Valve:
textbox | Bleed valve:
checkpoint | Safety/Environmental Controls
textbox | SWMS Name:
radio | Have all workers reviewed and signed off on SWMS prior to commencing work? | Yes,No (do not commence works)
textbox | Safe disposal of test fluid:
textbox | Test area controls (barricades, signage, etc.):
textbox | Inspection requirements (before, during, and after the test):
radio | Is test equipment rated for test pressure: | Yes,No (do not commence works)
radio | Are end caps sufficiently tightened: | Yes,No (do not commence works)
textbox | Pressure Gauge reading at completion of test:
textbox | Any visible water leaks?:
textbox | Test Date and Time Commenced:
textbox | Test Date and Time Completed:
checkpoint | Approvals
textbox | Supervisor in charge of test:
textbox | Person conducting test:
date | Date:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
holdpoint | Signatures
checklist | GM-ITPS-014 In Slab Conduit | itp |  |  |  |  | GM-ITPS-014 In Slab Conduit
section | Details
checkpoint | 1 - CHECK CONDUITS ARE CORRECT TYPE, SIZE AND QUANTITY TO CRITERIA
label | ACCEPTANCE CRITERIA SPECIFIED - In-house QA
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
textbox | DRAWING REFERENCE NUMBER - Cut Sheet Drawing Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 2 - CHECK CONDUIT ROUTE IS AS SPECIFIED IN LAYOUT/ DESIGN CRITERIA
label | ACCEPTANCE CRITERIA SPECIFIED - Shop drawings (certified by an RPEQ engineer) are to be provided for each and every item required within 1170.4 Structural design actions – Earthquake actions in Australia.
label | COMMISSIONNIG CODES AND REQUIRED DOCUMENTATION - N/A
label | DRAWING REFERENCE NUMBER - By others.
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 3 - INSTALLATION, CONDUIT IS JOINED CORRECTLY
label | ACCEPTANCE CRITERIA SPECIFIED - Installation is in compliance with AS 1170.4 Structural design actions – Earthquake actions in Australia.
textbox | DRAWING REFERENCE NUMBER - Construction Issued Drawings Number:
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 4 - CONDUIT IS TIED IN
label | QUALITY CONTROL - I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | 5 - CONCRETE COVER IS IN PLACE
label | ACCEPTANCE CRITERIA SPECIFIED - General Technical Requirements – Services Ripley Sub-Acute Facility (RSAF) 2.2.3 - 9. All Fire services penetrations post concrete pours are to be immediately sealed with sheet metal cover plates (mastic or similar) to prevent water ingress. Plates to be fixed by use of nylon anchors or similar. Plates to remain in place and maintained until directed by Hutchinson Builders to remove.
label | DRAWING REFERENCE NUMBER - Seismic Design Drawings as supplied by Seismic Engineer.
textbox | Construction Issued Drawings Number:
label | QUALITY CONTROL - A & I
textbox | PERFORMED AND/OR WITNESSED BY: |  |  | GM / PC / CS / CL
date | DATE:
checkpoint | Hold Point Details
button | Hold Point Required: | Yes,No,Other:
textbox | Other (if applicable):
textbox | GM Sign Off - Name:
textbox | PC Sign Off - Name:
textbox | CS Sign Off - Name:
holdpoint | Signatures