## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP-141-RAIL-BRUNT-Track Formation - General Fill Rev.0 | itp |  |  |  |  | ITP-141-RAIL-BRUNT-Track Formation - General Fill Rev.0
section | 1. Referenced Documentation
checkpoint-no-status | 1. Referenced Documentation
label | Document Title: ITP-141-RAIL-BRUNT-Track Formation - General Fill
label | ITP Description: Track Formation - General Fill
label | Document Number (in Teambinder): MRP-0000-MRPA-ALT-ITP-00XX
label | Discipline (e.g. CIV/STR/RAIL): RAIL
label | Revision Number: 0
label | Revision Date: 14/03/2024
label | ITP created by: Mac Cameron
label | ITP approved for use by: Jon De Castro
checkpoint | 1.1 - Drawing Pack - Rail Track and Civil
label | Reference - GNC-MRP-ACD-GNC-XDM-1304-20230714_Brunt Rd _PKG-61
checkpoint | 1.2 - Metro Engineering Specifications - Earthworks & Formation Specification
label | Reference - L1-CHE-SPE-178 (VERSION 3)
checkpoint | 1.3 - Metro Engineering Specifications - Earthworks & Formation Standard
label | Reference - L1-CHE-STD-029 (VERSION 4)
checkpoint | 1.4 - Australian Standard - Methods of testing soils for engineering purposes
label | Reference - AS 1289
section | 2. Preliminaries - Materials
checkpoint | 2.1 - General Fill Material Conformance (1 of 2)
label | Reference - L1-CHE-SPE-178 - Clause 5.10.1. Australian Standard - AS1289
label | Acceptance Criteria - General Fill shall consist of suitable material that shall be compacted to a minimum characteristic value of density ratio 98%
label | ○ Refer to AS1289 for tests
label | Method - Visual, Review Test
label | Frequency - Once, for each material type - prior to works commencement
label | Category - HP
label | Responsibility - SE/PE
label | Verifying Documents - This ITP Signed Off
label | Attach: Supplier Material Conformance Certificate
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.2 - General Fill Material Conformance (2 of 2)
label | Reference - L1-CHE-SPE-178 - Clause 5.10.4.1. Table 1 AS 1289
label | Acceptance Criteria - General fill shall comply with the criteria listed in Table 1 (L1-CHE-SPE-178 - Clause 5.10.4.1.):
label | ○ Soaked CBR - 3% min nominal
label | ○ Plasticity Index 9-20%
label | ○ Dispersion (pin hole dispersity) - ND1/ND2
label | ○ Dispersion (Emerson class number of soil) - not to be class 1 or 2
label | ○ Collapse strain - to be agreed by MTM geotechnical engineer
label | ○ Free swell index - 2.5% max.
label | ○ Soil soluble salt content - 3%
label | ○ Organic content (dry weight) - 2% max.
label | – Refer to AS 1289 for Tests
label | Method - Visual, Review Test
label | Frequency - Once, for each material type - prior to works commencement
label | Category - HP
label | Responsibility - SE/PE
label | Verifying Documents - This ITP Signed Off
label | Attach: Supplier Material Conformance Certificate
holdpoint | AUTHORITY HOLDPOINT
section | 3. Preliminaries - Procedures & Documentation
checkpoint | 3.1 - Pre-Commencement of Fill Works
label | Reference - L1-CHE-SPE-178 - Clause 5.12.5. Table 7 AS1289 Tests
label | Acceptance Criteria - The Contractor shall not commence placing any fill on the prepared areas until the area has been reviewed by the Responsible Engineer.
label | Method - Visual Inspection
label | Frequency - Prior to commencement of fill works
label | Category - HP
label | Responsibility - SE/PE
label | Verifying Documents - This ITP Signed Off, MTM representative signoff
label | Attach: Site Photos
holdpoint | AUTHORITY HOLDPOINT
section | 4. Pre-Construction Activities
checkpoint | 4.1 - Approval of IFC drawings
label | Reference - GNC-MRP-ACD-GNC-XDM-1304-20230714_Brunt Rd _PKG-61
label | Acceptance Criteria - Approved IFC Drawings
label | Method - Document review and approval
label | Frequency - Prior to works commencing
label | Category - HP
label | Responsibility - SE/PE
label | Verifying Documents - This ITP Signed Off
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.2 - Survey Set Out
label | Reference - IFC Drawings
label | Acceptance Criteria - Set out pegs in place and clearly mark out limits of works.
label | Method - Visual Inspection
label | Frequency - Prior to commencement of fill works
label | Category - HP*
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP Signed Off
section | 5. Construction Activities
checkpoint | 5.1 - General Fill Preparation and Installation - For track constructed on embankment (1 of 2)
label | Reference - L1-CHE-SPE-178 - Clause 5.10.3.1. Australian Standard - AS1289 IFC Drawings.
label | Acceptance Criteria - Any surface on which fills are to be constructed shall be proof rolled.
label | ○ All layers of general fill material shall be compacted to a minimum characteristic value of density ratio of 98% (Standard Compaction)
label | ○ Where a layers to be constructed in fill it shall be constructed in uniform thickness not exceeding 200mm lose.
label | – One test per 1000m³
label | – Volume < 1000m³ atleast one set of tests shall be carried out
label | Method - Standard Compaction
label | Frequency - Each Lot
label | Category - HP
label | Responsibility - SE/PE
label | Verifying Documents - This ITP Signed Off
label | Attach: Compaction Test Report
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.2 - General Fill Preparation and Installation - For track constructed on embankment (2 of 2)
label | Reference - L1-CHE-SPE-178 - Clause 5.10.3.1. Australian Standard - AS1289 IFC Drawings.
label | Acceptance Criteria - General fill shall comply with the criteria listed in Table 1 (L1-CHE-SPE-178 - Clause 5.10.4.1.):
label | ○ Soaked CBR - 3% min nominal
label | ○ Plasticity Index 9-20%
label | ○ Dispersion (pin hole dispersity) - ND1/ND2
label | ○ Dispersion (Emerson class number of soil) - not to be class 1 or 2
label | ○ Collapse strain - to be agreed by MTM geotechnical engineer
label | ○ Free swell index - 2.5% max.
label | ○ Soil soluble salt content - 3%
label | ○ Organic content (dry weight) - 2% max.
label | Refer to AS 1289 for Tests
label | ○ One test per 1000m³
label | ○ Volume < 1000m³ atleast one set of tests shall be carried out
label | Method - Standard Compaction
label | Frequency - Each Lot
label | Category - HP
label | Responsibility - SE/PE
label | Verifying Documents - This ITP Signed Off
label | Attach: Test Report
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.3 - Proof rolling
label | Reference - L1-CHE-SPE-178 - Clause 5.4.1. and Clause 5.10.3.1.
label | Acceptance Criteria - Proof roll as per L1-CHE-SPE-178 - Clause 5.10.3.1.
label | Method - Proof roll
label | Frequency - Each Lot
label | Category - HP
label | Responsibility - SE/PE
label | Verifying Documents - This ITP Signed Off, MTM representative Signoff
label | Attach: Site Photos
holdpoint | AUTHORITY HOLDPOINT
section | 6. Post-Construction Activities
checkpoint | 6.1 - General Fill Finishing and Tolerances - For track constructed on embankment / Survey Conformance
label | Reference - L1-CHE-SPE-178 - Clause 5.10.6.1.
label | Acceptance Criteria - General fill on embankments shall be installed within +/- 40mm of approved design surface level
label | Method - Document Review
label | Frequency - Each Lot
label | Category - IP
label | Responsibility - SE/Surveyor
label | Verifying Documents - This ITP Signed Off
label | Attach: Survey Conformance Report
checkpoint | 6.2 - Non-conformance Report (NCR) Closure
label | Reference - MRPA Quality Management Plan
label | Acceptance Criteria - Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed.
label | Method - Document Review
label | Frequency - Once, prior to closure of this lot / element / Work area
label | Category - HP*
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP Signed Off
checkpoint | Final Inspection
note | On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
textbox | Name:
textbox | Position:
date | Date Completed:
signoff | Sign ITP