## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
f0db95d4-873f-4b29-a738-5cfcf82cc2a8 | checklist | 561482-ITP-001 - Switchboard Delivery and Electrical Installation | itp | 561482-ITP-001 - Switchboard Delivery and Electrical Installation
03d96dad-b6d7-4370-b6c2-e93fe8881bfc | section | SECTION 3 – RECEIVING INSPECTIONS
2efffef1-0820-489a-a6a5-a8ef55310afc | checkpoint | 3.1 - Inspection of Switchboard Cabinet Pieces prior to delivery to site
66cf0f2b-c4f6-5712-8603-9995cffecabb | note | Inspection Point: Quality Control Activity - Check overall condition. check connections for internal electrical components
f5de3d8d-3fd4-5dd3-b21f-5d174bcadf98 | note | Acceptance Criteria - Visual check and report any defects or areas of concern
1eb6bd9c-7eb9-52cc-a1e0-c8f886ed71a2 | note | Verifying Document - Email or NTE to report
40293768-b21d-5856-9a68-1db2e0561aa0 | note | Frequency - Once
46092adb-95d8-58bb-8945-e3af623f5e28 | note | Inspection Type (Visual, other) - Visual + Photograph
49ff573e-728b-515a-aab9-bb7e255b54b1 | note | Inspection: Key - C
60cdabeb-f92a-52f1-b54b-f0ccabf16018 | note | Inspection: By - IP/B
22693e5a-b5aa-489d-8715-95cc5cfa99b3 | checkpoint | 3.2 - Delivery of Switchboard materials to site
9475c1bb-facd-5bd7-8b17-7314d8a9ff0c | note | Inspection Point: Quality Control Activity - Check and verify that the switchboard materials have been delivered damage free
06932993-0987-5da5-b363-2973929cad60 | note | Acceptance Criteria - materials are damage free
02a8df15-dde5-5d9d-bd57-6bba8e2ed7c0 | note | Verifying Document - Material Delivery Docket
9b8c9801-5cfb-53ff-93ec-979fc764d56b | note | Frequency - Once
0a0a485e-0fb8-52ad-81b5-a04d059e86d7 | note | Inspection Type (Visual, other) - Visual + inspection
26797898-83e2-59b7-8727-af672ed37fb7 | note | Inspection: Key - C
4f306a28-36d9-5d94-ab2d-fc4516766fa2 | note | Inspection: By - IP
f7a26402-6f5f-472b-95ee-fc7d9079dc2e | section | SECTION 4 – IN-PROCESS INSPECTIONS
1f2080f5-1d90-4790-ac81-e4972c4e8419 | checkpoint | 4.1 - On-site assembly
67b391b3-ac14-5f31-8c1d-8cbee95df221 | note | Inspection Point: Quality Control Activity - Pre-Removal of required covers from Switchboard
701126a1-dd9d-5bda-a322-6a4215c4a696 | note | Acceptance Criteria - isolation of switchboard is proven
9abd8938-3952-52e2-ba3d-6d5e8726bc49 | note | Verifying Document - on site testing, isolation tags in place
ff96fd02-43d6-557d-8b84-6c14ec485f97 | note | Frequency - once
872b69f4-29ea-58d5-bcb5-90accf923cac | note | Inspection Type (Visual, other) - Visual
1f013e52-ec05-5e16-b3e1-37ded06fc6cf | note | Inspection: Key - I
d08ecc5b-3264-5416-9a2a-32c5a584b28c | note | Inspection: By - IP
e3d78801-3b21-4d4a-b872-c6a249e87ad4 | checkpoint | 4.2 - On-site assembly
b6b8ecec-8e2a-5fbc-9eb2-b6aba0b2f912 | note | Inspection Point: Quality Control Activity - Switchboard exterior panels removed as required
1cd50ba0-40b5-5b3e-99de-139bbb2b9af7 | note | Acceptance Criteria - work area secured, all voltage sources isolated. no signs of degradation on switchboard.
83982f87-e96d-57ec-a21f-1347a0155842 | note | Verifying Document - Testing, photos as required
76e7d5eb-2056-5178-b96a-269df23f2b63 | note | Frequency - once
da655707-1ef0-5ffb-bc62-3682c330c080 | note | Inspection Type (Visual, other) - Visual + Photograph
9482329f-fc59-5e4a-8578-ed030df91ce2 | note | Inspection: Key - I
7a5be0f8-08d8-5588-9e72-369b6462ca15 | note | Inspection: By - IP
8f070261-c725-4c63-97db-74d9b200b889 | checkpoint | 4.3 - Connection of new Generator Change-over cabinet.
99ef6b58-70eb-5d61-99b9-bfb209856466 | note | Inspection Point: Quality Control Activity - connections of electrical cabling/bus bars.
a796355a-6445-52c0-948f-68c719b7bb7c | note | Acceptance Criteria - Cabling/busbars connected correctly, insulation resistance between conductors acceptable.
9b2e8732-e108-5fc9-b59c-6e316c559310 | note | Verifying Document - Switchboard Acceptance Test. C.O.C from Switchboard Manufacturers.
33786f13-e2df-5d9d-b64f-495930bb8337 | note | Frequency - Once
014f67bb-b2bc-52e6-83f2-8999ebe8f114 | note | Inspection Type (Visual, other) - Visual + Photograph
d89f3fef-e7d2-527e-b249-b28b571d0495 | note | Inspection: Key - I
180afe3e-3065-569a-8f7a-5c30cca4c86e | note | Inspection: By - IP
bc9903e8-8ef2-45bc-82d3-ef25dffc347b | checkpoint | 4.4 - Re-Energizing of switchboard
96587c88-e25f-57c7-8629-fbda9608bc0a | note | Inspection Point: Quality Control Activity - Switchboard work completed.
c14e1f3c-fa3f-5fc1-a965-942685ee31d7 | note | Acceptance Criteria - Switchboard upgrades completed. testing completed, interlocks between main switch and generator switch tested and verified, phase rotation confirmed
4f23c6f5-24ec-53ce-b555-efe529b88908 | note | Verifying Document - Switchboard C.O.C, instrument test of supply mains.
31f675b5-f6de-526e-ba0c-4ea69c70f370 | note | Frequency - once
ce7b4382-2ac9-5cf0-9115-2b9a0ce223ca | note | Inspection Type (Visual, other) - Visual + Inspection
1b472704-4f0a-5f1d-b211-4b7136b2cb5e | note | Inspection: Key - I
e0c87eed-6474-55e1-a86d-9aaa77357573 | note | Inspection: By - IP
2cf05069-8ace-4579-bb29-5d50d0be125c | checkpoint | 4.5 - Submission/review/appr oval of the Level 2 FD
45546cc8-64fc-54ae-97da-14b18be19e31 | note | Inspection Point: Quality Control Activity - Software functionality meets expectations
8b7df376-1d2d-56d5-ab20-71d5c05ad662 | note | Acceptance Criteria - Approval from consultant
7241d513-2778-5351-ad63-194763a4638b | note | Verifying Document - NTC
891b2744-6cd5-55c1-b301-7baa67d521bd | note | Frequency - Once
6af9ef14-3237-58fd-a947-5ababa2b77fe | note | Inspection Type (Visual, other) - Visual
c8a4dacb-daa8-5891-a6e4-5cd4720d1957 | note | Inspection: Key - I
193ddabe-c026-5779-a445-666fca1212b2 | note | Inspection: By - IP
04e4ede5-9076-4eeb-ab18-105bff22ca76 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
8cea6a96-d312-4232-bef7-528edf10d115 | checkpoint | 5.1 - Switchboard
118d1e96-ff38-537f-b516-a61ddb46b57f | note | Inspection Point: Quality Control Activity - Assembled, inspection carried out and approved
c4c31e54-0234-5973-b1a3-c1476f7f5941 | note | Acceptance Criteria - Electrical Testing completed, all covers in place and secured.
960a08b5-1aa0-528a-bae2-a9847c35ec52 | note | ○ All bolts present.
a291fe3d-27cc-5f26-be43-b601f128ee19 | note | ○ R.O.I issued by electrical inspector.
96308669-9641-5e44-8054-7aaac5952947 | note | Verifying Document - Switchboard acceptance test sheet.
b064dc5c-1dce-5fe7-8b9d-50cc7f194439 | note | Frequency - once
af5d213c-b87f-525d-9915-e78d715997b3 | note | Inspection Type (Visual, other) - Visual + Document
7ead4aa6-528a-577e-bf03-880e8b536eed | note | Inspection: Key - I
a3c2cac1-7498-584a-a18d-fdfaaddfd9c8 | note | Inspection: By - IP
5694bb18-1ee9-4546-8f2e-7f5411470860 | checklist | 561482-ITP-002.2 - VSD2 Delivery and Installation | itp | 561482-ITP-002.2 - VSD2 Delivery and Installation
e8a29596-f907-47ed-a3ff-d56447e70a97 | section | SECTION 3 – RECEIVING INSPECTIONS
0a620231-31ea-4fc1-84ab-6bf05ae7c91b | checkpoint | 3.1 - Inspection of VSD prior to delivery to site
b711e90d-6a9d-5236-b488-f29469f05207 | note | Inspection Point: Quality Control Activity - Check overall condition of packaging, noting any obvious signs of damage, Check rating of drives is correct.
02c259ec-6d19-59f1-882c-00756d6433e8 | note | Acceptance Criteria - Visual check and report any defects or areas of concern
31b328e5-7da7-55a3-a2b9-45f4d3690541 | note | Frequency - Once
2dd46d13-49ea-5aa2-965a-2cafdc117f89 | note | Inspection Type (Visual, other) - Visual + Photograph
d40e8e6b-7597-52b2-a5ba-394883a07183 | note | Inspection: Key - C
042a200f-d3fc-5163-bb83-d649db9607a1 | note | Inspection: By - IP/B
cc720413-a9a4-4318-adee-e3a6aca0763c | checkpoint | 3.2 - Delivery of VSD to Site
e926fcc3-1e48-5f5b-910d-f0d7dec1a0aa | note | Inspection Point: Quality Control Activity - Check and verify that correct VSD are delivered and that drives are undamaged
0a701dce-4779-5117-bb11-4bdd7637b32d | note | Acceptance Criteria - VSD are damage free
45123216-e665-523d-bb78-8c965ac2b79c | note | Verifying Document - VSD Delivery documents
927c450b-6da0-5c1a-9cdc-719efaee4d31 | note | Frequency - Once
a4cc56e3-d443-5dc3-8c12-ff505199ad2d | note | Inspection Type (Visual, other) - Visual
ba9fadfb-b4d5-5cab-8e26-384a4c824a43 | note | Inspection: Key - C
fc00601b-667b-5a99-aa53-6d6a11b9319d | note | Inspection: By - IP
bea26331-ec78-4063-b365-ba695662a850 | section | SECTION 4 – IN-PROCESS INSPECTIONS
f205976b-ce14-4e06-af56-87887192ec61 | checkpoint | 4.1 - On-site assembly of mounting Frame
9e6ac5d6-01d5-56a6-afa1-d07750a9505a | note | Inspection Point: Quality Control Activity - materials for frame delivered to site
8a1d6bb1-f172-53b8-87a9-de6461b3d109 | note | Acceptance Criteria - Correct materials on site, protective coatings correct.
963bc178-819b-5a4e-9ec6-1ad00658b112 | note | Verifying Document - Delivery Docket for Materials
cca45854-eb98-5b78-ab6a-26da9eb8e526 | note | Frequency - Once
0e4d0793-b2f2-5310-a009-f9bfff14386c | note | Inspection Type (Visual, other) - Visual
0107fcc8-da26-52dc-9a40-a692cfdd3883 | note | Inspection: Key - I
6a14d11b-1688-5bac-9912-5bc0c11831b7 | note | Inspection: By - IP
9204f331-acd2-4094-8b87-4b7f87a2d091 | checkpoint | 4.2 - Assembly and mounting of Frame
b369c196-c6b3-516a-aaa6-3bbbe3b32442 | note | Inspection Point: Quality Control Activity - Frame Built and bolted to Ground.
54b69342-6b74-5cc3-b1ba-14311fa557f5 | note | Acceptance Criteria - Frame built and Securely attached to ground, minimal flex/ movement when force applied.
c7fe9ac8-f3e6-525c-9c8f-b3426d9b6238 | note | Verifying Document - N/a
045cfaa9-854e-50c0-a255-035130966748 | note | Frequency - Once
1b8549f9-5afb-5129-a784-3024459bc94a | note | Inspection Type (Visual, other) - Visual + Photograph
67ee5aba-98c9-5be6-b794-c23ce8bafb7b | note | Inspection: Key - I
c47c6f63-4d23-5231-be5d-360ffbf07e53 | note | Inspection: By - IP
29e6913e-ce98-4b6a-a993-5e65066dc34b | checkpoint | 4.3 - Mounting of VSD to Frame
21f90df7-b9d5-506a-a2d1-6d989977ef08 | note | Inspection Point: Quality Control Activity - VSD Mounted to frame
5e8062da-6c36-5337-b1fd-c84eb48c1048 | note | Acceptance Criteria - VSD Mounted satisfactorily, bolts tight, washers and spring washers present, S/S bolts and fixings used.
b4e55954-9dbf-521b-927a-49a3d24038fd | note | Verifying Document - VSD Inspection Sheets.
544c1703-1944-5dec-a858-315fe9b71eaf | note | Frequency - Once
34b38009-d74b-5a01-a132-ba6b0774bf59 | note | Inspection Type (Visual, other) - Visual + Photograph
43531518-fe1d-5dca-b08d-32a016d059bf | note | Inspection: Key - I
7bb7a2bc-020e-5ec1-9242-234ec1c4889b | note | Inspection: By - IP
f10462aa-c656-45f9-9e5d-0acf00f303b2 | checkpoint | 4.4 - Installation of supply cables to VSD
1535154d-ff9e-53ec-b063-ee730876a191 | note | Inspection Point: Quality Control Activity - Cables installed, not terminated into VSDs or switchboard
a3db684f-8908-5fb3-94a4-473619c760cd | note | Acceptance Criteria - Correct Cables installed, suitable for full load plus 20 percent of VSD, insulation resistance acceptable
3138948c-61b0-5644-8600-e1f25aeac078 | note | Verifying Document - VSD Cable Test Sheets.
bcef6a0f-129b-58fc-acb2-839efce275e7 | note | Frequency - Once
dcb21b52-fd27-5cae-ae38-c954de75998f | note | Inspection Type (Visual, other) - Visual + Inspection
88657b4e-be97-521b-b5a0-3ca40519b06c | note | Inspection: Key - I
2ee048d6-a97a-54ef-a41b-a01e4f98e8ee | note | Inspection: By - IP
93a3b3cc-891c-43bf-8769-18b34b4ed940 | checkpoint | 4.5 - Installation of Output Cables From VSD to Motors
7c179e9b-3e5c-5e25-b9e8-20e5d923f21b | note | Inspection Point: Quality Control Activity - Cables installed, not terminated at motors or VSD
1d2f3cb5-df59-5d9f-929e-42fd43efad14 | note | Acceptance Criteria - Correct Cables installed, suitable for full load of motor plus 20 percent, insulation resistance acceptable
87406536-8b5a-56f7-8b5e-eea0d8a03acd | note | Verifying Document - VSD Cable Test Sheets.
1ef91cec-2858-5498-90ff-05328fe28de8 | note | Frequency - Once
a971308f-5280-55f0-8203-1090d3b85a9c | note | Inspection Type (Visual, other) - Visual + Inspection
d9a40b50-ab69-567e-95fd-a56648fc48ca | note | Inspection: Key - I
32becccc-2120-525a-ad21-4302f639487f | note | Inspection: By - IP
6834322a-b86f-429a-98da-f4df8a909c4b | checkpoint | 4.6 - Termination of cabling to VSD
26a3b432-9d6a-5737-b5a7-c522ebb54082 | note | Inspection Point: Quality Control Activity - Cables terminated into VSD
5d656b39-29c4-59a9-8870-457de0c65db5 | note | Acceptance Criteria - Correct Cables installed, terminals tightened to correct torque, cables prepared correctly. cable earths and screens fit off correctly.
62df3caf-cad4-571c-b909-f06301772524 | note | Verifying Document - VSD Cable Test Sheets.
bfa2cf51-8c8b-5978-aa38-238f8d45da16 | note | Frequency - Once
22ce3704-402e-5179-896c-6c7e2e643482 | note | Inspection Type (Visual, other) - Visual + Inspection
398f1e97-c4ee-5e87-bfde-d1abf15e3b20 | note | Inspection: Key - I
46c2d451-8ada-5aac-aa38-f9e1664803d8 | note | Inspection: By - IP
1f50617e-7bec-4c3a-bfbe-c829c347580b | checkpoint | 4.7 - Termination of cabling to Switchboard
d4e50742-f7e8-5d3c-a869-0efee2101bb4 | note | Inspection Point: Quality Control Activity - Cables fit off at Switchboard.
a6cc7cfe-3668-5d8e-b230-46227e11ab09 | note | Acceptance Criteria - Correct Cables installed, terminals tightened to correct torque, cables prepared correctly. cable earths and screens fit off correctly.
48f8a4f7-1048-5a44-84d4-18fca3238ce6 | note | Verifying Document - VSD Cable Test Sheets.
252dd7fe-78bd-5889-9a36-704e9c88372c | note | Frequency - Once
baccd78e-cc27-5072-be57-ca0d99278868 | note | Inspection Type (Visual, other) - Visual + Inspection
a1045ebd-0251-529c-951a-5df52c876793 | note | Inspection: Key - I
3991e6b9-d724-50c9-8fd4-f24e894327ec | note | Inspection: By - IP
76b886d0-0907-42cf-b5d0-5ad396911d95 | checkpoint | 4.8 - Verification of motors electrically
245e2e0b-14b8-5113-99f7-7194c0a6d8f4 | note | Inspection Point: Quality Control Activity - Cables installed, not terminated into motor
ed25256b-35e8-51e6-9357-48ff7f3f1358 | note | Acceptance Criteria - Correct motors installed. insulation resistance verified, winding configuration confirmed against nameplate.
4cf608b0-6068-53e5-ada2-693ba7c6ef66 | note | Verifying Document - VSD Cable Test Sheets.
32b18451-a516-5189-abb3-6ee21b707ce9 | note | Frequency - Once
34e2290e-ecf2-5122-8b61-f3b8e65fcef2 | note | Inspection Type (Visual, other) - Visual + Inspection
41eea300-a2a7-5112-bcdc-98c9b57d2327 | note | Inspection: Key - I
09e9a904-09a4-5572-bbcb-122104f75108 | note | Inspection: By - IP
be9dc99c-23fe-448b-9e37-6b57af62aa8e | checkpoint | 4.9 - Termination of cabling to Motor
1d466e69-3466-5035-8b99-b88a610867b6 | note | Inspection Point: Quality Control Activity - Cables fit off at Motor
6cf886a8-10b1-5ade-9402-09c1bb8cebfe | note | Acceptance Criteria - Cables Lugged off correctly, terminals tightened to correct torque
ebe0d2ac-3887-5f19-b621-f24e8446c473 | note | Verifying Document - Motor Inspection Sheets
951e699e-3795-5857-b0a7-c56875b5538c | note | Frequency - Once
5e4a1f89-b885-5cc9-8601-6c97aa4e0aac | note | Inspection Type (Visual, other) - Visual + Photograph
675d23d1-71e0-5f0b-b8d2-56c7532a234f | note | Inspection: Key - I
eb1d5199-2c86-59d9-aad2-b5d98aeac4c4 | note | Inspection: By - IP
97679dd4-ad5c-44c8-9576-4d18e20ddb37 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
1055a22c-979f-4231-bd9f-8ca2a1678a13 | checkpoint | 5.1 - VSD
8ef2c718-a6af-5000-851f-2549b9a7b8b8 | note | Inspection Point: Quality Control Activity - VSD Energised and set up, motor nameplate data entered, protections set, Labels attached
9420ca62-f273-5ac0-b52e-780bd4501906 | note | Acceptance Criteria - VSD parameters set correctly, inputs set up as per drawings. analog i/o set correctly and verified to plc
2ced564d-e6da-547c-8943-2f7ce7fdcdb1 | note | Verifying Document - VSD ITR Document
886d4fba-5bec-5b8d-8d2c-20b921559b9c | note | Frequency - Once
05f87880-7060-5e87-b8a7-c7d771bd6bb3 | note | Inspection Type (Visual, other) - Visual + Document
846488cd-1f81-5d7c-b284-c8a8809e53ee | note | Inspection: Key - I
52e42ff7-d3af-5902-9617-ca2c3f72fcc5 | note | Inspection: By - IP
c1cd517c-531e-4ce2-a647-93184ee752ac | checkpoint | 5.2 - Motors
ab7200cf-9c69-5c6c-9b01-f724b367cb98 | note | Inspection Point: Quality Control Activity - Assembled and in position, inspection carried out and approved
1d5de886-0223-51dc-ba4e-0cc8aec81f1a | note | Acceptance Criteria - Motors Tested, rotation direction confirmed, pumps operating as intended.
73c3ec5a-62ca-5ff7-986b-d043a7e4abf4 | note | Verifying Document - Motor inspection Sheet
49ce9f86-5dba-5bad-8f46-d729706e9907 | note | Frequency - Once
c57cdebc-e5d2-5d3b-b02f-c6c61e6f59ea | note | Inspection Type (Visual, other) - Visual + Document
3ff45640-1380-5d8e-add6-16a6222bce0c | note | Inspection: Key - I
6ff626d5-607a-5a38-a7cb-4e3d643d0cbb | note | Inspection: By - IP
b45d75dd-4d34-45f0-98ee-64636958e098 | checklist | 561482-ITP-002.3 - VSD Delivery and Installation | itp | 561482-ITP-002.3 - VSD Delivery and Installation
2393c0ea-dfcc-417b-80be-76492c5f4ae7 | section | SECTION 3 – RECEIVING INSPECTIONS
02301741-977c-4570-9026-ec4968bbc621 | checkpoint | 3.1 - Inspection of VSD prior to delivery to site
e638b967-be43-5a38-ab2f-dbe16a4f525e | note | Inspection Point: Quality Control Activity - Check overall condition of packaging, noting any obvious signs of damage, Check rating of drives is correct.
7014054f-75ed-587b-a7ac-598ecc501cbe | note | Acceptance Criteria - Visual check and report any defects or areas of concern
d9c9d92d-ea71-5879-8998-27af8cee43b7 | note | Frequency - Once
ad593165-5832-58d8-8591-810e1f29878a | note | Inspection Type (Visual, other) - Visual + Photograph
6314ffff-d3e0-578a-a460-1a8da9d5f399 | note | Inspection: Key - C
439e7077-358c-50d2-89cc-ba0645d453e1 | note | Inspection: By - IP/B
d9f1c287-66b4-449f-b4e6-da9e8531f985 | checkpoint | 3.2 - Delivery of VSD to Site
64beadac-c488-572e-a976-aab39d24e57a | note | Inspection Point: Quality Control Activity - Check and verify that correct VSD are delivered and that drives are undamaged
545419a7-4392-5834-94de-10f8849cf5e9 | note | Acceptance Criteria - VSD are damage free
fe10d294-beea-5df8-823b-1e65ad6c317c | note | Verifying Document - VSD Delivery documents
87e165a1-cab3-5270-a69c-4ca2958cd900 | note | Frequency - Once
6510bdfd-4d32-5c51-a90b-87d397f09306 | note | Inspection Type (Visual, other) - Visual
6f6a1a49-059d-556d-9bf0-96fe87167e60 | note | Inspection: Key - C
65383a29-6ea4-5ff4-ab4d-4ed24cd1a9a5 | note | Inspection: By - IP
2f564d66-eb7f-4589-8d3a-78006ef4cf80 | section | SECTION 4 – IN-PROCESS INSPECTIONS
e00cc8a3-f665-4563-8c32-97513f1aa4a7 | checkpoint | 4.1 - On-site assembly of mounting Frame
0fb44e38-7e46-5430-b5eb-f17df98ef34c | note | Inspection Point: Quality Control Activity - materials for frame delivered to site
42f1a079-321f-5de4-9271-6e357b02ae91 | note | Acceptance Criteria - Correct materials on site, protective coatings correct.
254aa36f-6ae9-5712-963f-ef9ae173b91e | note | Verifying Document - Delivery Docket for Materials
e9f60b3a-1bf1-5f95-8778-56c400aefc77 | note | Frequency - Once
619c9776-feb0-5f00-97ef-414148aca636 | note | Inspection Type (Visual, other) - Visual
36db81c9-cb50-570f-9997-16641910ba65 | note | Inspection: Key - I
17682ce3-557f-566d-bcda-cfb9356bd3c2 | note | Inspection: By - IP
a110b86c-a8fb-4247-a6d5-23c11aa9e903 | checkpoint | 4.2 - Assembly and mounting of Frame
90aab059-67d9-5a0d-86ca-32dd766aed31 | note | Inspection Point: Quality Control Activity - Frame Built and bolted to Ground.
6019cbfd-b08e-5e27-b39e-1b11938b77b6 | note | Acceptance Criteria - Frame built and Securely attached to ground, minimal flex/ movement when force applied.
a8eb00d2-3b03-55d0-aa0d-15bba2e4130a | note | Verifying Document - N/a
570a059a-9265-5adf-9018-0127d868235d | note | Frequency - Once
9ab30dc7-7f36-5013-8b4c-2562d72e57b9 | note | Inspection Type (Visual, other) - Visual + Photograph
6fff6911-0fae-5502-9986-7c2f85d49c0c | note | Inspection: Key - I
2e0011e5-8bff-5726-9b52-ae5d7296bc24 | note | Inspection: By - IP
7f25864b-cfc7-4106-ac16-1ea478271a3a | checkpoint | 4.3 - Mounting of VSD to Frame
e9f0c403-ba0e-59e4-ae98-aa3fb5309aeb | note | Inspection Point: Quality Control Activity - VSDs Mounted to frame
738a8ff6-8e25-5ef1-91d2-c84e897c09dc | note | Acceptance Criteria - VSD Mounted satisfactorily, bolts tight, washers and spring washers present, S/S bolts and fixings used.
df81cc09-cd70-5c72-b6c1-57dbd8e88eb9 | note | Verifying Document - VSD Inspection Sheets.
35153245-d380-5dd4-b5e7-4452d543183c | note | Frequency - Once
75f9c373-27e7-5798-9399-d87c4a7e6b49 | note | Inspection Type (Visual, other) - Visual + Photograph
acc4a448-3560-57cb-807e-fc8486e840c0 | note | Inspection: Key - I
6e390a68-2210-5a96-bbc5-fa45c5b996b6 | note | Inspection: By - IP
85a6bf5d-9b19-4899-bc8b-b03edafaea00 | checkpoint | 4.4 - Installation of supply cables to VSD
acbc88d1-faa8-5399-ac5a-2cb799b4e6c3 | note | Inspection Point: Quality Control Activity - Cables installed, not terminated into VSD or switchboard
ebffbd7f-f728-5ec4-89f3-e887934c0324 | note | Acceptance Criteria - Correct Cables installed, suitable for full load plus 20 percent of VSD, insulation resistance acceptable
0accc637-1d48-58b1-86a6-7d1c0cd34d6f | note | Verifying Document - VSD Cable Test Sheets.
13396456-6553-5c40-aac6-b6d5eae29bb4 | note | Frequency - Once
b196647e-0413-5efd-92d5-6e8be52688dc | note | Inspection Type (Visual, other) - Visual + Inspection
410070d9-b730-5ebe-a1ae-d826fd3b2809 | note | Inspection: Key - I
fd0bdc50-73e9-5cb5-ae6e-09d82d6c10b0 | note | Inspection: By - IP
59470769-4953-47e1-8289-c613cdaa7a17 | checkpoint | 4.5 - Installation of Output Cables From VSD to Motors
07d1e711-a0af-5b80-b10e-bc42da38374c | note | Inspection Point: Quality Control Activity - Cables installed, not terminated at motors or VSD
a0ccb903-93e9-501d-82e6-b08d114104ce | note | Acceptance Criteria - Correct Cables installed, suitable for full load of motor plus 20 percent, insulation resistance acceptable
d2368aa1-d892-5de8-9bb6-7abf419380c2 | note | Verifying Document - VSD Cable Test Sheets.
7b2701f4-05de-57ff-99ea-7a3679f67d13 | note | Frequency - Once
f52baad8-e62c-5f77-ab58-0970824f275b | note | Inspection Type (Visual, other) - Visual + Inspection
8a94a4f6-05e2-5c2e-9d09-6cdcaab92e5a | note | Inspection: Key - I
ceede671-448f-59db-9ca1-0d86bad5b02c | note | Inspection: By - IP
59850520-005d-4fed-896f-3729b6d7dffc | checkpoint | 4.6 - Termination of cabling to VSD
f17d8d90-f783-5d25-b66e-3be2f6862d5e | note | Inspection Point: Quality Control Activity - Cables terminated into VSD
925ad370-5c9e-51ec-881f-2bca7f6df065 | note | Acceptance Criteria - Correct Cables installed, terminals tightened to correct torque, cables prepared correctly. cable earths and screens fit off correctly.
a6650d2d-90d5-5b9b-9e81-7ade985660d8 | note | Verifying Document - VSD Cable Test Sheets.
bacf4799-c741-513a-bfca-c42f987287e1 | note | Frequency - Once
67fc7851-baa4-5cd1-a89f-9e6c46db6e15 | note | Inspection Type (Visual, other) - Visual + Inspection
194f6f70-691f-54e2-a9cd-5485b6d436a1 | note | Inspection: Key - I
a527cc14-881a-5182-a073-e5514b23093d | note | Inspection: By - IP
2ceeb426-5c7d-499a-b151-110aa422135f | checkpoint | 4.7 - Termination of cabling to Switchboard
95fdd7db-4547-51cc-813e-2aff2ec6cbde | note | Inspection Point: Quality Control Activity - Cables fit off at Switchboard.
568e280e-e868-56c1-98ae-6f4237d90ac2 | note | Acceptance Criteria - Correct Cables installed, terminals tightened to correct torque, cables prepared correctly. Cable earths and screens fit off correctly.
96c74336-f0f8-518a-b748-bf5192fb231e | note | Verifying Document - VSD Cable Test Sheets.
d398e7b9-1653-5252-b979-84781a90dff8 | note | Frequency - Once
be9c959c-9a07-541d-80e1-829ff093f858 | note | Inspection Type (Visual, other) - Visual + Inspection
4997927f-3e18-512a-93f1-57e94ab7b21d | note | Inspection: Key - I
10bb3b16-ef05-5dcf-b6dd-e731f606dad6 | note | Inspection: By - IP
f57b317d-5672-4e55-ac06-d35bb9f208fd | checkpoint | 4.8 - Verification of motors electrically
c3cb97fd-358a-57d9-93ba-9aa42ee9dbb6 | note | Inspection Point: Quality Control Activity - Cables installed, not terminated into motor
10b5cbda-8f33-5b22-8fa4-38cbb7b5be2b | note | Acceptance Criteria - Correct motors installed. insulation resistance verified, winding configuration confirmed against nameplate.
741911a7-fb1e-5493-9ad9-bb57074a662c | note | Verifying Document - VSD Cable Test Sheets.
aad5d5bb-4923-595c-8559-f7bb99cd3267 | note | Frequency - Once
63dbc81d-e794-5736-85fb-a5706177f0ac | note | Inspection Type (Visual, other) - Visual + Inspection
2929316c-7df4-5011-97c1-5b5b90c000bf | note | Inspection: Key - I
11e5ebdb-8850-52f3-b2ac-3598774fec99 | note | Inspection: By - IP
317e4470-5aba-4e78-99c9-2d0cc15c8595 | checkpoint | 4.9 - Termination of cabling to Motor
3ca3b56b-5d6c-52b5-9229-46bb5d120b13 | note | Inspection Point: Quality Control Activity - Cables fit off at Motor
db1c9caa-ce99-5d55-a4b3-4799bab29858 | note | Acceptance Criteria - Cables Lugged off correctly, terminals tightened to correct torque
794a234b-4103-5a9d-b34d-5c586a6a1746 | note | Verifying Document - Motor Inspection Sheets
c00d6a0e-1412-5aa3-b0f7-fe326c32bf95 | note | Frequency - Once
0bc28977-659b-55a2-96e2-6ebea1733300 | note | Inspection Type (Visual, other) - Visual + Photograph
4302563c-2b41-50da-ae1c-e23361c80aeb | note | Inspection: Key - I
a86151a8-2e1f-504a-898b-238126ee6f64 | note | Inspection: By - IP
ff38ecbb-be6b-4e07-a3b7-86e0e42f4e43 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
1e8ddea4-4883-4d29-ba6c-14385ed7bc68 | checkpoint | 5.1 - VSD
e621889d-32c0-5ec1-bd92-62f18fdd4e1d | note | Inspection Point: Quality Control Activity - VSD Energised and set up, motor nameplate data entered, protections set, Labels attached
23c379e9-4792-5fcb-b289-842a66b469ad | note | Acceptance Criteria - VSD parameters set correctly, inputs set up as per drawings. analog i/o set correctly and verified to plc
91102be6-ef4d-5e9a-8255-48d8833a0b1b | note | Verifying Document - Switchboard acceptance test sheet.
cd706da6-5285-5f12-b394-26993e531161 | note | Frequency - Once
b8adc75e-77a2-5fd5-a6f9-e311ea4dda96 | note | Inspection Type (Visual, other) - Visual + Document
3745b8aa-ee6f-5426-901a-a7cd72daae21 | note | Inspection: Key - I
48eae12f-2423-5d4c-97f8-9b72593dcff2 | note | Inspection: By - IP
b5dda0fb-6adf-480d-8233-dbb814a694cc | checkpoint | 5.2 - Motors
26e71cf3-817a-504e-b860-ce675f96bf59 | note | Inspection Point: Quality Control Activity - Assembled and in position, inspection carried out and approved
3cda3185-0ba5-5196-8275-baeb28a765ed | note | Acceptance Criteria - Motors Tested, rotation direction confirmed, pumps operating as intended.
3cb5c9d3-0eaa-5fe3-a8d4-dc872bbbcb19 | note | Verifying Document - Motor inspection Sheet
f3082fc4-7eaa-5f55-8ea1-3dbe2c683ee1 | note | Frequency - Once
8b710a90-5f40-5869-86f7-cc5a04481ddb | note | Inspection Type (Visual, other) - Visual + Document
efa02dad-cd6c-5d02-b43f-3e16694c3dc8 | note | Inspection: Key - I
b1af8750-ea34-5257-bb72-03a5e0c85a4f | note | Inspection: By - IP
288bb8ed-b7cb-4300-9722-89f072634305 | checklist | 561482-ITP-003.1 - Wet Well Wall Penetration 1 preparation | itp | 561482-ITP-003.1 - Wet Well Wall Penetration 1 preparation
70d2b7d8-0f17-46af-aa25-bb4162eb20bb | section | SECTION 3 – RECEIVING INSPECTIONS
831d5383-d131-4131-a95a-0695bb228c43 | checkpoint | 3.1 - Masonry drill bits 18mm
2f2ec1d4-b5c9-5022-9ebf-331b19e64cea | note | Inspection Point: Quality Control Activity - Verify correct quantity & type
50c297ef-6a44-502b-b686-521bd8cdc41c | note | Acceptance Criteria - Compatable with the drill unit
0dd98786-2f63-5823-b9c9-168a0cc435f2 | note | Verifying Document - Manufacturers Technical data & Physical fitment
00956f22-44e6-5bdc-9eb6-f26fda4f86c7 | note | Frequency - Once
4ed4d68c-4b9d-5d85-be2a-61fab0741828 | note | Inspection Type (Visual, other) - Visual + Photographs
057f0f5d-ec13-5466-9f36-69d71ade2670 | note | Inspection: Key - Inspection
1b9e42cb-559e-5ac8-8519-26309831c833 | note | Inspection: By - IP
51256ae4-f8eb-4aad-9388-5f99b54dced9 | checkpoint | 3.2 - Reinforcing Bar
e0df326f-cd3a-5d35-a021-5592c6300caa | note | Inspection Point: Quality Control Activity - Verify correct quantity & size/diameter has been delivered to site
a6a88c20-ce85-5979-ab7e-ef7fb5ded6f2 | note | Acceptance Criteria - Quantities correct. Dimensions correct.
92a27d7d-2361-585b-ada9-1cead959f190 | note | Verifying Document - Drawing M0003
c94061b2-051d-5df9-a86e-2074c12f5e2c | note | Frequency - Once
b4d02de9-89aa-59e7-8449-6529e6bfbf46 | note | Inspection Type (Visual, other) - Visual + Photographs
8920a18e-6b43-5c24-b2b7-0e3aacc21fc2 | note | Inspection: Key - Inspection
572dd9aa-1097-52c7-8f3b-70c99df509c8 | note | Inspection: By - IP
d8f4b626-be11-4e01-8397-e0a095c44a74 | checkpoint | 3.3 - Hilti RE-500 Chemical Anchor
cf43255c-3e3c-5677-a7c4-6e862617f647 | note | Inspection Point: Quality Control Activity - Verify correct product is delivered.
8931543f-3473-555b-b872-e55facacc074 | note | ○ Check expiration date.
63f3b29d-808b-574b-b458-ccb01de62485 | note | Acceptance Criteria - Quantities correct. Within expiration date
4248694b-5436-543d-9649-0731ee7dee54 | note | Verifying Document - HILTI Product Calculator APP. Delivery Docket
cbaf1df7-cef0-5860-8099-15573a209ef1 | note | Frequency - Once
3dbc79ac-85a5-5884-b58d-4c0c5dd6a773 | note | Inspection Type (Visual, other) - Visual + Photographs
238b3ed0-ad63-5e23-b5b5-9e650693bb72 | note | Inspection: Key - Inspection
4940acd8-3de9-58c8-9cd5-71666d24c7b2 | note | Inspection: By - IP
07963279-7330-400c-b183-282f8d249eb3 | checkpoint | 3.4 - Grout (Sika MonoTop 438R)
b3f2cbb0-a459-5f15-bc1b-68b0bfb7dc01 | note | Inspection Point: Quality Control Activity - Verify correct product is delivered.
bebdb64b-ffbd-57fa-9eae-b759d47ed83a | note | ○ Check expiration date.
15b32474-7cee-5782-ad3b-4dabfcf1a2a5 | note | Acceptance Criteria - Quantities correct. Within expiration date
67b69021-00f7-59ea-b0ed-f8fad4183ea3 | note | Verifying Document - Delivery Docket
00a3afdf-770a-5d5a-9920-beef582dea14 | note | Frequency - Once
6cdc79b1-4c01-5f78-a867-370801cffd23 | note | Inspection Type (Visual, other) - Written/Submission
bbb63290-b8ae-5c9b-b1ad-62197ba21183 | note | Inspection: Key - Inspection
163c630c-ef83-50a8-9da1-02d27d0e4ce9 | note | Inspection: By - IP
628ee1fc-3780-44ee-adae-cbea0708361a | section | SECTION 4 – IN-PROCESS INSPECTIONS
97d347a8-108f-4510-a740-0fcaf4b5c661 | checkpoint | 4.1 - Mark out penetration on both sides (wet & dry sides) using existing pipe as reference
b9e50428-bc80-59e3-9f0c-b1f639725e2c | note | Inspection Point: Quality Control Activity - Check and verify dimensains against drawings
edce4d73-347e-5386-a0d8-7cd4c15697fa | note | Acceptance Criteria - Approval from Engineer
f9010629-d394-551f-94b0-64116706d71f | note | Verifying Document - Drawing M0003
768024bd-f85a-5b9f-8a1e-938725fb20ff | note | Frequency - once
25373ab7-82a1-557b-ab54-fce66130b41f | note | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
4fb18328-b59c-5d33-a7ac-4627bda16e4f | note | Inspection: Key - V
371dcc04-417d-5f8e-80fb-c489a1658b56 | note | Inspection: By - CR
549e2aeb-3e36-4013-a0b3-b5173363e8c7 | checkpoint | 4.2 - Proceed with breakout. Hammer drill
f978e7dc-ec13-52fc-a6af-69f263e5ea7c | note | Inspection Point: Quality Control Activity - Monitor work and progress report any issues
a2fd2d9c-9faf-5c01-a692-89c9ee75e0a6 | note | Acceptance Criteria - Approval to proceed from item 4.1
75900694-3c87-5cc5-ac40-5659a7985458 | note | Verifying Document - As per drawings listed dimensions & measurements
fc8beb5a-170e-5c34-998e-599f26cde7e8 | note | Frequency - once
3c036cfb-bc33-5b19-8f55-a86370b1e560 | note | Inspection Type (Visual, other) - Visual & Document
acf8a47d-30af-5ff2-853b-cf991c1da4ef | note | Inspection: Key - I
65361f03-4181-550e-ac46-ead919526566 | note | Inspection: By - IP
86c81254-a297-43e4-90e2-25971925947c | checkpoint | 4.3 - Pre-pour inspection
4d426552-4e3d-53a8-b844-0b6fc5f2951c | note | Inspection Point: Quality Control Activity - Engineer Inspection
b4e6bd5f-c0e3-56df-abb3-dd9e38a26290 | note | Acceptance Criteria - Dimensioin & Surface check. As per Drawing M0003 and notes.
62e9e1ff-6f39-5433-a616-6ba944b7a87c | note | ○ Approval to proceed via NTC.
06fa3152-e975-544f-9fa7-630fc7adc1a2 | note | ○ Correct profile achieved with 5mm roughness and any loose material removed
8702d979-e249-5a09-852f-30e4c4877c13 | note | Verifying Document - NTC or other written confirmation
b2442aed-3eea-55f7-97e3-4b22676b7594 | note | Frequency - once
0b41513a-208b-53c9-b461-933b716afc01 | note | Inspection Type (Visual, other) - Document
91467593-807b-52af-9f52-b0fa8c58f010 | note | Inspection: Key - H
253a022c-ee53-5d22-aa11-8fb14f56f1f3 | note | Inspection: By - CR
210e4ba5-1099-41cc-af18-2bc4ed10e931 | signoff | AUTHORITY HOLDPOINT
a82c2e9a-980a-44c0-b8e9-d90ab8bd6329 | checkpoint | 4.4 - Procurement of Reinforcing bar, starters & trimmers
fb6203dd-fd1c-53f3-8b38-65fb11d6da7a | note | Inspection Point: Quality Control Activity - Check measurents and vereify correct fitment
acf6bd14-76ba-57be-9bab-925efa7d5ba1 | note | Acceptance Criteria - As detailed on Drawings & specifications
e29d11a2-4f8a-594f-b47b-bff668a7081a | note | Verifying Document - Drawing M0003
d50ab8bc-dad3-5791-aed9-6dcdf4e63eaf | note | Frequency - once
4f4fbf52-631f-5b6f-b933-aa71361ae6bc | note | Inspection Type (Visual, other) - Document + Visual
740c2857-55b9-5885-8381-49c2c21de75f | note | Inspection: Key - I
b62bf4f2-ec40-50c5-aa83-69722c44b737 | note | Inspection: By - IP
55902cda-a715-460a-b173-131876a08525 | checkpoint | 4.5 - Installation of Reinforcing bar, starters & trimmers
0cb8c155-69a7-52ec-b72a-c16a8342e3a5 | note | Inspection Point: Quality Control Activity - Drill holes around perimeter to receive reinforcing bar. Check for correct diameter & corret embedment
72e0f55b-4f92-536e-96a3-a73c28f2a773 | note | Acceptance Criteria - As detailed on Drawings
715e818d-a28c-5c5d-b11b-e2e8f90fe7d1 | note | Verifying Document - Drawing M0003
29e45e54-2233-54bf-8a6f-0690e1a84358 | note | Frequency - once
eec6bdcc-24c3-5a1f-b3d6-788daac4d1b2 | note | Inspection Type (Visual, other) - Visual + Photographs
8a1dcdac-70bf-5072-b67a-530e786ac3eb | note | Inspection: Key - I
4d40c43e-4291-5357-836a-823f5ce559c1 | note | Inspection: By - IP
2d3be309-151c-4c8b-887e-b456cf37fa91 | checkpoint | 4.6 - Install pipe spool with puddle flange to be cast within wall
e65f1e4f-f759-521f-84da-4c5d2e50cea1 | note | Inspection Point: Quality Control Activity - Check that orientation is correct and is in alignment with pump assembly
3fb0b602-03fa-5018-a6ca-f20f81b00e2e | note | Acceptance Criteria - As detailed on Drawings M0003 and drawing notes
f234fa9d-3bd3-5072-97dd-c1ea57f91372 | note | Verifying Document - Drawing M0001 Drawing M0002 Drawing M0003 Drawing M0004
0eba833b-cf6a-51f3-9aa9-bd558e627639 | note | Frequency - once
1564d1a8-b262-53db-a63d-f6ae24fcb73c | note | Inspection Type (Visual, other) - Visual + Photographs
15a61dd4-96c4-57ca-9a10-4e769bcc8f73 | note | Inspection: Key - I
d9e96fae-6ccc-53eb-920b-a9b3f842028e | note | Inspection: By - IP
4eddd335-7245-4395-97f1-f5ab7ce82d1c | checkpoint | 4.7 - Hilti RE500. Chemical Anchor reinforcing bar, starters & trimmers into position
5947a888-b60e-5179-9c6f-6552260830a6 | note | Inspection Point: Quality Control Activity - Observe Manufacturers instructions. Monitor curing times and temparatures. Use manufacturers calculator to determine product volumes. Sequence the installion to avoid obstruction
b14be2b8-b394-5adf-82d3-d9fb08f1b8e1 | note | Acceptance Criteria - As detailed on Drawings and completion of item 4.6
3bcd08f7-d2e2-537a-acc0-6f44075fc2a4 | note | Verifying Document - Drawing M0003
d8ded1b7-af78-5865-a078-9808545d84f5 | note | Frequency - once
c3cb1422-7d65-5867-846a-957f6cbd8934 | note | Inspection Type (Visual, other) - Visual + Photographs
e3928c7f-42d8-52c3-8598-9803dcbb4df6 | note | Inspection: Key - I
aaf6a2d9-39ba-56fc-b7e1-788813939b44 | note | Inspection: By - IP
b5d09d7b-b5c4-4d3f-8301-a4dd5a9a79fa | checkpoint | 4.8 - Chemically treat perimeter using product HYDROTITE CJ1020
f8bd7d98-a5c0-56a7-99c1-f8d3da09d1c3 | note | Inspection Point: Quality Control Activity - Observe Manufacturers instructiuons & Health and safety requirements
671043ea-04b7-5ed0-a91f-164a70ad2757 | note | Acceptance Criteria - As detailed on Drawings and completion of item 4.7
18c5924f-4585-5dfe-ab31-6c0ed738bb80 | note | Verifying Document - Drawing M0003
53bb8161-5907-54f4-aa74-59b07dbd7018 | note | Frequency - once
3b32276f-81bb-5606-8f35-43a758ee2d10 | note | Inspection Type (Visual, other) - Visual + Photographs
c4905fe5-5b51-53e2-822b-c03ad891c555 | note | Inspection: Key - H
ce7ce692-a20c-50a2-9d7c-f5c22ec720ce | note | Inspection: By - IP
f4956bf3-31e3-4a59-9c8b-80ccc557eaf2 | signoff | AUTHORITY HOLDPOINT
3914c02b-767a-42e3-a8f5-48cca0445bb0 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
5281b3a1-ab7f-4902-a52e-9ebbae8ae090 | checkpoint | 5.1 - Final dimensional check
25005eb0-4ff0-5928-80ff-77a475076d7d | note | Inspection Point: Quality Control Activity - At completion of all items on this ITP
42f26a64-1d2e-5e62-b3e4-48919c618ef4 | note | Acceptance Criteria - Dimensions match the measurements shown on drawings
23d0a6c3-4477-52bc-8287-b532c99d2a50 | note | Verifying Document - Drawing M0003
4eb438bd-f9f6-5c24-ba2f-ef3927a0abe9 | note | Frequency - once
8f06c144-4ad1-5e1e-a966-ea3a846ff20d | note | Inspection Type (Visual, other) - Visual + Photograph + Mark-up drawing
0ebbc0ec-9fe0-5fea-b995-e6bf6f4de2ec | note | Inspection: Key - H
993797aa-e298-52fe-97f5-2a4bca1e6a33 | note | Inspection: By - CR
532cfe1f-4f8b-4745-ac7d-b1aeaf75317a | signoff | AUTHORITY HOLDPOINT
1ba94c58-b0b3-4a2f-a2b7-f7d80d3e1ad1 | checklist | 561482-ITP-003.2 - Wet Well Wall Penetration 2 preparation | itp | 561482-ITP-003.2 - Wet Well Wall Penetration 2 preparation
b1169e19-b01c-4802-9a47-1bfec0c5fa54 | section | SECTION 3 – RECEIVING INSPECTIONS
bd566547-d426-4bfb-bc76-aaca0030a492 | checkpoint | 3.1 - Masonry drill bits 18mm
1a2de801-2662-50be-9ae4-267e7434adf1 | note | Inspection Point: Quality Control Activity - Verify correct quantity & type
1049b679-346b-57d4-8852-3bfb97047003 | note | Acceptance Criteria - Compatable with the drill unit
aea93f94-318d-5b67-9399-ee2aff0cdf2b | note | Verifying Document - Manufacturers Technical data & Physical fitment
fe23cc55-2ddf-5d36-8417-2c293687b49c | note | Frequency - Once
b8662d38-4ff9-5533-9ab3-0df4a31b8e2f | note | Inspection Type (Visual, other) - Visual + Photographs
5b690832-cd26-5838-9760-eb736079fe11 | note | Inspection: Key - Inspection
8e8b335e-7d51-5aad-aaeb-1bca6648b5b1 | note | Inspection: By - IP
e3daef1d-734c-43b2-8e60-a85916754393 | checkpoint | 3.2 - Reinforcing Bar
490034f7-1636-588a-8189-5e0aaa600d3e | note | Inspection Point: Quality Control Activity - Verify correct quantity & size/diameter has been delivered to site
b9227575-7b66-5226-b9a6-b87e5d6bd9fa | note | Acceptance Criteria - Quantities correct. Dimensions correct.
5097db3f-5d3c-580a-b50f-97b4a5897bb4 | note | Verifying Document - Drawing M0003
8950332e-043d-5d8b-b6bd-4232275da2a0 | note | Frequency - Once
0698354b-dca2-511e-8a80-8aa2ea2e454e | note | Inspection Type (Visual, other) - Visual + Photographs
32f696cf-389d-5bcd-82b7-ca779640d76b | note | Inspection: Key - Inspection
1f24ee52-9dfc-5998-a7c3-8b5db42c22ab | note | Inspection: By - IP
a30251df-2aa5-4961-80ee-b23dacd44141 | checkpoint | 3.3 - Hilti RE-500 Chemical Anchor
70792bd7-7869-51e3-a82c-d3b24803d948 | note | Inspection Point: Quality Control Activity - Verify correct product is delivered.
50c392c4-b68e-56dc-9cab-949278f985b9 | note | ○ Check expiration date.
31671e94-738b-5e04-9ec0-ab62c2085c97 | note | Acceptance Criteria - Quantities correct. Within expiration date
7af6b21a-6c3d-5879-91f7-1590f5e3c974 | note | Verifying Document - HILTI Product Calculator APP. Delivery Docket
26ddd092-3c5c-5bfd-b5bd-33be2b07a30e | note | Frequency - Once
ab99e089-0b8c-5fbe-8747-f95d688e69e2 | note | Inspection Type (Visual, other) - Visual + Photographs
34f567c9-a5e7-55ab-874d-114ec3395375 | note | Inspection: Key - Inspection
626a6d89-baaa-571a-91c0-80ed41c53b8d | note | Inspection: By - IP
0a10b923-c9d6-4011-9dbb-086214e82e6d | checkpoint | 3.4 - Grout (Sika MonoTop 438R)
0ab4a437-4317-5a4d-86c7-1acc2cef33c3 | note | Inspection Point: Quality Control Activity - Verify correct product is delivered.
4b1ab8dc-0f92-5dc0-b8c8-6f3c953ef307 | note | ○ Check expiration date.
d2473af5-b90f-5501-80a9-3f91e67e42a9 | note | Acceptance Criteria - Quantities correct. Within expiration date
16a6ebbf-ea5a-501a-b8a4-94f8dd992c13 | note | Verifying Document - Delivery Docket
6c3028ad-7b92-51e0-b299-afd85c400a5d | note | Frequency - Once
0ec81f21-4359-5fe6-845b-4b7582264ee0 | note | Inspection Type (Visual, other) - Written/Submission
73e0511e-54ad-51de-a908-6cb4ce7e7c3d | note | Inspection: Key - Inspection
5941e82f-3d35-58e7-bb55-f27a6114b10d | note | Inspection: By - IP
fc152f8e-c6c9-4475-911e-a2dfd4391ba6 | section | SECTION 4 – IN-PROCESS INSPECTIONS
76ec880c-e101-4ad5-9f75-293958dc9853 | checkpoint | 4.1 - Mark out penetration on both sides (wet & dry sides) using existing pipe as reference
19c1fec6-0b04-5997-8a32-03a77935b4ee | note | Inspection Point: Quality Control Activity - Check and verify dimensains against drawings
cb3e2d79-373a-5c49-b2f8-20fdfec1451c | note | Acceptance Criteria - Approval from Engineer
90802df0-e025-5a18-a693-035fca4b8d98 | note | Verifying Document - Drawing M0003
8efa5235-d7d8-525a-8ebe-f80aa3667092 | note | Frequency - once
90881e0e-89d2-5733-b6ea-99218b24870d | note | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
05f6f690-2774-5284-bb27-db401829b25f | note | Inspection: Key - V
5ccf52a2-7c9e-575b-ae74-42903f2e66f4 | note | Inspection: By - CR
53ccfa49-87a1-4f1a-8793-54839f0c799f | checkpoint | 4.2 - Proceed with breakout. Hammer drill
ecc8fb97-7a56-5f5d-a364-a10b3b7e17da | note | Inspection Point: Quality Control Activity - Monitor work and progress report any issues
429d2ae8-8a4a-5aa1-82da-4e216ae34ee4 | note | Acceptance Criteria - Approval to proceed from item 4.1
987ee841-930d-5071-b36e-59b7d71066a3 | note | Verifying Document - As per drawings listed dimensions & measurements
0c39f5d4-cb43-5adc-9c90-f106abc00d21 | note | Frequency - once
794a557b-21e1-534c-8d3d-a7fecfb56840 | note | Inspection Type (Visual, other) - Visual & Document
a625a9c8-a09e-59ba-8b67-fee6d95770cf | note | Inspection: Key - I
c1f94467-9558-5cbc-aab2-c9e476f784dc | note | Inspection: By - IP
f4cb6c2e-97ff-4302-ae1f-2ce295e74344 | checkpoint | 4.3 - Pre pour inspection
2394dd60-ca48-5bf3-809d-ae9fe164f1f6 | note | Inspection Point: Quality Control Activity - Engineer Inspection
855a76be-0015-5e8e-b0cb-178286ae117e | note | Acceptance Criteria - Dimensioin & Surface sheck. As per Drawing M0003 and notes.
3853936e-0caa-5f85-8fc5-1d56239b2028 | note | ○ Approval to proceed via NTC.
514b90d3-ab7f-5748-8bdf-3061957011ec | note | ○ Correct profile achieved with 5mm roughness and any loose material removed
8720d665-db13-56d4-87a2-27ecb0bc0854 | note | Verifying Document - NTC or other written confirmation
ee140a13-e954-509c-ab91-48d6648cf37e | note | Frequency - once
b3b11926-61e6-5bb4-8dd8-4e439ce33bf5 | note | Inspection Type (Visual, other) - Document
7a9aebbb-1129-5803-84e9-e0fcd82d9fba | note | Inspection: Key - H
8c0a229c-c5cd-5b6e-af90-cf50a501d3c9 | note | Inspection: By - CR
6061b745-b578-41c0-8d2b-32686098d6bd | signoff | AUTHORITY HOLDPOINT
34b642b5-d84c-4c6a-84fd-ea1cb2488072 | checkpoint | 4.4 - Procurement of Reinforcing bar, starters & trimmers
a33c6a55-b703-560a-8c77-2e618c753677 | note | Inspection Point: Quality Control Activity - Check measurents and vereify correct fitment
b91b352a-46f7-5fbf-bbbb-e03ae6883737 | note | Acceptance Criteria - As detailed on Drawings & specifications
79e108fa-c139-5e3d-a71e-d770acbb0180 | note | Verifying Document - Drawing M0003
46db40c8-88af-50cb-b8fd-87c9a77b9580 | note | Frequency - once
28d15d0a-4633-5509-9f55-9127761eba18 | note | Inspection Type (Visual, other) - Document + Visual
d14e6927-aa0e-5f35-89bf-d79f0a3ba9e3 | note | Inspection: Key - I
9833d1bd-4b2d-5e9b-9fba-354848efbab8 | note | Inspection: By - IP
8d125455-4968-43d2-9488-9dd64c336adf | checkpoint | 4.5 - Installation of Reinforcing bar, starters & trimmers
dee6e842-2af2-5ec3-8dcb-36aff3461ab8 | note | Inspection Point: Quality Control Activity - Drill holes around perimeter to receive reinforcing bar. Check for correct diameter & corret embedment
8a5e25af-1eea-551d-9f13-1ca04a8fcf95 | note | Acceptance Criteria - As detailed on Drawings
8542aba5-15a9-5b0f-a41f-285a9259a3cf | note | Verifying Document - Drawing M0003
e3f904a4-b6e5-578e-ad09-1c20d7cefbe7 | note | Frequency - once
42333b53-df33-5244-af8a-3fd2e384add4 | note | Inspection Type (Visual, other) - Visual + Photographs
887ec9f6-7381-5bfd-ac21-7983f0a6c166 | note | Inspection: Key - I
5206384b-6500-5738-a44c-25dc16e27687 | note | Inspection: By - IP
4ed548f2-1735-4d07-a1a8-d7395a5edeb4 | checkpoint | 4.6 - Install pipe spool with puddle flange to be cast within wall
137c0236-9139-55d9-9ce2-f2b7fdf27331 | note | Inspection Point: Quality Control Activity - Check that orientation is correct and is in alignment with pump assembly
9d650d33-9c9a-5a82-bb1a-5b824618430d | note | Acceptance Criteria - As detailed on Drawings M0003 and drawing notes
bf1bba4c-d06b-5c58-9ef2-cc8455a7c1f6 | note | Verifying Document - Drawing M0001 Drawing M0002 Drawing M0003 Drawing M0004
bb56db9c-101f-574c-a936-e79a3bfaf3ec | note | Frequency - once
8974ee04-443e-57b6-a98f-da2416588dd6 | note | Inspection Type (Visual, other) - Visual + Photographs
7fab25a2-38c9-528c-8b7d-f6f4bad2491b | note | Inspection: Key - I
26da9048-7c3f-5630-afc1-74758ffb6fda | note | Inspection: By - IP
bc49a98b-da60-4346-8847-1459b67777cc | checkpoint | 4.7 - Hilti RE500. Chemical Anchor reinforcing bar, starters & trimmers into position
64390c44-299d-51ba-9030-1d0c83cf98e8 | note | Inspection Point: Quality Control Activity - Observe Manufacturers instructions. Monitor curing times and temparatures. Use manufacturers calculator to determine product volumes. Sequence the installion to avoid obstruction
0c135c3a-6ccf-5bff-a780-b7b672622a82 | note | Acceptance Criteria - As detailed on Drawings and completion of item 4.6
2005bf83-6d96-5395-94db-aa167895f5dd | note | Verifying Document - Drawing M0003
a942370c-2e1d-5255-b8e7-6c2cbbf90c03 | note | Frequency - once
05ced271-f35d-5eb4-a7ec-8346d9942736 | note | Inspection Type (Visual, other) - Visual + Photographs
34dc0e04-1877-5350-b233-a1d35f59db1e | note | Inspection: Key - I
c706d622-ed4b-535b-8bdc-5116b072f810 | note | Inspection: By - IP
66e245ac-0be0-46e1-88e6-220f6763a588 | checkpoint | 4.8 - Chemically treat perimeter using product HYDROTITE CJ1020
ce31c908-1efd-53e5-8abb-052d4ce54590 | note | Inspection Point: Quality Control Activity - Observe Manufacturers instructiuons & Health and safety requirements
6fa29dba-0a3f-5c98-9f6f-3e3875bd36f9 | note | Acceptance Criteria - As detailed on Drawings and completion of item 4.7
84255bb7-fc6a-5e25-9d6f-8104025cd09b | note | Verifying Document - Drawing M0003
c348a5bb-960f-500b-a9da-916cd9781430 | note | Frequency - once
772a7167-205f-5cf3-ac86-7d33015cc379 | note | Inspection Type (Visual, other) - Visual + Photographs
d08dceca-7ee0-508d-bc08-c306cc6d6819 | note | Inspection: Key - H
e7b79494-b0bb-5111-b8c6-cdde001f5a36 | note | Inspection: By - IP
613ab478-b1af-4f60-b9b2-32c453d259be | signoff | AUTHORITY HOLDPOINT
6c03f36d-008b-4d71-bfc0-819596f9ad63 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
c2b141c2-efa7-4370-8868-7d93a82737af | checkpoint | 5.1 - Final dimensional check
c88c326a-661c-5f9e-8437-e85c2ff9c667 | note | Inspection Point: Quality Control Activity - At completion of all items on this ITP
f86f00e5-9f04-562f-85f2-4423ece7ebfe | note | Acceptance Criteria - Dimensions match the measurements shown on drawings
0f36af1f-1d1d-5ada-90e8-182ecc283d03 | note | Verifying Document - Drawing M0003
5a82595b-ef88-5269-ba41-b5434253666c | note | Frequency - once
9bb9331f-c92d-5586-8d73-904a8f6c697d | note | Inspection Type (Visual, other) - Visual + Photograph + Mark-up drawing
d398248e-e32d-5f39-8d0e-594355ba4544 | note | Inspection: Key - H
73ad91b7-e3ee-5891-8aab-1dfbb3577155 | note | Inspection: By - CR
9ceaf1d0-3dcc-46a5-a7fa-08ff883c44b2 | signoff | AUTHORITY HOLDPOINT
1dc760eb-f1f5-4f4a-bca0-a0031132081b | checklist | 561482-ITP-003.3 - Wet Well Wall Penetration 3 preparation | itp | 561482-ITP-003.3 - Wet Well Wall Penetration 3 preparation
5ed444c4-65b6-4d53-9046-3459123349d7 | section | SECTION 3 – RECEIVING INSPECTIONS
a9b5b906-95d9-4868-8f2d-6760c6fd566b | checkpoint | 3.1 - Masonry drill bits 18mm
c4a56371-f7fc-5cc2-b574-78e4277251a1 | note | Inspection Point: Quality Control Activity - Verify correct quantity & type
eccef8bf-a8af-5d3b-86d6-44d95e309c27 | note | Acceptance Criteria - Compatable with the drill unit
43423ac1-6857-5b3d-bde1-e87d1808e0a8 | note | Verifying Document - Manufacturers Technical data & Physical fitment
2aa2b0fd-f8b7-5795-8228-bb5ad76521e4 | note | Frequency - Once
767c77c5-8ef6-540e-ac1f-4a2c2c072652 | note | Inspection Type (Visual, other) - Visual + Photographs
91d4778f-b80d-5f10-b867-6c32cfa8df6b | note | Inspection: Key - Inspection
4ecf6cab-b4a1-56bb-bc4c-a3455af0732c | note | Inspection: By - IP
acbe9a7b-e785-4fda-90a1-a10095cfb745 | checkpoint | 3.2 - Reinforcing Bar
98ed4f1f-0e02-5f01-9795-02dfde9772a0 | note | Inspection Point: Quality Control Activity - Verify correct quantity & size/diameter has been delivered to site
bad348d8-f1c2-5abc-a3f3-d9ee8d8d07d8 | note | Acceptance Criteria - Quantities correct. Dimensions correct.
1f579878-5cef-560e-acfe-ecf9e64d3c11 | note | Verifying Document - Drawing M0003
d5023806-7f97-5a76-a850-f0deb10d2f50 | note | Frequency - Once
bc6b0e20-7c12-52d6-b83c-728ef314e48b | note | Inspection Type (Visual, other) - Visual + Photographs
7010a7d2-4042-543b-bdc7-c94da028b38b | note | Inspection: Key - Inspection
60bc3985-d3df-5cc1-8d85-9b57df6c129e | note | Inspection: By - IP
3a5c371f-ec21-438f-b1c9-df17615e4be6 | checkpoint | 3.3 - Hilti RE-500 Chemical Anchor
c5915dbb-d150-5f91-bf84-fe8ccb07b350 | note | Inspection Point: Quality Control Activity - Verify correct product is delivered.
47f3a1a6-406b-5001-8536-2068d7c1d882 | note | ○ Check expiration date.
6759d78a-5204-5703-bd05-83013fb523a0 | note | Acceptance Criteria - Quantities correct. Within expiration date
ee6286dd-63a7-59a9-a69e-c7c14be682c2 | note | Verifying Document - HILTI Product Calculator APP. Delivery Docket
2dfe4f7b-51c2-5ce0-ac49-9ca0d52f71ac | note | Frequency - Once
62e06b6d-566a-51f6-b409-38b9e8243798 | note | Inspection Type (Visual, other) - Visual + Photographs
1d52c1f7-d2f0-55c4-9128-6c05b4c3b737 | note | Inspection: Key - Inspection
82bd780e-bbbc-58fc-a621-9c25086ceadd | note | Inspection: By - IP
05b2ee05-f439-4e89-b116-28ab8cb89779 | checkpoint | 3.4 - Grout (Sika MonoTop 438R)
a971c529-f88a-5e93-b175-101e77777c3c | note | Inspection Point: Quality Control Activity - Verify correct product is delivered.
49511b0c-08e2-54a9-afc2-3c4a7371870d | note | ○ Check expiration date.
1fa37b5a-b2f6-5c93-92f0-e21ab4802cf7 | note | Acceptance Criteria - Quantities correct. Within expiration date
59c3406e-b013-547d-a65e-4652611da43e | note | Verifying Document - Delivery Docket
77d767cc-c9b2-5fe0-a15d-7cf8a2674211 | note | Frequency - Once
bef9f1ef-eba0-53d5-83ae-270729df0874 | note | Inspection Type (Visual, other) - Written/Submission
e490160d-0204-5f87-a437-42b50c98cfe0 | note | Inspection: Key - Inspection
4c5e6d94-8451-519e-b7ae-2b61476342ce | note | Inspection: By - IP
0cb96fa4-247a-4bb9-91f1-566ff64da61d | section | SECTION 4 – IN-PROCESS INSPECTIONS
c87814a9-5816-450a-9c8f-44ee67aade89 | checkpoint | 4.1 - Mark out penetration on both sides (wet & dry sides) using existing pipe as reference
9628bbf8-63ea-55a4-9926-0cafebfe3d05 | note | Inspection Point: Quality Control Activity - Check and verify dimensains against drawings
e7caf85a-ec9b-58b0-b542-01ed05441cba | note | Acceptance Criteria - Approval from Engineer
c4ea6020-dcf4-57a5-9d00-19bacc50ce4e | note | Verifying Document - Drawing M0003
0e7fff70-8af9-570b-ae6e-d89c254234a4 | note | Frequency - once
36c68a58-e735-578c-b357-5757c6ce91da | note | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
100cc10e-9b9d-5849-9f5d-62a52a3558fd | note | Inspection: Key - V
93cd02f5-5e48-510b-a1df-d09c207a254c | note | Inspection: By - CR
d4cf5233-cde6-4c3e-90f0-d1397abb5e62 | checkpoint | 4.2 - Proceed with breakout. Hammer drill
4f7934e8-3027-5811-8608-f2d3a3a60883 | note | Inspection Point: Quality Control Activity - Monitor work and progress report any issues
d8eb8bb1-4b37-5a9d-9bb3-b3322fd02857 | note | Acceptance Criteria - Approval to proceed from item 4.1
6d55a4cd-6d69-502a-87de-18bed92824de | note | Verifying Document - As per drawings listed dimensions & measurements
8a9aa87a-4356-5a45-a90f-aa819e8f6c72 | note | Frequency - once
7766ac91-8e05-527f-bba9-7cc53273f8f8 | note | Inspection Type (Visual, other) - Visual & Document
e3b6b701-53e7-5376-97c1-a56fd73985ad | note | Inspection: Key - I
603633b9-2429-5ec9-bc25-a6605b4478ab | note | Inspection: By - IP
c09ae30b-143b-431f-b94d-4af84899eec3 | checkpoint | 4.3 - Pre pour inspection
833de4c7-4893-5c89-8a7f-62bd7583617b | note | Inspection Point: Quality Control Activity - Engineer Inspection
76c99516-9f16-5e03-956b-739d4571960e | note | Acceptance Criteria - Dimensioin & Surface sheck. As per Drawing M0003 and notes.
07a0c299-b85b-55b8-a3c0-c103c89d7ed2 | note | ○ Approval to proceed via NTC.
0a75b353-2e83-5ea6-8015-a6d834864adf | note | ○ Correct profile achieved with 5mm roughness and any loose material removed
321493f8-28df-59ea-9242-748ad90dc494 | note | Verifying Document - NTC or other written confirmation
86ba8aa0-48a6-5c8e-8e21-6fafa0634e24 | note | Frequency - once
6f21602b-8cc4-5714-a127-530c38d34062 | note | Inspection Type (Visual, other) - Document
a1430b90-4bab-5e66-bf22-11a027058351 | note | Inspection: Key - H
85278ac7-dbd1-550b-b8ef-611b68ee5052 | note | Inspection: By - CR
6e883907-69a1-48f7-b45e-566e0d548225 | signoff | AUTHORITY HOLDPOINT
3dc4cb61-e9e4-4802-86df-3e833a7f5c94 | checkpoint | 4.4 - Procurement of Reinforcing bar, starters & trimmers
97c4cc04-222d-5243-823a-58d100ca0d82 | note | Inspection Point: Quality Control Activity - Check measurents and vereify correct fitment
8eeaea31-3068-5ebc-b759-742b1bf79779 | note | Acceptance Criteria - As detailed on Drawings & specifications
c3f3a011-3a05-5e8b-8ac4-678064257598 | note | Verifying Document - Drawing M0003
b055805d-3cfe-503d-aef2-924917bf14f8 | note | Frequency - once
bfe7ed94-68bc-581c-a2e1-50bc8f655d9e | note | Inspection Type (Visual, other) - Document + Visual
6b14f853-d9e7-5849-8d97-0cfb7d199700 | note | Inspection: Key - I
fec86473-1c61-528a-a26f-ca10ed0c1b9e | note | Inspection: By - IP
3cf924a0-2cfd-449b-a01f-7df9766eb4d6 | checkpoint | 4.5 - Installation of Reinforcing bar, starters & trimmers
f67c7b15-65f0-5528-98fc-a4654338ed8a | note | Inspection Point: Quality Control Activity - Drill holes around perimeter to receive reinforcing bar. Check for correct diameter & corret embedment
dc4399c0-f75c-55b0-b418-5c89c44cd1fb | note | Acceptance Criteria - As detailed on Drawings
418af4a8-b92e-5b41-a5df-607d758fe738 | note | Verifying Document - Drawing M0003
e7fdff39-7bb5-5f45-ac64-2368349903fe | note | Frequency - once
e1fb42e0-61f6-5771-b5db-0996dfae80f2 | note | Inspection Type (Visual, other) - Visual + Photographs
d65924ba-605d-5e21-ad83-c314eb177437 | note | Inspection: Key - I
76d46312-162f-597c-a547-a820ecc08d7a | note | Inspection: By - IP
af2afe16-2ab9-4de0-a1b1-ad666b7af2a3 | checkpoint | 4.6 - Install pipe spool with puddle flange to be cast within wall
1d374415-f5d4-56a9-901d-ec97decb98ae | note | Inspection Point: Quality Control Activity - Check that orientation is correct and is in alignment with pump assembly
df4fe819-2489-5c21-900e-bc2f8bde9c07 | note | Acceptance Criteria - As detailed on Drawings M0003 and drawing notes
d3f144a5-e997-532d-b010-f29f646b8197 | note | Verifying Document - Drawing M0001 Drawing M0002 Drawing M0003 Drawing M0004
18529ad3-7a5d-5630-8918-a49b1f0c8017 | note | Frequency - once
c15e88ff-81bf-5e33-92c4-1a29edb8db8a | note | Inspection Type (Visual, other) - Visual + Photographs
f9aaa5d0-90fb-5295-99d8-6f1530462e11 | note | Inspection: Key - I
b53f45fc-31b6-57a9-9b2d-1687deb42c19 | note | Inspection: By - IP
8969be87-5e13-4fba-a08c-e9242527ef00 | checkpoint | 4.7 - Hilti RE500. Chemical Anchor reinforcing bar, starters & trimmers into position
16e220ff-7e86-52fb-ad78-0bd8d62c71fe | note | Inspection Point: Quality Control Activity - Observe Manufacturers instructions. Monitor curing times and temparatures. Use manufacturers calculator to determine product volumes. Sequence the installion to avoid obstruction
edafc1de-0bd3-57dd-8bd5-cfd303e80e7c | note | Acceptance Criteria - As detailed on Drawings and completion of item 4.6
718cd957-3bea-56fa-90a8-1a5c6e0fba10 | note | Verifying Document - Drawing M0003
7eb7ca13-d5de-5c61-80f6-b5129254b733 | note | Frequency - once
629c2340-525b-5b6a-8631-972ea1748cff | note | Inspection Type (Visual, other) - Visual + Photographs
bb63396a-c44f-5506-a95b-b1faf2268419 | note | Inspection: Key - I
cdbd9e99-f650-5a44-94ec-53238b304c7b | note | Inspection: By - IP
3cf02a3e-caa1-4dba-b3a1-dc6b7a55140a | checkpoint | 4.8 - Chemically treat perimeter using product HYDROTITE CJ1020
67339f37-47da-51f5-83eb-e8198fd3c5e9 | note | Inspection Point: Quality Control Activity - Observe Manufacturers instructiuons & Health and safety requirements
bf4ed5af-58d4-501d-9928-782a6bfd321c | note | Acceptance Criteria - As detailed on Drawings and completion of item 4.7
8247bde7-2e88-59a2-97fc-1a692190a911 | note | Verifying Document - Drawing M0003
6efb568c-4396-56a4-9fb4-85c20ddef891 | note | Frequency - once
85fd3468-29ae-5932-b2db-8ebaa35e740d | note | Inspection Type (Visual, other) - Visual + Photographs
ebdc0b58-ef13-534f-9b83-87e9de533d89 | note | Inspection: Key - H
f063ad3e-dd68-54a8-a3f7-eea871543eea | note | Inspection: By - IP
94ab3dfd-ccc5-4d28-a550-beeee1be216b | signoff | AUTHORITY HOLDPOINT
e981f6ff-dc41-4a49-9cc0-dee4a37a3838 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
1e63fe07-e964-4385-9234-46e0bb61b58e | checkpoint | 5.1 - Final dimensional check
2c44634c-a222-5354-b5a5-5aa35e2c4264 | note | Inspection Point: Quality Control Activity - At completion of all items on this ITP
da34e358-c56c-55e7-be04-6f6359c00e6b | note | Acceptance Criteria - Dimensions match the measurements shown on drawings
2e7f6172-cee5-5605-a54c-bce5714f99b8 | note | Verifying Document - Drawing M0003
f902b2e7-0706-5350-b079-ab7371fa4059 | note | Frequency - once
2d309f47-5c33-57f2-8b5f-b124b3238552 | note | Inspection Type (Visual, other) - Visual + Photograph + Mark-up drawing
f2444cc3-9b93-5477-b868-6f470d914e3c | note | Inspection: Key - H
760136ad-1915-50bb-8abf-5013894b03d4 | note | Inspection: By - CR
9db7d794-ff29-4496-9bcc-9bcc56b884de | signoff | AUTHORITY HOLDPOINT
c0176c4b-1cb9-4e09-8eaa-fd3b67331c4b | checklist | 561482-ITP-004.2 - Base. Pump. Motor Installation - Pumpset 2 | itp | 561482-ITP-004.2 - Base. Pump. Motor Installation - Pumpset 2
852ee526-2121-4a19-a62e-596344d4adc0 | section | SECTION 3 – RECEIVING INSPECTIONS
84cbfd59-ba2a-48b0-bd48-cec37546f434 | checkpoint | 3.1 - Inspection of Plinths for pump 2
0944af89-4e92-5ff2-905c-089bb0548cf5 | note | Inspection Point: Quality Control Activity - Check overall condition. Cracks/fissures or breaks or areas of weakness
319468c4-7958-53d7-a7b7-5d755608a988 | note | Acceptance Criteria - Visual check and report any defects or areas of concern
135c82ec-f9c1-5da5-bf73-d344009c98c8 | note | Verifying Document - Email or NTE to report
dd11f01c-1ea8-5ad5-ae71-a85eed798fc3 | note | Frequency - once
bf445cc0-85da-5887-9f85-27ccd22c7be9 | note | Inspection Type (Visual, other) - Visual + Photograph
2fb27d1f-ec8a-5de9-9573-6f1b8a1bcbb7 | note | Inspection: Key - C
4c1e8eb9-d3dc-5183-a6fb-b13241dbdf77 | note | Inspection: By - IP/B
9a1ca43e-7692-4ed4-8a24-b31831100704 | checkpoint | 3.2 - Delivery of Pump 2 to site from Downer storage facility
d61aa01f-8024-53ee-9002-b98beff2d500 | note | Inspection Point: Quality Control Activity - Check and verify that correct pump is delivered
7ee2bb0f-3786-549e-b3b6-705bbc95db3a | note | Acceptance Criteria - Pump is damage free
b377f5a4-bd10-5dce-ab8f-debd5a64a27b | note | Verifying Document - 1. KSB delivery docket.
8556bb09-e5f7-508c-88e5-4caa394e8439 | note | 2. Pump storage ITP
392496e6-a99b-5cef-9161-f011e1dcfc60 | note | Frequency - Once
df02cda1-5ddd-51bc-a6d6-ae782f3c269d | note | Inspection Type (Visual, other) - Visual
3cd6d7ba-2206-50da-8bd0-b77d4d3ced2e | note | Inspection: Key - C
26426cac-e99a-5ba9-983d-02b80f973c1d | note | Inspection: By - IP
954e8b13-ad6c-4c1e-8b52-d168b9859daa | checkpoint | 3.3 - Delivery of Pump 2 Motor to site from Downer storage facility.
0892dd42-8209-51c7-8400-ecfc185882f1 | note | Inspection Point: Quality Control Activity - Check and verify that correct motor is delivered
99f766cf-4270-5eb1-9736-eb124bd3cd90 | note | Acceptance Criteria - Motor is damage free
9e50a624-30cd-5d48-ac9c-3917d73db56c | note | Verifying Document - 1. KSB delivery docket.
b009fb85-608f-54f5-98f1-6199a512ad47 | note | 2. Pump storage ITP
15e60d4c-85be-52dc-b137-e3d4e6c60bdf | note | Frequency - Once
615cd180-da94-5c41-abfb-039e4b29c100 | note | Inspection Type (Visual, other) - Visual
8907eee1-2437-5d43-835c-4453792442ae | note | Inspection: Key - C
33ca49f8-2e60-56b5-b7f7-0d01a03914bd | note | Inspection: By - IP
34f206b9-afd9-457e-91af-e3753671e53d | checkpoint | 3.4 - Delivery of Pump & Motor mounting plate Downer storage facility
fa6f80e1-e7d9-5f62-ac53-55666f8d7581 | note | Inspection Point: Quality Control Activity - Check & Verify that correct Mounting plate is delivered
ed3e5d66-6685-586c-9538-4789013fca64 | note | Acceptance Criteria - Mounting plate is dumensionally correct and is damage free
329f7c4e-230f-5786-87e7-1ac4cfc286ad | note | Verifying Document - 1. KSB delivery docket.
349bb1ae-3ad9-54aa-a65e-5022af8efe90 | note | 2. Pump storage ITP
0f223b15-e080-59e4-85b1-805e8d6d289b | note | Frequency - Once
85d776f4-e13f-52aa-a570-f73d20c9b7ba | note | Inspection Type (Visual, other) - other
87d9b259-41f0-5d9e-b68e-602fb4474cbd | note | Inspection: Key - R
4ea29381-ef97-5ca6-8edc-abced362e6f4 | note | Inspection: By - CR
83b0d062-00ea-4e11-949e-c48b137b2a98 | section | SECTION 4 – IN-PROCESS INSPECTIONS
211f308a-ca17-4d48-ac63-5cac4e60c05c | checkpoint | 4.2 - On-site assembly
d23904cf-480e-598b-86e0-49ff7be2b2de | note | Inspection Point: Quality Control Activity - Correct Pump to Mounting Plate Assembly.
5e9b4823-e612-51c9-9e4e-d1b1afb7a9f0 | note | Acceptance Criteria - Ensure all fasteners are tight and toqued to manufacturers specifications
2ee4bfab-acdc-5872-aefb-42e95f4d9afb | note | Verifying Document - KSB documentation & Installation Instructiions
d34d7818-2765-52f9-bb1b-36a9fdbac04a | note | Frequency - Once/per pumpset
3f8d5d2e-cf3b-5fb0-b1e6-07e511fe6efe | note | Inspection Type (Visual, other) - Visual + Written
002eeeff-d20e-50be-9ea5-61e057b3e8ee | note | Inspection: Key - Inspection
5e9aabb9-7cac-515f-8af0-c4cd12a7071b | note | Inspection: By - IP
997cf824-83e0-4185-b250-4d19e4ef9899 | checkpoint | 4.3 - Pump 2 Installation
d2a905fe-2464-50b9-9b0d-5cf6635c3fed | note | Inspection Point: Quality Control Activity - Correct Mounting plate position on plinth, correct use of fasteners and torque requirements, in accordance with KSB installation instruction
f72417e0-a1e2-5c8d-9457-8fcf2d06e1bf | note | Acceptance Criteria - Position is determined by the fixed pipework. Ensure alignment of flange face is parallel to wet well wall
a16f3447-455e-56c6-90d6-7934f298ce26 | note | Verifying Document - Drawing M0001
8d8fc916-5413-5a76-a5cb-d6344ed90d14 | note | Frequency - Once
5c48086d-b44d-5cd9-8afa-d9168e18fa69 | note | Inspection Type (Visual, other) - Visual + Photograph
fd05b4ab-d8a8-5cad-9124-c2d3db507ca2 | note | Inspection: Key - A/D
e75ea7ce-5a0f-5a26-b098-0758c82b0e93 | note | Inspection: By - IP
f2c5caf5-11f8-4a5a-8335-fb4516a356ed | checkpoint | 4.4 - Pump 2 Motor Installation
9ab31a73-fa55-59be-a576-365f86a125fb | note | Inspection Point: Quality Control Activity - Motor/Pump shaft alignment
e5763ae3-8739-5050-b7c1-680e91e605af | note | Acceptance Criteria - Motor and shaft aligment as best as possible
5275eb14-ab5a-5f1c-95f7-99ad2d15a649 | note | Verifying Document - KSB documentation & Installation Instructiions. Nothing final alignment to be undertaken by a Technician - Ref: 561482-ITP-005.2
87c7e287-e622-59ab-9645-9e93b4b2b4eb | note | Frequency - Once
067f226d-8757-5ac4-a10b-0675002fd1d2 | note | Inspection Type (Visual, other) - Visual + Photograph
f2f141ff-df7f-59e9-b2f9-bff5e0671d1c | note | Inspection: Key - A/D
dee13af4-a63b-5eb4-a791-db18f977e500 | note | Inspection: By - IP
e26919e1-44ff-4f31-a8be-15cd528f4cc2 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
0912a208-d304-476e-97f1-0b94dfa91e56 | checkpoint | 5.1 - Pump 2 & Motor assembly complete
7e33aa1a-b72d-5df3-97d1-e1867f7b4a4a | note | Inspection Point: Quality Control Activity - Proceed with 561482-ITP005.2
6205ad35-6fda-5f9c-830f-911a0b4805f2 | note | Acceptance Criteria - Pump & Motor bolted to mounting plate and mounted to plinth.
dee0e475-15a7-5071-90a3-de114026ee70 | note | Verifying Document - This ITP
a99293ae-6679-53df-9214-ddefbcb96ffd | note | Frequency - once
f4b0c380-dd92-528a-acc8-248a73008f47 | note | Inspection Type (Visual, other) - Visual + Document
fff2c70d-72d1-51e5-82c1-93e30519b607 | note | Inspection: Key - I
6c95a871-a8d1-5772-80d8-a341a61b7a97 | note | Inspection: By - IP
da880a12-b43e-4edf-b9da-bea02b5ef762 | checklist | 561482-ITP-004.3 - Base. Pump. Motor Installation - Pumpset 3 | itp | 561482-ITP-004.3 - Base. Pump. Motor Installation - Pumpset 3
171b2e5b-339a-4f7b-98d6-38a92269a832 | section | SECTION 3 – RECEIVING INSPECTIONS
47850c6e-12e2-4972-9a21-0d73230aaf24 | checkpoint | 3.1 - Inspection of Plinths for pump 3
1083ea28-664d-5b42-aa30-d931ba59a9c2 | note | Inspection Point: Quality Control Activity - Check overall condition. Cracks/fissures or breaks or areas of weakness
e9275c00-33b9-55ba-9711-2ca0d8f39244 | note | Acceptance Criteria - Visual check and report any defects or areas of concern
c6add31b-60bd-51a2-988b-bf3a5afdc965 | note | Verifying Document - Email or NTE to report
a42a33eb-3d1a-5330-94d5-8655a8addb59 | note | Frequency - once
c2331a3c-a134-57df-b4bb-09ac7ae75ef7 | note | Inspection Type (Visual, other) - Visual + Photograph
bdf3c056-ef2e-5104-8d40-b23cdca9018e | note | Inspection: Key - C
4164830e-9048-5c17-92e4-da19e62da82f | note | Inspection: By - IP/B
44975ec3-feae-4658-8e83-fad7d6a28c1e | checkpoint | 3.2 - Delivery of Pump 3 to site from Downer storage facility
32ab29a3-3622-56c8-9723-1417a6880362 | note | Inspection Point: Quality Control Activity - Check and verify that correct pump is delivered
bf28d5cf-51c3-51ea-82e6-83680b3f1cbf | note | Acceptance Criteria - Pump is damage free
ac208a22-4fbd-572a-a079-8df9d186886d | note | Verifying Document - 1. KSB delivery docket.
4f549916-0e98-533d-aec8-5b7c34b35c26 | note | 2. Pump storage ITP
85ee8090-d905-5973-a343-568251e9d95c | note | Frequency - Once
a7d66ef6-d59e-52a9-b705-61d5b3be45a0 | note | Inspection Type (Visual, other) - Visual
3c809e28-4248-5020-b82b-e231a25627f7 | note | Inspection: Key - C
f6fd1bea-d1c5-5b39-9483-b4952c5320a2 | note | Inspection: By - IP
65a21a6a-3ab7-4044-ba97-9c2c03c8df62 | checkpoint | 3.3 - Delivery of Pump 3 Motor to site from Downer storage facility.
361a8997-4d4e-5d87-ac16-f29dea536c7f | note | Inspection Point: Quality Control Activity - Check and verify that correct motor is delivered
b0aa6018-15ae-51a5-925a-b8177d07386f | note | Acceptance Criteria - Motor is damage free
4727cb84-ec2c-5549-a4c7-b62935567e09 | note | Verifying Document - 1. KSB delivery docket.
47309c8a-339b-5273-bb2d-d15291d4e229 | note | 2. Pump storage ITP
17dbf657-31c5-53e4-a635-c7ac8e84bcdf | note | Frequency - Once
6d85dd0f-c025-5246-9f63-335b2a27757d | note | Inspection Type (Visual, other) - Visual
fa5974c8-8652-59ed-9b21-e57fc05e5f41 | note | Inspection: Key - C
9e915db2-2c73-55d4-8fa7-2cac62e3f325 | note | Inspection: By - IP
fd7c4b1c-2449-4e37-8c45-067380c5a087 | checkpoint | 3.4 - Delivery of Pump & Motor mounting plate Downer storage facility
807dbf09-b14f-59dc-8d97-b487efffe0a1 | note | Inspection Point: Quality Control Activity - Check & Verify that correct Mounting plate is delivered
ad51e87b-9dbd-5f6c-9bdc-4af02e718eba | note | Acceptance Criteria - Mounting plate is dumensionally correct and is damage free
b05c3591-cc64-5597-8659-ea02c97e1663 | note | Verifying Document - 1. KSB delivery docket.
3a45e670-2d45-5f11-b400-2bc27b840561 | note | 2. Pump storage ITP
02752286-fcde-571f-932d-04c39fca2b6e | note | Frequency - Once
5fe35890-8285-55c6-a8e2-3ae45eac11d0 | note | Inspection Type (Visual, other) - other
a936ecac-8a5c-529e-b281-16c1beecb2f0 | note | Inspection: Key - R
836025bd-8740-52cc-83ed-ee97656b967e | note | Inspection: By - CR
11c2bc38-cb69-403b-b028-6a57ec7a1926 | section | SECTION 4 – IN-PROCESS INSPECTIONS
89d41f40-be56-4205-be78-1f02ef921c12 | checkpoint | 4.2 - On-site assembly
bb4318d4-6d0f-57dc-8676-683e929ed6db | note | Inspection Point: Quality Control Activity - Correct Pump to Mounting Plate Assembly.
401e46f2-3719-525c-85da-3998a12e54af | note | Acceptance Criteria - Ensure all fasteners are tight and toqued to manufacturers specifications
a16e1c1b-6c26-588d-9d70-37a075fac1c1 | note | Verifying Document - KSB documentation & Installation Instructiions
787aca91-0d7d-5c37-a416-9e53f7f67942 | note | Frequency - Once/per pumpset
dc7ce1db-4e72-5b44-90fe-3712b60e8981 | note | Inspection Type (Visual, other) - Visual + Written
70942dc6-5b7b-5ab9-ab49-9316f13237bb | note | Inspection: Key - Inspection
b7828699-9297-589d-9642-a8d3608047ef | note | Inspection: By - IP
7806e442-ecb1-4054-b67a-7f00e3b0e5fb | checkpoint | 4.3 - Pump 3 Installation
b98d24d6-1fbc-592e-b598-4b80eb5e9733 | note | Inspection Point: Quality Control Activity - Correct Mounting plate position on plinth, correct use of fasteners and torque requirements, in accordance with KSB installation instruction
2bf60efc-1d07-5f59-8a72-b58052d97ba5 | note | Acceptance Criteria - Position is determined by the fixed pipework. Ensure alignment of flange face is parallel to wet well wall
59f8ebb7-2d46-5295-9cb5-41ffef664fe9 | note | Verifying Document - Drawing M0001
39d47a9e-e073-5f1e-8385-63eff2d8727d | note | Frequency - Once
da4974c2-6537-5298-8685-2231e3b50399 | note | Inspection Type (Visual, other) - Visual + Photograph
bf760d84-4564-5a23-b3a8-4253594905b9 | note | Inspection: Key - A/D
d36cdeed-a525-5688-972e-b51693de3817 | note | Inspection: By - IP
19b411e7-b891-41e9-a2f5-2ae278b50e24 | checkpoint | 4.4 - Pump 3 Motor Installation
7bffab20-f494-585a-931e-fab6eecdf073 | note | Inspection Point: Quality Control Activity - Motor/Pump shaft alignment
b4a3e3ed-f976-5b7c-bd4a-e81ac0c58292 | note | Acceptance Criteria - Motor and shaft aligment as best as possible
58dd5040-5542-53aa-b23d-de61ff1170fe | note | Verifying Document - KSB documentation & Installation Instructiions. Nothing filal alignment to be undertaken by a Technician - Ref: 561482-ITP-005.3
17f85d29-80b7-5070-baf4-ab921eecb953 | note | Frequency - Once
beb3311c-7f86-5210-a825-c06129977618 | note | Inspection Type (Visual, other) - Visual + Photograph
0a66979b-c3fe-5e48-ad7f-7d30ffa16869 | note | Inspection: Key - A/D
f7a2e0a0-d5c6-5efe-9c46-1a00cf70fa35 | note | Inspection: By - IP
e0e7b0f6-2e01-4458-82c1-6b15a5710627 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
c0c2a096-b699-42c4-bf8c-9080214f042b | checkpoint | 5.1 - Pump 3 & Motor assembly complete
3a5ff1cb-b47a-5f4c-974f-6f7bcc3fcf2b | note | Inspection Point: Quality Control Activity - Proceed with 561482-ITP005.3
990689cc-55f4-5b69-bcef-1f1f3e16ba1a | note | Acceptance Criteria - Pump & Motor bolted to mounting plate and mounted to plinth.
ad31f0e2-d2e0-5385-94ef-09edab383081 | note | Verifying Document - This ITP
71399935-e36b-50d5-a61a-1979b1db3877 | note | Frequency - once
87d4aad6-4211-5c1d-9829-3bd54301127a | note | Inspection Type (Visual, other) - Visual + Document
7ba6a694-6a36-514b-81c5-9f89d49f7bcf | note | Inspection: Key - I
aa385e8e-1437-548e-b820-5afbda4d7479 | note | Inspection: By - IP
cf776114-6195-4b72-8b9f-d7eda9ea622b | checklist | 561482-ITP-005.2 - Pump. Motor Shaft Alignment - Pump 2 | itp | 561482-ITP-005.2 - Pump. Motor Shaft Alignment - Pump 2
fcc3f6cd-2b16-4e25-bc3e-893ac9d39f7e | section | SECTION 3 – RECEIVING INSPECTIONS
f61d0b52-8290-45db-b526-aa984c9aac2c | checkpoint | 3.1 - Align pump and motor shafts and install coupling - Pump & Motor Assembly 2
c5a3a016-2274-570a-96a9-ba71a6ae5570 | note | Inspection Point: Quality Control Activity - Downer to engage a specialist to laser align motor and pump shafts to within 0.025mm
59baec02-0980-5010-b49e-605b142d1167 | note | Acceptance Criteria - Completion of the assebmly to pump and motor 2 including mounting to the plinth.
28111e01-4316-54b3-984d-97481b10fdaf | note | Verifying Document - Downer 561482-ITP-004.2
9d92e142-6604-5aa8-a7db-e634ab48a789 | note | Frequency - once
1a5f6b5f-055f-5d6c-a408-1118d8f213ce | note | Inspection Type (Visual, other) - Visual + Photograph + document provided by specialist
871f1cd6-d632-553f-9804-ebd26f922835 | note | Inspection: Key - QE
60f59dae-d7d7-54b2-938c-4d112adfd516 | note | Inspection: By - D / E
3cbb84b7-b719-41fa-b238-d8f1e137fa4f | section | SECTION 4 – IN-PROCESS INSPECTIONS
fdd805d9-ded6-44ad-b93e-9e87fe8fe8bf | checkpoint | 4.1 - Align pump and motor shafts and install coupling - Pump & Motor Assembly 2
ae231f52-a04f-5b7e-9889-29c1a4474882 | note | Inspection Point: Quality Control Activity - Engage Engineering Specialist to adjust and align motor and pump shafts using laser alignment
952d1da7-e92b-5596-a722-ef2e38cddc38 | note | Acceptance Criteria - Pump and motor shafts are aligned to the specified tolerances on X-Y-Z axis to tolerance of 0.025mm
ccc041ca-1276-5cdc-a876-d241ce505348 | note | Verifying Document - Report provided by Engineering Specialist - Wallace Murray Electrical
3429c640-387f-5ee0-ae24-6d0fe9ffc625 | note | Frequency - once
7354e46c-1d82-5a44-93ea-01831f6d6900 | note | Inspection Type (Visual, other) - Visual + Photograph + document provided by specialist
a873ccd8-a74e-57f6-be90-9eda4d6bb923 | note | Inspection: Key - QE
4ee02c9f-98c1-5c25-9afd-b0d78eabe0e5 | note | Inspection: By - D / E
c22ef4f9-f701-4489-92b0-203b90616733 | checkpoint | 4.2 - Install drive coupling to Pump 2
179b174f-5e40-52b7-b508-33086056c1f0 | note | Inspection Point: Quality Control Activity - Completion of the nstallation of shaft drive coupling - Pump 2
27b4aaeb-206a-56f2-b360-6a5b186f6013 | note | Acceptance Criteria - Completion of Item 4.1
d8726d32-37c5-58ce-a808-a6f4a82f0fbb | note | Verifying Document - Report provided by Engineering Specialist - Wallace Murray Electrical
7cfe7920-7033-5cf7-916f-55e70c12374f | note | Frequency - Once
f7e651f8-e8de-5359-8cfe-30e52cb25726 | note | Inspection Type (Visual, other) - Visual + Photograph
2d226274-4de7-58f7-9497-d4dfa47a7c22 | note | Inspection: Key - A / I
40955d40-9cfd-50d2-a2c6-9fba1a0f6f41 | note | Inspection: By - IP
2406cc7d-0e69-46d4-932f-1cddfa5fef51 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
fe412602-90a4-4c76-a340-e52b69b48c6c | checkpoint | 5.1 - Pump 2 & Motor assembly
fe5a81b2-6c82-5edb-8f4b-2676532cf0ae | note | Inspection Point: Quality Control Activity - Final inspection & check. Rotate motor/pump assembly by hand to esnure smooth operation
57963e0f-f27e-58c0-997e-be393c0d7b34 | note | Acceptance Criteria - Pump/Motor assembly completed and laser alignemt completed and verified. Drive coupling installed
f716c40d-6178-5f9f-8aff-65a0daeaa04d | note | Verifying Document - As per methodology, Shaft lignment verification & Manufacturers Instructions.
e53402b0-f5f7-51bc-bad9-752d5f2ef0b1 | note | ○ Detailed report provided from specialist - Wallace Murray Electrical
ccacc0f0-da82-55a3-830b-1e63289f86ee | note | Frequency - once
7dc2feea-9690-575c-9a93-20dfe0fd9b77 | note | Inspection Type (Visual, other) - Visual + Document
62f8e1c7-6cfa-552c-9880-fe7f9eda7570 | note | Inspection: Key - I
324b6e40-59c6-5417-bf45-87fa8893b203 | note | Inspection: By - IP
5cd85ed7-0b91-401b-ba45-152d4961880c | checklist | 561482-ITP-005.3 - Pump. Motor Shaft Alignment - Pump 3 | itp | 561482-ITP-005.3 - Pump. Motor Shaft Alignment - Pump 3
7a375857-cb6f-4a86-bc78-9ada83fa342e | section | SECTION 3 – RECEIVING INSPECTIONS
27dcceae-aa2b-44d5-bf16-e8750fb5da12 | checkpoint | 3.1 - Align pump and motor shafts and install coupling - Pump & Motor Assembly 3
5893dcb7-823b-53fc-90e2-ed7a5049ae76 | note | Inspection Point: Quality Control Activity - Downer to engage a specialist to laser align motor and pump shafts to within 0.025mm
e8a59a0c-671f-5815-a53c-33d98c03186a | note | Acceptance Criteria - Completion of the assebmly to pump and motor 3 including mounting to the plinth.
ebc75702-0c4e-51f6-8cd0-3d64d3a49a50 | note | Verifying Document - Downer 561482-ITP-004.3
048512a9-5467-5cea-9c36-dc4c7e61963d | note | Frequency - once
24c92551-7f22-59b3-bcd8-ca507cffe7b2 | note | Inspection Type (Visual, other) - Visual + Photograph + document provided by specialist
f240bc3c-0205-58f6-bdcd-cdd62bc343a7 | note | Inspection: Key - QE
0e5b566a-8dcf-566f-b4bf-f36f3d1683ac | note | Inspection: By - D / E
371e6ee1-41e8-4751-8542-a125f745120c | section | SECTION 4 – IN-PROCESS INSPECTIONS
ae2aa987-58d0-4046-b92d-6a5e58daa4b2 | checkpoint | 4.1 - Align pump and motor shafts and install coupling - Pump & Motor Assembly 3
94f927e1-e24c-5f8b-adf4-ae53f8a22775 | note | Inspection Point: Quality Control Activity - Engage Engineering Specialist to adjust and align motor and pump shafts using laser alignment
c82bbd30-5e21-5029-a5be-3213fccd4832 | note | Acceptance Criteria - Pump and motor shafts are aligned to the specified tolerances on X-Y-Z axis to tolerance of 0.025mm
a7370b22-f297-55ab-a381-a68958038191 | note | Verifying Document - Report provided by Engineering Specialist - Wallace Murray Electrical
15b723b7-2f2d-51db-839c-de7c4b08fbf6 | note | Frequency - once
f22e0acb-e13e-5790-84c2-32cc3ec37fb5 | note | Inspection Type (Visual, other) - Visual + Photograph + document provided by specialist
9de4197e-aa94-520d-9013-03e47bde7aba | note | Inspection: Key - QE
5d2bbc37-6777-5175-a06f-e6aa9b336feb | note | Inspection: By - D / E
bd4a6dde-2312-4ad4-bf2a-7ee9dc86c756 | checkpoint | 4.2 - Install drive coupling to Pump 3
3e8086cd-ab5c-51d1-8d0d-0544ae8a2dc6 | note | Inspection Point: Quality Control Activity - Completion of the nstallation of shaft drive coupling - Pump 3
5f622266-cffb-5738-9a52-1fa00d38ab68 | note | Acceptance Criteria - Completion of Item 4.1
8bc8a698-46e6-5b26-a66b-2f4abd61db60 | note | Verifying Document - Report provided by Engineering Specialist - Wallace Murray Electrical
8c21c70e-7d8b-53a4-a808-4edf4490f52a | note | Frequency - Once
b14c57e7-6cd2-5c06-a2a3-18014ea77fe3 | note | Inspection Type (Visual, other) - Visual + Photograph
03aef200-c098-56f9-a677-caca5d3ba887 | note | Inspection: Key - A / I
01abb95a-5825-5a44-83bf-c9335708ef24 | note | Inspection: By - IP
84de3274-b806-4364-bf27-9eb2f3010bb9 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
e5ffc516-3461-4033-8375-11c79c4253c7 | checkpoint | 5.1 - Pump 3 & Motor assembly
5a8b6fa7-6d32-56cc-8715-eaacd1625404 | note | Inspection Point: Quality Control Activity - Final inspection & check. Rotate motor/pump assembly by hand to esnure smooth operation
030e7ebd-e0e8-532a-9826-454b82d22c03 | note | Acceptance Criteria - Pump/Motor assembly completed and laser alignemt completed and verified. Drive coupling installed
44504101-c5f3-585f-a1ec-50900f8ab3b2 | note | Verifying Document - As per methodology, Shaft lignment verification & Manufacturers Instructions.
a87b5f7e-2cad-56f0-9241-bb9b5c787630 | note | ○ Detailed report provided from specialist - Wallace Murray Electrical
3f381d50-90a2-5d54-a32e-26d9cf34891b | note | Frequency - once
3dde77c1-afad-50eb-81b4-0835e4e5d12a | note | Inspection Type (Visual, other) - Visual + Document
9a9a70e3-975a-50d1-badd-29fd03d6a9e0 | note | Inspection: Key - I
40b63d3d-0ebf-5ddd-95e4-24814ffca5df | note | Inspection: By - IP
b8eff675-8b3a-47b5-b0db-e9ef0bd8c878 | checklist | 561482-ITP-006.1 - Pipe & Fitting Installation Pump 1 | itp | 561482-ITP-006.1 - Pipe & Fitting Installation Pump 1
d8606108-ebfb-423c-8430-5a2335d9b85c | section | SECTION 3 – RECEIVING INSPECTIONS
e9765e7b-4e31-4d23-bf9b-1f5a05af5352 | checkpoint | 3.1 - Stainless Steel Pipe components
67672620-43ef-5a3f-8b7d-6e1b4a5ef88c | note | Inspection Point: Quality Control Activity - Obtain the mill certificates for the materials used - 316L Stainless Steel
79d47014-2ca7-5cfa-be4a-c9b9927e0b2f | note | Acceptance Criteria - Documents from the supplier/Manufacturer
6bae09bf-4975-5f73-81b0-f7b6195cf537 | note | Verifying Document - Mill Certificates & Welding certificates
82d24078-91c9-50e8-841c-0600d5f5171c | note | Frequency - Once
abc8b964-d056-53d2-b016-c466a5fc5291 | note | Inspection Type (Visual, other) - Documentation
31145320-c8a3-5798-b5e8-bf64eab9acc7 | note | Inspection: Key - C
6dd768ad-70dd-5a61-9fa0-00a1e643b3a9 | note | Inspection: By - IP
b9fa7e86-aee2-4b55-aaaf-845611b82a1e | checkpoint | 3.2 - Stainless Steel Pipe components
aa78ee3e-9b8c-5a94-a55a-150d28caf04d | note | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been delivered
d25722c5-8e9b-50d8-b5f8-228e72e77e11 | note | Acceptance Criteria - Quantities as shown on the drawings
f0467330-f29e-5459-bbf5-2d1ad12bfd48 | note | Verifying Document - Drawing M0001
3dd1fee4-1dd6-5528-ac44-c83da3e5dc13 | note | ○ Drawing M0002
8ec8dab6-b2a2-5f41-84c5-68158f351b6e | note | ○ Drawing M0003
a3cf5de5-668d-5c90-b8ea-bda32360f224 | note | ○ Drawing M0004
ab38019e-37f1-554a-90b0-d0a88e6f55eb | note | Frequency - Once
2411d3f4-a043-54a5-966b-9e758c53a73f | note | Inspection Type (Visual, other) - Visual
7421e0bc-2d56-52e6-ad11-29b4885464bb | note | Inspection: Key - C
57263c10-8b0a-51e8-8566-03d959482438 | note | Inspection: By - IP
1e3b5505-301b-4a29-85ef-378048a4b6a0 | checkpoint | 3.3 - Stainless Steel Pipe components
fa5912f0-d69d-551d-8b73-a37aca1d6dbb | note | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been manufactured to the correct dimensions
a9a59311-7f10-56a6-8875-854aef1ed8d3 | note | Acceptance Criteria - Dimensions & orientation as shown on the drawings
a0ff312a-3346-52c0-9ffe-d23e37b9d0fe | note | Verifying Document - Drawing M0001
e6a50a71-93d6-5954-99b7-09be0ae25ab1 | note | ○ Drawing M0002
9f0fc32b-8cc1-5494-884c-114d84cca37a | note | ○ Drawing M0003
4fd0c703-4d9d-5683-8c7e-c575907027d4 | note | ○ Drawing M0004
90a4b2b3-04ef-541a-b28c-2eac602fbb63 | note | Frequency - Once
0c169dde-f5be-5f3b-ac8f-56758c46aea1 | note | Inspection Type (Visual, other) - Visual Dimension Inspection
b2cc7987-ffec-5e07-94e0-60d289f6ca07 | note | Inspection: Key - D
c0ad7035-c3e3-565f-898f-896a4d3dfc12 | note | Inspection: By - IP
de3fe68f-67fd-439f-bdd2-e67a9354e14e | checkpoint | 3.4 - Valves & Ancillaries (Blanking Flange)
3da76aee-349f-548a-935d-80884f6213bb | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client
1a35a80a-1ef0-5d1d-bc01-b392a4b9541a | note | Acceptance Criteria - Must be on the Approved Products list
c33a1f54-b26f-5d32-9c9c-c67b0c06c647 | note | Verifying Document - Specification - Approved Materials list
8fef2806-344c-56dd-833b-aa1310066493 | note | Frequency - Once
f8e07a5d-c12b-5d6d-ae15-5e2a5da97d69 | note | Inspection Type (Visual, other) - Visual
6b14be53-cca0-5163-bcb9-a5d93530105e | note | Inspection: Key - C
645c18ec-fa19-5d8c-b789-1095999dc6e9 | note | Inspection: By - IP
a73108ff-003f-4c10-bbfe-df23cf36fc34 | checkpoint | 3.5 - Dress Sets (gaskets & fasteners)
05147020-0c68-5762-93af-258dfaf1b51f | note | Inspection Point: Quality Control Activity - Check and verify that the dress sets are compatible with the flanges and the gasket material is correct. Check correct quantities/sizes/flange patterns etc
14efc88d-e2aa-5377-a626-67d7737f40b5 | note | Acceptance Criteria - Must be on the Approved Products list
696fb468-eeb1-5f60-b200-57347879e2c8 | note | Verifying Document - Specification - Approved Materials list
704a5f48-6ecd-5973-a1b3-9322a2f9552d | note | Frequency - Once
cc791cf9-1b96-5040-bf34-90c121eb497c | note | Inspection Type (Visual, other) - Visual
fc8bae6f-d177-5a8a-8b7f-374f11e64fc7 | note | Inspection: Key - C
5975537e-aae6-5b8c-b387-a1d2f291baa9 | note | Inspection: By - IP
ca555757-2216-49b6-ada2-259186b44f79 | section | SECTION 4 – IN-PROCESS INSPECTIONS
234ce304-6996-47d8-997d-dafd6c7f0803 | checkpoint | 4.1 - Fasten Wet Well side/pick-up to spool (cast in wall) Item # 1
d9ca77c5-f64a-539a-9fe0-28f36b7cfa87 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners
70ecac8f-b2b8-58a1-a13c-d42bdb992f79 | note | Acceptance Criteria - Use diametrically opposed touque sequence
94c12448-4346-5a89-b860-bcc54a177aa2 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
5caa2650-7916-5f43-a0b4-4918b4e20503 | note | Frequency - Each flange
030df472-58b0-53dd-82b7-14d4fcc69cf5 | note | Inspection Type (Visual, other) - Record & attach to ITP
8784db47-019a-52ed-9b2d-dde375ebc6ec | note | Inspection: Key - Inspection
a32c9cde-52ee-5438-8c43-a11b9f4c3746 | note | Inspection: By - IP
cd3c3b76-a124-443f-bd7a-f241674c00c6 | checkpoint | 4.2 - Fasten Dry Well side from spool (cast in wall) Item # 2
ddda5591-02d7-5b21-bb7a-5c46fb966a8a | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
d55462eb-3c5a-587a-89d1-56750fb7120f | note | Acceptance Criteria - Use diametrically opposed touque sequence
ac3d693e-57fa-561e-98f7-1f9e12038f1b | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
71fc488d-23d0-5ea2-9c76-172ea8453304 | note | Frequency - Each Flange
5864a802-cce4-569f-a8fc-8a1542b3c03d | note | Inspection Type (Visual, other) - Record & attach to ITP
2b56a0bd-da85-51c1-8053-a98ab741d001 | note | Inspection: Key - Inspection
0920fd53-3c16-53a4-9085-1ac43130254b | note | Inspection: By - IP
aefae2ae-bff1-4069-90b3-ba748ce0dbee | checkpoint | 4.3 - Blanking Flange150mm (suction side)
c28c4bd3-0700-55f6-81d8-e8868952bbd6 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
bdb3082e-1fa6-5440-b97f-b6d80f08a2dc | note | Acceptance Criteria - Use diametrically opposed touque sequence
26dc2a55-4ea6-55da-90c4-8a5df5cc2564 | note | Verifying Document - As per WSA-109 Australian Water Standards Guidelines - 80N.m
fe50b6d0-badf-5848-ab72-868ace4ef695 | note | Frequency - Each Side of Valve
eb043b32-75c3-556a-931d-deb608a867bc | note | Inspection Type (Visual, other) - Record & attach to ITP
fdacc0d6-5f18-58c5-bf4e-5b780132abc9 | note | Inspection: Key - Inspection
cb133296-8ba9-56ba-9367-e97629a0e40d | note | Inspection: By - IP
874ae99a-8535-440d-8a6e-be877dcd371b | checkpoint | 4.3 - Blanking Flange150mm (Discharge side)
1ad00f9d-520f-50ea-bd68-6c273e456590 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
79556b7e-21ca-5610-95ae-03b0ba7a7b5d | note | Acceptance Criteria - Use diametrically opposed touque sequence
c131d0cb-7c77-57bf-ac0c-a3fb5713784c | note | Verifying Document - As per WSA-109 Australian Water Standards Guidelines - 80N.m
a6e4dc1d-cea6-57b6-b8a5-e7e9271b29f5 | note | Frequency - Each Side of Valve
811bea7d-2158-515d-959f-2c0f00aa9212 | note | Inspection Type (Visual, other) - Record & attach to ITP
beae2312-2df3-5242-9531-4917116f3ea3 | note | Inspection: Key - Inspection
a65a3fa0-4638-587b-95c1-70b08cb1478c | note | Inspection: By - IP
a0be18aa-0a41-472c-bf1b-87273405f569 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
7af52dfa-a61c-4d58-b3bc-5f3b3f0e0f7a | checkpoint | 5.1 - Final inspection to installed pipework
b4ca4837-155d-54c0-b11e-346e8acaebca | note | Inspection Point: Quality Control Activity - At completion of pipework
befff066-16e5-5cac-b4ac-5abf0f3723ce | note | Acceptance Criteria - Flanges are straight and bolts tightened all threads sealed and leak free
1d877c3b-4812-5e5e-81f4-95eeb14450b0 | note | Verifying Document - As per drawings
41278976-0f33-56d1-af3f-c4abf6517896 | note | Frequency - once
9edb0b65-5090-59bb-bf56-95b053c7da62 | note | Inspection Type (Visual, other) - Visual
c142ee9e-93e7-595f-aff9-0fdb87fabdf0 | note | Inspection: Key - I
500f23bd-15ff-54fa-8a1d-c8e3f432f5bc | note | Inspection: By - IP
ecdf23f9-2dce-4a64-ad57-ff520af84341 | checklist | 561482-ITP-006.2 - Pipe & Fitting Installation Pump 2 | itp | 561482-ITP-006.2 - Pipe & Fitting Installation Pump 2
b9880f77-e1c8-44ce-94c2-cebf2646204e | section | SECTION 3 – RECEIVING INSPECTIONS
96911d34-4328-4c52-b275-d0ad6c03d911 | checkpoint | 3.1 - Stainless Steel Pipe components
1ca77c7c-bf6c-55eb-814f-8e84200ea91d | note | Inspection Point: Quality Control Activity - Obtain the mill certificates for the materials used - 316L Stainless Steel
69e0455c-9c4e-511b-9431-44cd9ca76673 | note | Acceptance Criteria - Documents from the supplier/Manufacturer
0c2734df-b74d-51a2-a2a8-47ca3e96b553 | note | Verifying Document - Mill Certificates & Welding certificates
4b4df5a7-4df7-5703-b323-e1792e8435a9 | note | Frequency - Once
d99316f8-7912-52d3-814a-2a6e34b79d3e | note | Inspection Type (Visual, other) - Documentation
2d915948-4443-5143-b2a5-23b4b2c140d9 | note | Inspection: Key - C
e83ac92d-6b01-51ad-b656-c79f916796e1 | note | Inspection: By - IP
0281de9e-c1b8-4367-a651-282796551903 | checkpoint | 3.2 - Stainless Steel Pipe components
2e6501e2-6581-5988-bbbf-179e959e88d8 | note | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been delivered
92f4b7dc-d94e-5b88-9fd3-0181d796c402 | note | Acceptance Criteria - Quantities as shown on the drawings
67ccecd8-69d4-5df3-b076-dd0b8756b050 | note | Verifying Document - Drawing M0001
fddb0806-6092-508c-a395-4f5f75f8a155 | note | ○ Drawing M0002
8886385b-ad13-534e-9f39-7bafa5bfb056 | note | ○ Drawing M0003
fdf90a21-824a-5768-804c-e8c947cc4506 | note | ○ Drawing M0004
a1c7d928-3df6-55c4-bf05-db7f4404cf1e | note | Frequency - Once
8737336a-050d-5d21-8472-3671a54b1483 | note | Inspection Type (Visual, other) - Visual
7f53d69c-1c3e-515e-a4bf-a524fd8be644 | note | Inspection: Key - C
9ef1e997-e97d-5121-8ee2-98162dbff7f3 | note | Inspection: By - IP
2309c2ea-68be-44a9-8302-9c0606e25188 | checkpoint | 3.3 - Stainless Steel Pipe components
8d83767a-1648-56f4-a597-8ed6f8380a5f | note | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been manufactured to the correct dimensions
d14e2a9d-e65c-5b0a-be71-b807bd957027 | note | Acceptance Criteria - Dimensions & orientation as shown on the drawings
5bd07c60-fd46-5908-a55e-e92a2de589f3 | note | Verifying Document - Drawing M0001
436245b2-1d0c-57e1-8aec-4d5df3700fbe | note | ○ Drawing M0002
bcd8cdf7-ce9a-5ced-a1fd-3d370fe812bd | note | ○ Drawing M0003
5670afc3-34a9-597c-a0c0-15579afe5cf6 | note | ○ Drawing M0004
963a9be0-a0bc-5343-866e-36a95c9ff1fe | note | Frequency - Once
29b42713-3f21-59e5-a8dc-1ad7caa31c58 | note | Inspection Type (Visual, other) - Visual Dimension Inspection
5f7f2485-615b-53e4-81ce-dc94987ea330 | note | Inspection: Key - D
6621146e-afb0-502c-914d-eb37ea737e30 | note | Inspection: By - IP
3e16f3e6-42cf-4b22-b499-3a42452d0401 | checkpoint | 3.4 - Valves & Ancillaries
8aeaac1c-c901-5d40-b14c-e5b74e5bf42f | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client
f8bc6db5-14d7-5676-a47c-93751f390838 | note | Acceptance Criteria - Must be on the Approved Products list
ba85bc8c-ab3d-5d6b-91be-8991911237fa | note | Verifying Document - Specification - Approved Materials list
5b8cddff-db5e-5747-b6da-49cd73a7f5d0 | note | Frequency - Once
255c6152-10a0-5f43-a880-947037fd0f83 | note | Inspection Type (Visual, other) - Visual
6b42a257-4535-554f-95a8-85aec352cf41 | note | Inspection: Key - C
0e9615cd-a0ad-5264-9721-d32136f41f66 | note | Inspection: By - IP
1d305302-a30a-4912-8f5b-bdc71feca59d | checkpoint | 3.5 - Dress Sets (gaskets & fasteners)
bfef5849-5b28-5637-b5c1-68f423af4355 | note | Inspection Point: Quality Control Activity - Check and verify that the dress sets are compatible with the flanges and the gasket material is correct. Check correct quantities/sizes/flange patterns etc
c477352d-5940-5742-9d6a-578b6a5b3fd4 | note | Acceptance Criteria - Must be on the Approved Products list
76e0c7a9-e1eb-5689-8f13-129a4114756f | note | Verifying Document - Specification - Approved Materials list
1ba82a15-4e16-5321-8bc0-1a7aececfe25 | note | Frequency - Once
700bbfed-cca6-581a-ab04-5880857b1c3c | note | Inspection Type (Visual, other) - Visual
4d91a056-9d58-5ee8-a927-07c6185935cd | note | Inspection: Key - C
5a1da9fb-833a-5d04-b36f-deb01cec82f8 | note | Inspection: By - IP
58018d37-34f5-4cb8-a119-6deab1f412f6 | section | SECTION 4 – IN-PROCESS INSPECTIONS
d6747565-bff8-4321-9945-002f3452ecc2 | checkpoint | 4.1 - Fasten Wet Well side/pick-up to spool (cast in wall) Item # 1
5611d823-2f7c-5390-952b-3c7fc5cf5b01 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners
aa1a8fee-607f-56dd-baff-db3175e363ae | note | Acceptance Criteria - Use diametrically opposed touque sequence
556e4882-147a-55f5-83a1-cadeb808f0d9 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
e053d352-c643-5343-8643-18016b447bdb | note | Frequency - Each flange
19aa908e-1457-5deb-9ea0-a0c48c48a269 | note | Inspection Type (Visual, other) - Record & attach to ITP
93dfc4c7-5e24-5a72-85bb-89787013cdaf | note | Inspection: Key - Inspection
c5ebfab9-ede5-55ca-81e8-3afb7eaa6255 | note | Inspection: By - IP
30328ebf-df38-4bc4-bab4-3fb159ddcac2 | checkpoint | 4.2 - Fasten Dry Well side from spool (cast in wall) Item # 2
dfdb7daf-640d-5971-bbb8-6b4bcc687b55 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
86d43d3e-2599-5f34-bebe-d4fd71178f8a | note | Acceptance Criteria - Use diametrically opposed touque sequence
aa492383-856f-5268-a57f-9b17ac58e4a8 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
2989b14d-b129-5dda-9547-c7b2b0af22dc | note | Frequency - Each Flange
8848765d-a6ad-55a7-ba42-a1d70e0d71d5 | note | Inspection Type (Visual, other) - Record & attach to ITP
c17377b7-550e-5d1e-bd77-37ea4e61c759 | note | Inspection: Key - Inspection
13376683-82cb-5b62-864d-6f732344d5e9 | note | Inspection: By - IP
33bf0813-5649-4ba1-8e50-021015259516 | checkpoint | 4.3 - Isolation Valve 150mm Item # 3 (suction side)
c88d13e6-fd25-5b51-bf35-b70cc7887658 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
1e7defdd-25e1-511f-b5c4-1905fa029fdb | note | Acceptance Criteria - Use diametrically opposed touque sequence
04526a9e-aa93-59e6-ae75-fddb7971917d | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
a86685e2-0e0d-59dc-9111-76bf2205c013 | note | Frequency - Each Side of Valve
b59f6f92-8a7f-5eba-885b-4b52e7237e5d | note | Inspection Type (Visual, other) - Record & attach to ITP
7d321e87-18d8-5f40-9d7b-4e322c9b0a15 | note | Inspection: Key - Inspection
8990b10f-32bf-5d62-b05b-0b82ccb0801b | note | Inspection: By - IP
9b7e863b-cd0a-4ff3-9a74-515c0d40b176 | checkpoint | 4.4 - 150mm Dismantling joint (suction side) Item#4
a48d90ae-82fe-5233-bd66-4e686e72b2f4 | note | Inspection Point: Quality Control Activity - Torque fasteners to relevant water standards
4d90d7c6-8895-5bf4-b85a-7713f7e39b4d | note | Acceptance Criteria - Use diametrically opposed touque sequence and manufactruers instructions
781a06a1-af8b-52f2-9f00-56c477bd1909 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
806b0b2a-8c4b-5dea-9ff6-3b790343bfe6 | note | Frequency - Once
36382eac-9dc8-5927-a4af-78d217505a4a | note | Inspection Type (Visual, other) - Record & attach to ITP
0e627b03-c207-598f-8225-09442e1336c8 | note | Inspection: Key - Inspection
3353e402-eab8-5b45-9851-42fb90356b25 | note | Inspection: By - IP
5a83b1c1-8876-4250-b65d-ee9da2f35050 | checkpoint | 4.5 - 150mm Flange Adaptor Spool. Item # 5
81e50aae-8f77-5470-ab6f-2a2e2c196333 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
a573a8d7-c9f8-559a-b18a-5425d20f41af | note | Acceptance Criteria - Use diametrically opposed touque sequence
62c6d8b6-bc93-59ff-a168-5315908b8647 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
158f44a9-84f9-54a5-97bf-ddbe4bbad44e | note | Frequency - Once
517a35cf-6616-5926-8e05-eefea773b971 | note | Inspection Type (Visual, other) - Record & attach to ITP
e17b08cb-08a8-55ca-a9ff-c9f07c1f56eb | note | Inspection: Key - Inspection
d2a7b2e0-5fb1-5c4e-9c72-7b700b1e0fb3 | note | Inspection: By - IP
941b9736-617f-4385-9d4c-b0e6817f37bb | checkpoint | 4.6 - 100mm to150mm Sweeping Flange Adaptor Spool. Item # 6
d1fa2a07-1b60-5dd7-abd8-1453ff6e4a2b | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
f2980767-a659-51ce-8079-9ea2c13ec066 | note | Acceptance Criteria - Use diametrically opposed touque sequence
3fe7d66c-b900-5128-b854-560c3479e413 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
fe919e49-f083-58ee-b72b-91c0ec7641bc | note | Frequency - Once
f724fd6c-4264-5f2a-868d-cdbfe8de81c9 | note | Inspection Type (Visual, other) - Record & attach to ITP
ba7960e7-bd71-5bb6-8c43-e06007ddde1d | note | Inspection: Key - Inspection
5bbb5043-b9a1-56cf-8a78-1b6a60f82e6c | note | Inspection: By - IP
7d28013e-08a6-451c-8899-0b1a746cc8b2 | checkpoint | 4.7 - 150mm swing check valve. Item # 7
68fedaf9-1c93-52f8-8494-ccc105f996b2 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
a8f688d7-93aa-5b6e-9469-075f65178db8 | note | Acceptance Criteria - Use diametrically opposed touque sequence
c8ba7434-f511-5c49-a37a-36db29a00022 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
7e666594-265e-5bcd-8c1c-ff2ed6d9a15f | note | Frequency - Each Side of Valve
60a5f616-5575-5f5f-8058-6dd7fe19633b | note | Inspection Type (Visual, other) - Record & attach to ITP
55107423-76a6-5897-9ffa-3b7f2ea4af32 | note | Inspection: Key - Inspection
560b2abf-8eca-5c0d-be4a-5d1a01e19563 | note | Inspection: By - IP
f8549c83-313d-436d-be67-c3d451d64d8c | checkpoint | 4.8 - 150mm Sweeping Spool (discharge). Item # 8
ca7cab1a-1b5c-55b8-87aa-0799bf9b2293 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
0cfd491f-0e90-5dfd-b0ad-e030e97ae621 | note | Acceptance Criteria - Use diametrically opposed touque sequence
02bdc93c-e0a7-5f8b-9487-5848d26917fa | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
64389bfd-f807-583c-82fb-0871e8d1c01b | note | Frequency - Once
c36c7b08-aceb-56df-b0bb-ebbcbe9ecdab | note | Inspection Type (Visual, other) - Record & attach to ITP
7702735e-619c-5592-8720-626b24c70212 | note | Inspection: Key - Inspection
0406c148-cce0-510e-bca8-296a55d02692 | note | Inspection: By - IP
b7716a82-861b-438e-8787-925137762fb9 | checkpoint | 4.9 - 150mm Dismantling joint (discharge side) Item#4
decf3ce8-edf3-5a76-80e1-3da848e0fe8d | note | Inspection Point: Quality Control Activity - Torque fasteners to relevant water standards
d626b6c0-483e-541b-bf86-ff7391bc3819 | note | Acceptance Criteria - Use diametrically opposed touque sequence and manufactruers instructions
301e77bc-f1bc-5d5d-b87d-0452a23b6372 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
3563dc44-029b-5290-a2c1-b2236befd340 | note | Frequency - Once
381d90d5-95a8-5f72-8a27-8bc534da706e | note | Inspection Type (Visual, other) - Record & attach to ITP
18aac799-0742-5ab4-9a34-0bdb3e479e09 | note | Inspection: Key - Inspection
0cace3a1-a025-5494-b9f0-5733503b2d35 | note | Inspection: By - IP
3603ab52-fe18-476c-94e5-0424786ca1f4 | checkpoint | 4.10 - Isolation Valve 150mm Item # 3 (discharge side)
613fd92e-aae0-5759-bd40-e3eacfbd46c8 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
6f79b1de-5e89-5d8c-9f88-1a06b6589cfa | note | Acceptance Criteria - Use diametrically opposed touque sequence
88a2feda-4480-54d3-a5ff-de3ee216cde3 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
cb284ec9-8031-5b30-80b9-36a15b0d402c | note | Frequency - Each Side of Valve
43721e36-87af-55a4-a053-bc15ca9b818b | note | Inspection Type (Visual, other) - Record & attach to ITP
a8f8d25f-7be5-5f2f-add1-81c17ff56564 | note | Inspection: Key - Inspection
0cd9f547-d66a-5629-a5eb-75060ed5a389 | note | Inspection: By - IP
11901f3e-bad4-476f-9353-5bd85eb6d399 | checkpoint | 4.11 - Pipework bracketing installed and is secure.
fdbb4115-1f02-5f6c-87ec-78431e7f23f4 | note | Inspection Point: Quality Control Activity - At completion of pipework
bd4766f0-a879-5893-a35e-edffc4a7584f | note | Acceptance Criteria - Pipework complete and installed. Adjustable brackets
6d6cf4a5-3422-519f-881a-ea13227d7b6e | note | Verifying Document - As indicated on the drawings
39f4cd8a-f3a7-5bca-bd6a-922163e9c699 | note | Frequency - once
827754bb-ba28-5e8d-963f-6bf3d621ec9b | note | Inspection Type (Visual, other) - Visual
fa247592-bcc4-5d5e-ac1b-340d18aa614a | note | Inspection: Key - I
3b2fc194-2ffe-5380-9d62-14f093c87b43 | note | Inspection: By - IP
82f82659-7981-4ab8-9106-de9eef390547 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
b15fce3b-9ae2-4f16-a2d4-09d96b0acff5 | checkpoint | 5.1 - Final inspection to installed pipework
56eb81d5-3d61-5517-b44f-e1a39cacc9a6 | note | Inspection Point: Quality Control Activity - At completion of pipework
1a1dd471-95ec-598c-9a5e-751b709eb234 | note | Acceptance Criteria - Flanges are straight and bolts tightened all threads sealed and leak free
7ef4cf0e-89f7-5e4c-8816-011089a43493 | note | Verifying Document - As per drawings
de0e872c-0b95-5304-85cf-38246875cb19 | note | Frequency - once
9ad6143d-254a-5120-9d01-878b06c1852d | note | Inspection Type (Visual, other) - Visual
7a864cc4-8d05-5475-9940-1b6353fa7adc | note | Inspection: Key - I
c9892299-d337-56f1-a9c3-e5cc795b04ee | note | Inspection: By - IP
559938ce-47b6-4e93-a7d5-54028306e682 | checkpoint | 5.2 - Instrumentation. e.g. Pressure transducers and sensors are fitted correctly - No Damage
e471ec81-aedb-518f-8302-a91804279c2d | note | Inspection Point: Quality Control Activity - At completion of pipework
e1ed3373-38a8-50a9-be8e-493c8a0d7736 | note | Acceptance Criteria - Pipework is installed and correct fittings installed to accept the instrumentation
fe28191c-66e5-5205-bcfd-b87735094642 | note | Verifying Document - As per drawing schematics
3a726664-27a0-521c-a989-123ba74f2a6e | note | Frequency - once
2456b281-b35e-5116-b2b6-401fe6351b81 | note | Inspection Type (Visual, other) - Visual
82a9c429-392e-5900-9b8f-3043d16a7bb3 | note | Inspection: Key - I
832f2628-66df-5624-9099-3ece0f4f20df | note | Inspection: By - IP
92a84c7a-489c-41af-bd0e-ad686a4146a1 | checkpoint | 5.3 - Pipework bracketing installed and is secure.
3e3a7bda-df45-5036-992c-7de32f2f4cfa | note | Inspection Point: Quality Control Activity - At completion of pipework
f38349a3-375a-5916-a563-1712c62d9bae | note | Acceptance Criteria - Pipework complete and installed
d5475874-c751-5ed5-957d-af6419b79c28 | note | Verifying Document - As per drawings
94649beb-7e6c-58f0-94b6-e4b1edaa5356 | note | Frequency - once
36576e85-e91d-5db6-9caf-b33940f329af | note | Inspection Type (Visual, other) - Visual
5552ad98-941f-5916-8eb3-84151c5b5f44 | note | Inspection: Key - I
c5e393ae-714d-5506-9f78-bd60eaac0efb | note | Inspection: By - IP
cfb97827-fd38-4581-bc10-2e87e551ab85 | checklist | 561482-ITP-006.3 - Pipe & Fitting Installation Pump 3 | itp | 561482-ITP-006.3 - Pipe & Fitting Installation Pump 3
b42c6ac3-9255-4690-9283-4b31fb8454ac | section | SECTION 3 – RECEIVING INSPECTIONS
d0fede74-778d-4039-9331-52d1cdd65e22 | checkpoint | 3.1 - Stainless Steel Pipe components
c5261988-f054-51c9-8b4c-04b4e3670aee | note | Inspection Point: Quality Control Activity - Obtain the mill certificates for the materials used - 316L Stainless Steel
90992016-0cb2-58dd-aac0-205155fb4a76 | note | Acceptance Criteria - Documents from the supplier/Manufacturer
612e0151-a290-52ff-803f-03f5025bfbc4 | note | Verifying Document - Mill Certificates & Welding certificates
303e51ca-5fc0-5d2c-b83b-2b56eaf237e1 | note | Frequency - Once
a49bcd6a-a74f-5ffc-bdbb-c2a6950ae3fc | note | Inspection Type (Visual, other) - Documentation
79d45f11-90d8-54a2-8f8b-5a9b302c8d6e | note | Inspection: Key - C
c42324be-2eb0-5ca4-b956-62d44bff93f7 | note | Inspection: By - IP
8a9744e4-c18e-413a-aa00-1e123e2da9b4 | checkpoint | 3.2 - Stainless Steel Pipe components
93e85615-459e-59ba-b9a9-67ff7ff2230a | note | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been delivered
74c2a989-78f2-52aa-aa61-7824b3283fd3 | note | Acceptance Criteria - Quantities as shown on the drawings
c80fee4e-2aa0-5b6a-8e70-75f208f1f132 | note | Verifying Document - Drawing M0001
4d455161-f3a4-5d85-b6ae-46a0f4a3b725 | note | ○ Drawing M0002
122b0d82-d4b1-5114-833f-04df1be2aca2 | note | ○ Drawing M0003
98cfc088-855b-5608-a4e5-11caa6460a8b | note | ○ Drawing M0004
96b552a5-f253-5f49-816f-80ac78fccb3a | note | Frequency - Once
ab978ea9-71c3-5c1d-bdb3-b85cc676c1d3 | note | Inspection Type (Visual, other) - Visual
56a7278b-8b07-5c55-ace3-7851639b12a4 | note | Inspection: Key - C
cf9e8a08-cd79-512c-8d7b-4493f8616352 | note | Inspection: By - IP
ccaf9a83-66b6-4782-a28e-ca7e65417faa | checkpoint | 3.3 - Stainless Steel Pipe components
1f1d2f1e-050b-5b7b-83b5-2dc8b7e34179 | note | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been manufactured to the correct dimensions
17818ac9-ebc8-5160-abc6-55ad05762a60 | note | Acceptance Criteria - Dimensions & orientation as shown on the drawings
711ab90d-75c1-5152-a09a-f6b7c75da0a6 | note | Verifying Document - Drawing M0001
8261307c-0f5b-5458-92c6-f7350a95895c | note | ○ Drawing M0002
e96ae188-664f-5016-aa7a-85cdcc5486f1 | note | ○ Drawing M0003
a33b8f79-b4bf-5779-b809-59a232eaae00 | note | ○ Drawing M0004
80482a50-0812-50ac-923e-d8cba19197ba | note | Frequency - Once
5432dcd7-2792-5b10-b041-823a3fb7d994 | note | Inspection Type (Visual, other) - Visual Dimension Inspection
1f7a3f41-27e5-5d8e-abf2-2d80e1644422 | note | Inspection: Key - D
82869995-fb43-5875-825a-bc7c7419e6f1 | note | Inspection: By - IP
46dda6c9-eda8-4598-94a5-de7b19142f97 | checkpoint | 3.4 - Valves & Ancillaries
0e35853f-36d9-5eb3-be60-a18c65ca4cb3 | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client
96b1d56b-7663-5304-97b5-ee7039382770 | note | Acceptance Criteria - Must be on the Approved Products list
796279dc-466b-5071-8d06-f1398902b3e9 | note | Verifying Document - Specification - Approved Materials list
bb1e9ae0-5fed-5657-833a-77e67aa19c45 | note | Frequency - Once
7b3d49b5-4630-5e2f-8a4b-a9537db863f3 | note | Inspection Type (Visual, other) - Visual
caa595ac-254a-568e-9dc9-2b148a9e66c7 | note | Inspection: Key - C
4aa88059-8c23-561c-9487-e9f2c3accdde | note | Inspection: By - IP
2de45f86-3031-446a-b7a7-762599ae6ade | checkpoint | 3.5 - Dress Sets (gaskets & fasteners)
3a0f1f99-1269-5fe6-9828-3c6e6ac4156d | note | Inspection Point: Quality Control Activity - Check and verify that the dress sets are compatible with the flanges and the gasket material is correct. Check correct quantities/sizes/flange patterns etc
8f9cb03d-8536-5e99-a00c-678a24383dad | note | Acceptance Criteria - Must be on the Approved Products list
1cce3895-a10a-51aa-8c5c-71400c8cf6cd | note | Verifying Document - Specification - Approved Materials list
620833ed-05a6-54c6-a9d4-e103b05392e3 | note | Frequency - Once
0fde40c1-4319-5aeb-8476-be8b3f397606 | note | Inspection Type (Visual, other) - Visual
b0c0e7d7-9e0b-5c67-a93c-218a10dd15fe | note | Inspection: Key - C
50ca292e-0c4f-5a2b-bfe4-f9a2835b031a | note | Inspection: By - IP
1082815b-7f12-46f4-9644-53168c3469c6 | section | SECTION 4 – IN-PROCESS INSPECTIONS
f5970011-e40e-4088-b276-83d52ce4e0fe | checkpoint | 4.1 - Fasten Wet Well side/pick-up to spool (cast in wall) Item # 1
f355917e-fb89-5e8f-af9f-27c9c7e6fe28 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners
537059cc-1d7e-53da-ba51-3b8ff85a3653 | note | Acceptance Criteria - Use diametrically opposed touque sequence
0b9dc1c6-98a4-5ddb-bde9-be90e4d9620d | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
6b96b962-7b72-5c6e-bbac-108c8f7a0006 | note | Frequency - Each flange
c851e559-1641-5c9d-b748-bf96129dfd4f | note | Inspection Type (Visual, other) - Record & attach to ITP
15db1b77-09c7-5ac7-8a8a-0b726ef473f9 | note | Inspection: Key - Inspection
63a365ba-80fe-5ce4-8932-d345328a1b14 | note | Inspection: By - IP
854e8896-1f6d-4066-a508-2217683d4f2c | checkpoint | 4.2 - Fasten Dry Well side from spool (cast in wall) Item # 2
f7f7c8bf-5cb6-53dc-9bae-453c31febc73 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
7b36e7c6-ebab-5a11-b189-ef975fa4f733 | note | Acceptance Criteria - Use diametrically opposed touque sequence
58b33258-be7d-5eea-8cc7-d96aaf1f417d | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
b3e821db-b62e-5a15-b85b-0948edd9f0b7 | note | Frequency - Each Flange
577fb6a9-197a-5aed-865a-d50c26ce0e70 | note | Inspection Type (Visual, other) - Record & attach to ITP
d93fce37-d7a6-52d5-ab11-5a9bf6809568 | note | Inspection: Key - Inspection
3c3aeb3a-2ad6-5b6a-966d-e6518052c073 | note | Inspection: By - IP
29d4a627-364f-4b14-a925-4864b028b8c9 | checkpoint | 4.3 - Isolation Valve 150mm Item # 3 (suction side)
0375ec7b-7d15-57d9-98d2-8e7a543a7ad4 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
482efba2-a973-515e-8a77-ed5ef032b14c | note | Acceptance Criteria - Use diametrically opposed touque sequence
39cd518a-9e5b-57e6-a1f5-3443096bfc0f | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
f61b8005-d97d-5593-8a5c-4ff7843afc30 | note | Frequency - Each Side of Valve
c2687255-cc87-5ad2-ba69-828d75baea83 | note | Inspection Type (Visual, other) - Record & attach to ITP
4fd3cec5-6b22-5c4b-b5bd-4cb0fbb91c5c | note | Inspection: Key - Inspection
7957a4a6-5c9c-57e4-a737-f55aa8af4313 | note | Inspection: By - IP
78efdffc-e0d1-4a57-a893-d9d17664779b | checkpoint | 4.4 - 150mm Dismantling joint (suction side) Item#4
a232328d-1f84-5b34-ab76-5b73f4a5dd9a | note | Inspection Point: Quality Control Activity - Torque fasteners to relevant water standards
b1565531-640b-5c9a-8273-2b4821279298 | note | Acceptance Criteria - Use diametrically opposed touque sequence and manufactruers instructions
830f0a34-7b0f-5759-a540-74605dbf42ce | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
6bff1e55-d2dc-5be7-a076-27329adebcb4 | note | Frequency - Once
44ddfa07-81c0-5538-a6fd-cb9bf95634d8 | note | Inspection Type (Visual, other) - Record & attach to ITP
39aea7bc-928e-5903-8dab-9226fba79dfa | note | Inspection: Key - Inspection
53da1185-624a-573e-9108-c132fcbd0dc6 | note | Inspection: By - IP
983d988b-0e8d-45e6-94aa-7f067703fe6b | checkpoint | 4.5 - 150mm Flange Adaptor Spool. Item # 5
22ae6640-b6ab-5ade-bfe8-4e59b38da88f | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
577d5fce-8180-5838-9847-3d688ea8078a | note | Acceptance Criteria - Use diametrically opposed touque sequence
466efce7-f27c-5037-815e-77fcb0958732 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
66b484d4-df7e-513c-a96e-1b8106804c11 | note | Frequency - Once
ffab5aca-e2a5-505f-a931-81ce19d90787 | note | Inspection Type (Visual, other) - Record & attach to ITP
15ea6d3c-e4f6-5cd4-a165-b997725bb5ff | note | Inspection: Key - Inspection
83c77a7e-2270-5660-85b2-0a2dcd246852 | note | Inspection: By - IP
ff1b21a6-f2fe-4b77-8173-9ea539eccbb1 | checkpoint | 4.6 - 100mm to150mm Sweeping Flange Adaptor Spool. Item # 6
3d1fe5a6-3833-508a-bf2d-0f13ab178d49 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
2e9f5604-b5d7-5cc6-8d38-74062df8e349 | note | Acceptance Criteria - Use diametrically opposed touque sequence
abc9e1db-baa8-5220-ade7-c52485950a5f | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
ee43245d-7ab0-5f11-bc12-f726955fb47f | note | Frequency - Once
d2da54c9-2b8f-5c09-8efb-af0a07c2c819 | note | Inspection Type (Visual, other) - Record & attach to ITP
9e08647e-0b81-512f-81e2-5ee3c4a730c0 | note | Inspection: Key - Inspection
4083040e-dd17-5967-baa4-9f923ce2b4e6 | note | Inspection: By - IP
84784027-b08b-4162-976b-21c4fe506445 | checkpoint | 4.7 - 150mm swing check valve. Item # 7
e007c05f-4528-5056-b3be-fa1f538a265b | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
b319815a-8042-5f77-b56c-03fd9a010d9c | note | Acceptance Criteria - Use diametrically opposed touque sequence
f465c2ab-ac7e-53a3-b9c4-cf11223ff9dc | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
9fccb7f6-dea7-55c0-8b1f-3afd00e35696 | note | Frequency - Each Side of Valve
4f985bc2-20c8-5a6c-ae90-eb4583041f36 | note | Inspection Type (Visual, other) - Record & attach to ITP
5a1a4954-7b01-5fd9-98a4-5e8be388130a | note | Inspection: Key - Inspection
94d6fb25-27af-55c3-8d3e-f99519bb3b99 | note | Inspection: By - IP
a770471e-9117-4df3-a739-ce233c50b5d4 | checkpoint | 4.8 - 150mm Sweeping Spool (discharge). Item # 8
ff881459-5ae1-5ff5-8ae0-c5369e90a1f5 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
02184b3f-322e-5b0e-a5e8-70106b42815e | note | Acceptance Criteria - Use diametrically opposed touque sequence
6c86f0d4-c930-5b68-a35b-6a7f18890bcc | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
8644d680-9739-5c18-9126-37d15ff4cf23 | note | Frequency - Once
e4bff31f-3106-5ec2-9085-4dd165a8a89c | note | Inspection Type (Visual, other) - Record & attach to ITP
1e23501d-30c4-547d-b5a4-75fabad412ee | note | Inspection: Key - Inspection
d1c248be-adc4-5ce1-b9d7-6836a54f663f | note | Inspection: By - IP
60ada0fe-835e-48f4-918d-bc6975b1649a | checkpoint | 4.9 - 150mm Dismantling joint (discharge side) Item#4
e5da41ac-543b-5c5f-a433-1ad58616d74e | note | Inspection Point: Quality Control Activity - Torque fasteners to relevant water standards
b98d7e7c-9852-5827-855f-c0dcff68ad3a | note | Acceptance Criteria - Use diametrically opposed touque sequence and manufactruers instructions
8957ed58-2574-5547-9aca-9a9df9cc6ca1 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
5d126ca8-0c2e-5ba1-aaa9-53f7d939dc4d | note | Frequency - Once
8437cc27-e011-5886-b9c6-a07a6caf6475 | note | Inspection Type (Visual, other) - Record & attach to ITP
1009570e-8d54-5add-ac16-1f9183d87b1e | note | Inspection: Key - Inspection
365cda3d-1a48-5e5b-aa2b-abf18b90e42e | note | Inspection: By - IP
638157d3-3704-46a1-8a15-694a4dc3de01 | checkpoint | 4.10 - Isolation Valve 150mm Item # 3 (discharge side)
5fd86e09-fa49-5167-ad1a-5b5336f49421 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
84bafd06-76e3-5197-927f-692dd9ff29fa | note | Acceptance Criteria - Use diametrically opposed touque sequence
5c3073c1-dd0d-5525-a388-5eef3f2bbc14 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
76f19e05-b359-5b93-9187-8f3e78ef659d | note | Frequency - Each Side of Valve
765b8401-b109-5016-8ec6-a3ca954b58e2 | note | Inspection Type (Visual, other) - Record & attach to ITP
15b9e92e-f86b-5682-93cb-b5b83a1692de | note | Inspection: Key - Inspection
c3eed160-23a7-5a81-9f94-6a36ae3f1a6d | note | Inspection: By - IP
7ada870e-4791-485f-98bc-28bc940bf291 | checkpoint | 4.11 - Pipework bracketing installed and is secure.
e57d93b4-344c-54cf-8b18-5c385752d8c9 | note | Inspection Point: Quality Control Activity - At completion of pipework
565a8e62-b6eb-5a39-97fb-409ffea4f689 | note | Acceptance Criteria - Pipework complete and installed. Adjustable brackets
f761ac55-9b2d-5d21-bbb1-311c9def2252 | note | Verifying Document - As indicated on the drawings
d2d1ab37-64be-5247-98b3-69974f35b001 | note | Frequency - once
7d310d1f-fd2c-508c-a296-a6a4141fb9ca | note | Inspection Type (Visual, other) - Visual
fb78e04f-851b-5693-b98c-78ed9038210d | note | Inspection: Key - I
b5bc7163-808d-5024-b340-c0f0cdbc4ac2 | note | Inspection: By - IP
d791a7e9-3ae7-4fd1-99eb-e8ba37d0929e | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
06eac443-4ff1-4eca-80fa-3fc62b4def83 | checkpoint | 5.1 - Final inspection to installed pipework
ad903ae2-fc4b-5736-bdbc-85d2b2b3606b | note | Inspection Point: Quality Control Activity - At completion of pipework
3d0199d3-c4b1-58f8-9d34-b11941790c6d | note | Acceptance Criteria - Flanges are straight and bolts tightened all threads sealed and leak free
163207f0-641e-51d1-9a7c-4a39ae75fc57 | note | Verifying Document - As per drawings
60db29ca-3bca-5fda-9f81-6b88f6d641b5 | note | Frequency - once
fca7dc03-6751-5cb1-a956-7864a139045b | note | Inspection Type (Visual, other) - Visual
5e9b541a-5cc1-52f7-917b-7b751b284b66 | note | Inspection: Key - I
6e1dea6f-aba1-5369-9bbc-7ad039e32527 | note | Inspection: By - IP
02ed4267-273f-4fba-a0cc-8a29aa4e0e97 | checkpoint | 5.2 - Instrumentation. e.g. Pressure transducers and sensors are fitted correctly - No Damage
152cd870-74d1-5982-8143-c31480428267 | note | Inspection Point: Quality Control Activity - At completion of pipework
a3c23e62-1611-5ac3-a93e-b6ec7779c358 | note | Acceptance Criteria - Pipework is installed and correct fittings installed to accept the instrumentation
511ccd85-cfd8-58a8-b1bc-8da5c6e52864 | note | Verifying Document - As per drawing schematics
91ccd3c9-814f-5a5b-99bd-254fe5a4a2f4 | note | Frequency - once
e5b88775-4a7b-53a7-8aad-1a7996192535 | note | Inspection Type (Visual, other) - Visual
e5860c8a-1ffb-5663-8314-32acac5b437b | note | Inspection: Key - I
5198f3f0-ba55-5d05-b523-ae2ef08c5553 | note | Inspection: By - IP
66dfa977-ec12-496a-b3c7-0f81ca7931d2 | checkpoint | 5.3 - Pipework bracketing installed and is secure.
6d270fbc-facc-5a6c-917b-ac9a85071b88 | note | Inspection Point: Quality Control Activity - At completion of pipework
11e86d63-2962-500c-b784-9bde6c6ecdf6 | note | Acceptance Criteria - Pipework complete and installed
0f297426-3853-59b0-9e41-7765922019be | note | Verifying Document - As per drawings
8bd62f33-3999-5f6a-8264-8f6aef453293 | note | Frequency - once
a07bd5e3-6693-599d-a840-5b8c43406a34 | note | Inspection Type (Visual, other) - Visual
c4b4d552-6e28-5728-8e9d-9d35cca50d6b | note | Inspection: Key - I
eb2166f4-24d0-5d16-a977-13f7bdc081ce | note | Inspection: By - IP
2d811e6b-5f68-4566-884a-670cda68e9e7 | checklist | 561482-ITP-007.1 - Wet Well Wall Penetration 1 pour | itp | 561482-ITP-007.1 - Wet Well Wall Penetration 1 pour
22565930-02ed-47f8-bad0-430492d2b5dd | section | SECTION 3 – RECEIVING INSPECTIONS
6107b9b2-3892-4769-b565-dc6392124642 | checkpoint | 3.1 - Grout - SIKA MonoTop- 438R
3e263f13-ac94-50a2-90c2-bb04d9d3dff4 | note | Inspection Point: Quality Control Activity - Calculate Quantity
ac8ee9aa-aa58-59b5-b2f8-32dbc81b6164 | note | Acceptance Criteria - Correct volume to be calculated
fb0d8403-34be-520c-8571-1109c2963761 | note | Verifying Document - Product Datasheet
7ed15ed7-7c94-5d9c-9622-c84a3612655f | note | Frequency - Once
3aa542a0-8115-506c-8d4a-fc74ea622ddd | note | Inspection Type (Visual, other) - Written
85af33fa-b9e3-5e81-b5cc-6f14dbfe4d97 | note | Inspection: Key - R
5655b928-07be-522d-a0e4-3404f96086d9 | note | Inspection: By - CR
5d8fee43-1a9a-4b1e-a3fd-dfaddd761847 | checkpoint | 3.2 - Installed Reinforcing
8fad7073-4491-51a3-9d3d-6218b72da051 | note | Inspection Point: Quality Control Activity - Measure and check
b120ad3a-e746-5f43-a945-14b76604a782 | note | Acceptance Criteria - Matches Design Drawings
6a72a2bd-797d-5c01-944a-a302eb87d72e | note | Verifying Document - Drawing M0003
97cab6d5-4c09-5ecc-9cf0-d32f5d29bb1d | note | Frequency - Once
11cf89d3-103f-591d-92fd-6bc638d22b30 | note | Inspection Type (Visual, other) - Visual + Photographs
0e96cc18-bbec-52d8-a000-51c83180acbe | note | Inspection: Key - V
c398f192-8eda-5645-ad61-ad6c78d1d042 | note | Inspection: By - IP
a2e27920-d9f3-4157-882c-b80651633182 | checkpoint | 3.3 - Spool/Puddle Flange
e714f129-396e-5a70-8f25-d3418d00ded1 | note | Inspection Point: Quality Control Activity - Measure and check
b473b24f-5e51-57ae-b64e-25ce32a91364 | note | Acceptance Criteria - Pipework is straight and parallel to structure & pump
973ce2c0-9192-5114-8e2c-994fde379926 | note | Verifying Document - As per drawing M0001 & M0002
9787efda-c91e-5d9d-8fd6-1d8e98591ed4 | note | Frequency - Once
2ba46067-e7ef-53c0-a18d-42c357b04f4d | note | Inspection Type (Visual, other) - Visual + Photographs
d0e7f62e-0a69-5000-8d9e-3c5eb1964b8d | note | Inspection: Key - V
af9e0262-aef3-5516-876f-7399361295db | note | Inspection: By - IP
3a0d5b87-cb8f-4807-910b-d9d6a2f3f463 | section | SECTION 4 – IN-PROCESS INSPECTIONS
c43ba4cb-ff41-4154-a14a-7f6ccaddaa20 | checkpoint | 4.1 - Boxing of penertation
8d749ef8-5cfb-5281-a295-d0dc2d1f4851 | note | Inspection Point: Quality Control Activity - Measure & Check. Ensure perimeter of boxing and pipe penetration is sealed to stop grout spill.
5d87c58d-2c86-5f5f-b8b4-5f204409ace8 | note | Acceptance Criteria - Matches Design Drawings by dinension and configuration
a430130d-6b23-5ab2-948f-424c5fdf3436 | note | Verifying Document - Drawing M0003
f3b738bc-fc9d-55a4-8b21-ee7cccd0bb56 | note | Frequency - Once
5c9f3b32-4700-56cf-a076-401e76067273 | note | Inspection Type (Visual, other) - Visual + Inspection HOLD POINT
eb4eea91-8669-5b47-983a-512ca9f81b11 | note | Inspection: Key - H
39995cf0-109c-5818-80c0-2959c9587207 | note | Inspection: By - CR
0e54279f-0ad0-4a70-866e-7458970c6b0c | signoff | AUTHORITY HOLDPOINT
72f1d584-c8ac-4f9d-a112-be0cc94521bb | checkpoint | 4.2 - Mixing of Grout
994ecbd0-a8e3-548e-bcf9-3b48a2d17d6b | note | Inspection Point: Quality Control Activity - Ensure product is on hand & plenty of clean fresh water is readily available
131e123a-7693-557a-93cf-3400a37332f5 | note | Acceptance Criteria - As per manufacturers instructions/guidelines
0803c047-3a74-522c-a334-6c18c17b2b3f | note | Verifying Document - Product technical instruction sheets or certificate (if delivered)
c606ccc3-eb64-54c9-a166-3cb886324f15 | note | Frequency - once
d73b9fee-d98e-52d0-9353-0b32045c4ffc | note | Inspection Type (Visual, other) - Document
361142bd-2f08-5458-a966-e65d14d18634 | note | Inspection: Key - I
e68133af-3681-5fee-afd3-d6f9ca6a1a2a | note | Inspection: By - IP
cb94ee82-6070-4dee-b497-bdfcbe12641b | checkpoint | 4.3 - Casting of wall penetration
1952d89c-d341-5ea3-8167-09f2cc81ba2c | note | Inspection Point: Quality Control Activity - Monitor the consistency and quality of the grout fill
bd69721e-3265-5eed-b400-77d9f0eced33 | note | Acceptance Criteria - As per manufacturers instructions/guidelines
e660cdfa-aad7-5200-a0e1-a0324c599800 | note | Verifying Document - Product technical instructions
950effc7-7e56-5b69-aa1b-abaf15ab65d2 | note | Frequency - once
c7012365-ec6a-59cd-b3ef-9dc6d65ef9b5 | note | Inspection Type (Visual, other) - Dodument + Visual
855670dc-412e-56e5-9dd4-c56b0db47f26 | note | Inspection: Key - I
e5f6738b-b9ac-5e51-bac5-1438b1d3b8ac | note | Inspection: By - IP
fcdb6e17-b738-43b3-9fdb-7888f8efc96f | checkpoint | 4.4 - Vibrate
3aec6c0e-f38b-5b1c-9d07-2c971e24c81d | note | Inspection Point: Quality Control Activity - Vibrate to remove entrained air. Ensure all air is removed
edbc8222-6e18-5195-80d4-e388a94a9811 | note | Acceptance Criteria - Grout Placer Approval
86dcffee-1199-5ab7-9d58-04e0767bbee2 | note | Verifying Document - This ITP
40f841bc-09c0-578f-9ad3-02a4e58a12d9 | note | Frequency - once
0f3a9c5f-003c-5172-a4c7-831361b67b33 | note | Inspection Type (Visual, other) - Visual + Photographs + Short video
29a3d63c-9b1e-55a0-bce1-b83352e84081 | note | Inspection: Key - I
39c2e6e0-20b5-5b0e-903f-7bdcf429cd4a | note | Inspection: By - IP
031afd3d-1b7d-49cd-873e-1cea799eb633 | checkpoint | 4.5 - Monitor curing process
bd0fd0c0-63e5-5593-9a1b-c5e8438f4ee6 | note | Inspection Point: Quality Control Activity - Monitor curing inspectiong the boxing and areas of potential grout leakage.
34db7514-b2b5-5080-a978-1f7b438502ce | note | Acceptance Criteria - No evident shrinkage or deformation. Repotr any issues to Engineer
1dac76f4-8bcc-50a9-895b-fb8b84dbb8f6 | note | Verifying Document - As per drawings allowing 7 days curing time. Boxing can be removed after 72 hours
adf83959-a6e5-5e68-8d65-8eba08e60de6 | note | Frequency - once
ddf48fcf-d842-55f0-baf9-5cb326034f6d | note | Inspection Type (Visual, other) - Visual
b21dc596-50be-5cb6-b961-801bfdf8c54b | note | Inspection: Key - I
c64cbdf9-dcf1-55ba-89a0-8bc155f763de | note | Inspection: By - IP
cbe59882-8d84-4a4e-81ca-860e8205e92a | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
1da42167-ae12-4739-9349-be1dc4cea0f2 | checkpoint | 5.1 - Remove boxing
7e3981d7-6dd8-51ba-b60d-c945cff4ab88 | note | Inspection Point: Quality Control Activity - At completion of all items on this ITP
a69405f1-89f3-5d35-849f-bdcb9d211f8c | note | Acceptance Criteria - Time period as indicated on programme
7643bdb1-c591-5325-badc-607941c97364 | note | Verifying Document - This ITP
29fc7592-e87b-5853-84a1-eab500cd1cf7 | note | Frequency - once
2ef7ddc4-7331-5492-8958-13bd52efd559 | note | Inspection Type (Visual, other) - Visual + Photograph
bd658325-a60e-5ca1-97d4-119818b8a595 | note | Inspection: Key - I
3092f82f-f21d-5416-bec1-c06f9693aeeb | note | Inspection: By - IP
bc1420ff-2527-4de3-9429-46c6593839cf | checklist | 561482-ITP-007.2 - Wet Well Wall Penetration 2 pour | itp | 561482-ITP-007.2 - Wet Well Wall Penetration 2 pour
304a71b0-deca-4284-b9e9-7cdecd82de84 | section | SECTION 3 – RECEIVING INSPECTIONS
446fa00e-d91d-4d5e-86f8-0ea0861158b4 | checkpoint | 3.1 - Grout - SIKA MonoTop- 438R
b09f668c-1acb-5f77-8cda-5f7a03bcc2a6 | note | Inspection Point: Quality Control Activity - Calculate Quantity
16c0e77d-a0ce-51c2-b7e3-cc755f887fe0 | note | Acceptance Criteria - Correct volume to be calculated
83ff47a5-22ff-5cf5-a119-981f9f014097 | note | Verifying Document - Product Datasheet
ce5042e5-6f48-5b75-ac84-40ae241a9e05 | note | Frequency - Once
667f302a-729f-5749-8ae5-587f7433681d | note | Inspection Type (Visual, other) - Written
8040d909-f17d-50d2-abe7-2d990959f939 | note | Inspection: Key - R
79ff5fec-a062-5457-b8e4-51a09d7cc26c | note | Inspection: By - CR
9746883d-98f1-45b2-acaa-dddb08aaf916 | checkpoint | 3.2 - Installed Reinforcing
48bfec64-8f64-5a82-a569-426cabc33102 | note | Inspection Point: Quality Control Activity - Measure and check
ad5171e1-b46e-5d28-a0ab-2c6f8e834c84 | note | Acceptance Criteria - Matches Design Drawings
a8201a93-6501-5c11-904e-baabfe50266c | note | Verifying Document - Drawing M0003
a88b3469-3d2b-5ec4-8069-82f78305a11e | note | Frequency - Once
378afb55-f88a-545d-a1e2-16c63f82a916 | note | Inspection Type (Visual, other) - Visual + Photographs
3e904b51-018b-51c3-9812-1b7e32f57195 | note | Inspection: Key - V
bc3ed07b-c7b8-5ec9-9d61-6c81737f81cc | note | Inspection: By - IP
bd5eb125-8e54-46ee-a545-f2819f597d9d | checkpoint | 3.3 - Spool/Puddle Flange
22c279cf-9d78-57f6-8ed0-850b002fd0e7 | note | Inspection Point: Quality Control Activity - Measure and check
ac9d9943-4385-5bb8-8331-b426c6c7de69 | note | Acceptance Criteria - Pipework is straight and parallel to structure & pump
c3a07b8a-d1c1-577e-8a45-b9a600a5e23d | note | Verifying Document - As per drawing M0001 & M0002
b09e84da-f1e4-5402-8bac-c14a07c75ad1 | note | Frequency - Once
812a12b5-183b-5c5d-bb7b-789fcf795efd | note | Inspection Type (Visual, other) - Visual + Photographs
960e6986-5e19-5f18-b880-7e8aa386e69e | note | Inspection: Key - V
fb0bfee5-5a80-5f59-b51c-60f9ae9309ca | note | Inspection: By - IP
e97a1b88-c827-4bdd-8e16-86ec3852bda6 | section | SECTION 4 – IN-PROCESS INSPECTIONS
1ab7247c-e1f5-4664-a563-257538bcbe02 | checkpoint | 4.1 - Boxing of penertation
58b1e467-dc7e-5147-a2a2-7f987ecad595 | note | Inspection Point: Quality Control Activity - Measure & Check. Ensure perimeter of boxing and pipe penetration is sealed to stop grout spill.
818e413c-dddb-5961-b433-6617113bb206 | note | Acceptance Criteria - Matches Design Drawings by dinension and configuration
92b011a5-cd2c-5664-be04-ad8c1dc979cc | note | Verifying Document - Drawing M0003
237a8813-902f-5e61-8ced-e737e4136472 | note | Frequency - Once
ffd5b831-35f3-510e-a72c-75c0f27a4384 | note | Inspection Type (Visual, other) - Visual + Inspection HOLD POINT
4d2ce3d7-5d09-5444-b93b-ac072c1066e8 | note | Inspection: Key - H
d15aa45c-c854-5767-8471-22f500910d25 | note | Inspection: By - CR
f765d1f0-6366-4d87-ae92-270206985be4 | signoff | AUTHORITY HOLDPOINT
9462aaab-9a05-43d2-a13e-275a7a4f2144 | checkpoint | 4.2 - Mixing of Grout
cacc832b-8d5c-5b54-ae8e-5bff87262e0f | note | Inspection Point: Quality Control Activity - Ensure product is on hand & plenty of clean fresh water is readily available
d337d0ca-626a-547c-ac16-f9a5de5e92c0 | note | Acceptance Criteria - As per manufacturers instructions/guidelines
7f5baf11-3fd2-5f06-9eb9-47b39dc97107 | note | Verifying Document - Product technical instruction sheets or certificate (if delivered)
0e01ab11-5f98-5068-9f42-9d03631a3e90 | note | Frequency - once
a4c64f07-842c-5ea7-b3be-d0cd5a40103c | note | Inspection Type (Visual, other) - Document
81afd770-ae94-50e3-bbad-45c83b61e724 | note | Inspection: Key - I
331f19c5-4200-5f1a-92bd-13c6dc4cfc02 | note | Inspection: By - IP
5e308600-f7ea-4735-b153-09b7168731cc | checkpoint | 4.3 - Casting of wall penetration
2a1066bf-c5fd-508c-a8ea-0dd52e1712f5 | note | Inspection Point: Quality Control Activity - Monitor the consistency and quality of the grout fill
47e8e339-25d3-5ff0-8f2a-26cdd49103cd | note | Acceptance Criteria - As per manufacturers instructions/guidelines
756cd71b-ea0f-590e-83fc-20506dbac9df | note | Verifying Document - Product technical instructions
67af0522-30c4-5f9d-8431-3b4eb236bd0c | note | Frequency - once
420f4762-77dd-5d2e-ba95-b432b975ed45 | note | Inspection Type (Visual, other) - Dodument + Visual
9495d3a0-526f-5409-b1c5-3ba7c86f19af | note | Inspection: Key - I
0a1baa04-189e-5aac-aafa-56b311797ec7 | note | Inspection: By - IP
a769a468-c560-4199-940e-e679c77b945b | checkpoint | 4.4 - Vibrate
7cee828a-433c-5f05-ade0-07b90bba34b0 | note | Inspection Point: Quality Control Activity - Vibrate to remove entrained air. Ensure all air is removed
cb752ae0-d39a-5cf0-98a8-1ce73b7f23a1 | note | Acceptance Criteria - Grout Placer Approval
a41925cc-f88d-53f8-bb08-870dcb26a98f | note | Verifying Document - This ITP
862b7064-d975-599c-9662-ebd507984932 | note | Frequency - once
55b9f770-ff5e-5409-abfe-2278f10f3905 | note | Inspection Type (Visual, other) - Visual + Photographs + Short video
08e5b26e-d236-5a29-b496-1f14576ed585 | note | Inspection: Key - I
d2839bd6-32dc-58dc-97f6-6812c2ec43b9 | note | Inspection: By - IP
115f39c0-de85-4ae2-b447-d39310d613d6 | checkpoint | 4.5 - Monitor curing process
f7d8d8a4-584a-59bc-b5bd-fd09bb0f9fd4 | note | Inspection Point: Quality Control Activity - Monitor curing inspectiong the boxing and areas of potential grout leakage.
62493fb8-05b5-574a-bfb6-9669e6a5f816 | note | Acceptance Criteria - No evident shrinkage or deformation. Repotr any issues to Engineer
cfb336e0-5061-5dc4-999b-cd57a6b18c00 | note | Verifying Document - As per drawings allowing 7 days curing time. Boxing can be removed after 72 hours
8e51eaad-4c84-5bf6-b951-ca6974f473a1 | note | Frequency - once
0c13a9b4-757e-5dc9-adce-22c7c8c0b77e | note | Inspection Type (Visual, other) - Visual
026108b2-9fc3-5509-ba34-9c43f203fb90 | note | Inspection: Key - I
f2475628-65b3-5331-9704-77b822bcf96e | note | Inspection: By - IP
6b17e4b6-2885-4c70-8419-b2aa6013c102 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
c44061e9-a12c-4627-96bf-8111a4091041 | checkpoint | 5.1 - Remove boxing
e35ab971-04fe-5543-9d62-3d7c751c4c6e | note | Inspection Point: Quality Control Activity - At completion of all items on this ITP
4f2acf46-0b77-5bb0-a7e6-79d37e3ac093 | note | Acceptance Criteria - Time period as indicated on programme
3124708e-cfce-5c48-b443-4cd93f7d3d8a | note | Verifying Document - This ITP
52306257-62b3-5f57-b6f3-c00508ea21be | note | Frequency - once
33f7b4c9-ca77-525e-a44d-bc174cd55a82 | note | Inspection Type (Visual, other) - Visual + Photograph
8de2e360-ffc5-55e4-8f68-e10919a47d6c | note | Inspection: Key - I
189349ab-a3de-554a-a3d7-a65f7b1dc72f | note | Inspection: By - IP
04e34cac-7864-4ea8-be15-d3ad0351be9a | checklist | 561482-ITP-007.3 - Wet Well Wall Penetration 3 pour | itp | 561482-ITP-007.3 - Wet Well Wall Penetration 3 pour
06b0360d-0b21-4cc7-adc4-1820304f11c5 | section | SECTION 3 – RECEIVING INSPECTIONS
1424cc86-5d5f-4425-893d-9eff87b8a173 | checkpoint | 3.1 - Grout - SIKA MonoTop- 438R
867db15b-32e7-581b-8c4f-432622d0a50b | note | Inspection Point: Quality Control Activity - Calculate Quantity
bebd161a-d067-5d2d-a8aa-02b36ea4bb00 | note | Acceptance Criteria - Correct volume to be calculated
3a2c21de-d657-5f6c-bc52-9dda28934b26 | note | Verifying Document - Product Datasheet
f418ea4d-12a3-5816-96d2-978b0bff8b56 | note | Frequency - Once
21f2238a-bd9b-53ac-bfd3-777546856f3c | note | Inspection Type (Visual, other) - Written
1541954d-8c94-53df-ab70-06340bc41b7e | note | Inspection: Key - R
6bf755e4-fd10-56ba-98e8-91a2949b0d56 | note | Inspection: By - CR
ae70a5ba-d80f-4519-906b-22b8610dcbef | checkpoint | 3.2 - Installed Reinforcing
320befab-143c-52cf-8340-04ceeaa1568f | note | Inspection Point: Quality Control Activity - Measure and check
d31629d8-f724-5704-b351-d2b81627f359 | note | Acceptance Criteria - Matches Design Drawings
20b31b0a-6e22-5ca2-81b6-440f24a50ce8 | note | Verifying Document - Drawing M0003
c3a4ca37-9e0f-5168-b2f4-f35337067bb1 | note | Frequency - Once
83d94740-e4c0-58f7-a720-76166c76506e | note | Inspection Type (Visual, other) - Visual + Photographs
19dd9dd3-e5a3-5ca0-9c09-aac27bb4ad8d | note | Inspection: Key - V
cd606fdf-ee62-5b82-a4df-a4e06bee5ed6 | note | Inspection: By - IP
db7a8721-9ccb-43c7-bee5-32bb4ae370cb | checkpoint | 3.3 - Spool/Puddle Flange
83aef12f-4a1e-5374-a23d-a211da057a4b | note | Inspection Point: Quality Control Activity - Measure and check
bc1b9770-0aad-5370-a45a-5711bda889cd | note | Acceptance Criteria - Pipework is straight and parallel to structure & pump
dd78d8d1-5458-5cf8-b985-e25603639439 | note | Verifying Document - As per drawing M0001 & M0002
ad8e9905-b451-5e4f-b464-c2ce7839e662 | note | Frequency - Once
c2bbdc77-50ac-51ab-a922-483dc755fc8a | note | Inspection Type (Visual, other) - Visual + Photographs
2117d8d1-221a-58fb-ba03-fb7ee6ca704d | note | Inspection: Key - V
da359d0c-5ce7-53af-b049-009c87aa2af2 | note | Inspection: By - IP
f2106543-ee3a-4d0c-b5b2-d4e7152951ba | section | SECTION 4 – IN-PROCESS INSPECTIONS
7a302fd3-57f3-41d3-9ed3-ff81de64d1a4 | checkpoint | 4.1 - Boxing of penertation
622f7910-c5d6-5147-9147-83cdbd83b394 | note | Inspection Point: Quality Control Activity - Measure & Check. Ensure perimeter of boxing and pipe penetration is sealed to stop grout spill.
c2db3a3c-728e-52ee-94b1-f7d13ab7c236 | note | Acceptance Criteria - Matches Design Drawings by dinension and configuration
9c116b54-9078-5a30-9e76-916eae5fccbd | note | Verifying Document - Drawing M0003
6823b22b-9900-5960-8aad-223a9a4f276c | note | Frequency - Once
c94e6d23-04b5-543e-ba3b-1a9a997bf431 | note | Inspection Type (Visual, other) - Visual + Inspection HOLD POINT
dd476045-050f-5416-a939-6865718f1d47 | note | Inspection: Key - H
364503a6-324e-5c9a-96cd-b02a0b8e3d67 | note | Inspection: By - CR
f0483e66-5fbb-45ae-af36-b06543456593 | signoff | AUTHORITY HOLDPOINT
1f4e5af4-4b43-40fc-94d9-154344dff69a | checkpoint | 4.2 - Mixing of Grout
2f01ccb7-bdd3-5d7a-8c1c-b17d25aebe05 | note | Inspection Point: Quality Control Activity - Ensure product is on hand & plenty of clean fresh water is readily available
82c91494-42e8-50ec-a6ab-eed646bbe920 | note | Acceptance Criteria - As per manufacturers instructions/guidelines
e4aa97a3-ff34-5098-85cf-38ec79b35e98 | note | Verifying Document - Product technical instruction sheets or certificate (if delivered)
60799850-85f2-59e6-9b78-6d5b1275527e | note | Frequency - once
15b55ff5-0c03-552f-b75a-b4f0375691e9 | note | Inspection Type (Visual, other) - Document
b5a9fbae-9d85-5f7e-807e-bfd001dacd54 | note | Inspection: Key - I
461b7755-1d8a-5709-97ba-33642ff993ef | note | Inspection: By - IP
c98d0f80-4268-45e0-876f-0e269f4bdd5d | checkpoint | 4.3 - Casting of wall penetration
9e34b393-f557-5970-9f0d-8c0ad51dcea8 | note | Inspection Point: Quality Control Activity - Monitor the consistency and quality of the grout fill
137a3dfd-3b7f-5e4b-8d09-922cd04f8012 | note | Acceptance Criteria - As per manufacturers instructions/guidelines
311db0c9-fa8d-5bd4-93c0-29ca2b6a9cc3 | note | Verifying Document - Product technical instructions
d4d358cd-0811-57ff-9f01-7cad8c1e6db8 | note | Frequency - once
a91f6608-2f54-56f6-b8a3-b7a46baad0cf | note | Inspection Type (Visual, other) - Dodument + Visual
4ed0deee-20c0-579a-982e-6ec705d2c683 | note | Inspection: Key - I
04cd47f6-bf64-51cf-aa7e-ff74906182f9 | note | Inspection: By - IP
3b43b6e5-5e17-49fe-ada3-a5f9089b1ec5 | checkpoint | 4.4 - Vibrate
03b9b58d-d8d4-5482-b7ba-b9d8297e6a66 | note | Inspection Point: Quality Control Activity - Vibrate to remove entrained air. Ensure all air is removed
16670e7e-6717-58e8-b644-47f62d7f8f4d | note | Acceptance Criteria - Grout Placer Approval
f52486f9-171b-5fff-b79b-877f282c37bb | note | Verifying Document - This ITP
bd5f59f1-31a4-537f-ac78-36e5a0362b62 | note | Frequency - once
1444437b-022f-5369-a456-d0de623017b2 | note | Inspection Type (Visual, other) - Visual + Photographs + Short video
55644158-f90f-5b71-b076-ee03fe2333eb | note | Inspection: Key - I
7f87888f-8f7e-55b1-8099-01ad664e762b | note | Inspection: By - IP
dde21492-2b9c-4418-bf22-40e6953218be | checkpoint | 4.5 - Monitor curing process
4b6cf333-de95-5f7f-a76a-e58291f6c571 | note | Inspection Point: Quality Control Activity - Monitor curing inspectiong the boxing and areas of potential grout leakage.
e8408b5f-936c-58d6-8755-af7025e580a1 | note | Acceptance Criteria - No evident shrinkage or deformation. Repotr any issues to Engineer
694e6da1-b86f-54fc-8ee8-562158606634 | note | Verifying Document - As per drawings allowing 7 days curing time. Boxing can be removed after 72 hours
ed544cb2-6586-561e-9c6b-76e4d2e9e883 | note | Frequency - once
72766d84-38b0-55fa-826c-1aae81ad1e70 | note | Inspection Type (Visual, other) - Visual
33f8781b-07bb-57e5-9591-1b12206c649b | note | Inspection: Key - I
63dc05a9-bc18-59f0-9dd0-32bca517af1a | note | Inspection: By - IP
e183d0f6-2891-4218-8c26-ac36f805058f | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
3545f43d-e115-44ae-a573-3d35a84c41fb | checkpoint | 5.1 - Remove boxing
91ae54fa-1288-5fad-a57c-2eb95939d81a | note | Inspection Point: Quality Control Activity - At completion of all items on this ITP
b99e077a-6282-5693-a33a-50f5866d9919 | note | Acceptance Criteria - Time period as indicated on programme
0ede7792-4f59-578a-8431-fe23ed23489e | note | Verifying Document - This ITP
f7d7c046-0cf3-5193-8db3-b52fbdb2935d | note | Frequency - once
4ce08250-4549-58c9-b6f2-44fb18777ea3 | note | Inspection Type (Visual, other) - Visual + Photograph
adbbc3b7-3357-5bfa-bb2f-beb0f4461d7c | note | Inspection: Key - I
85b3f843-bd58-5fb7-a7b9-4f0f529ff805 | note | Inspection: By - IP
7642b5f8-f11d-41d5-a802-8db12ba8dea4 | checklist | 561482-ITP-008 - Wet Well Wall - Final Pre-fill inspection | itp | 561482-ITP-008 - Wet Well Wall - Final Pre-fill inspection
897643ba-07af-4fcc-9320-841be3674d04 | section | SECTION 3 – RECEIVING INSPECTIONS
f12897b8-2b19-4264-9d16-42ec0f75a2d0 | checkpoint | 3.1 - Grout Castings (Penetrations 1 through 3)
bbc24578-6407-5fb2-87a4-22a89aa22937 | note | Inspection Point: Quality Control Activity - Inspection of castings.
1960f9a4-e39d-5777-9cb5-076082b89e82 | note | ○ Inspection for air pockets, cracks, fissures oa any other imperfections
97f30c4c-8e07-5f50-b455-edb28f25b28f | note | Acceptance Criteria - Completion of ITP's
8291fbb4-3c36-54fe-a95f-d5d7b1f80349 | note | ○ 561482-ITP-007.1.
5415109c-1002-5bbb-ba2b-16e662c062c7 | note | ○ 561482-ITP-007.2
20101704-dd44-597d-82b5-793b4ebfdb21 | note | ○ 561482-ITP-007.3
bc9e9c4b-864a-596b-b322-2662d0bf79fe | note | ○ Elapsed time of 7 days post pour
5c3ae48d-5b25-5eee-9cc8-ba630ee25ca0 | note | Verifying Document - None
2b700765-d981-540c-96f8-f727c3f9d53e | note | Frequency - Once
deb94657-1d35-5ce7-a4c7-6dbc56fd2403 | note | Inspection Type (Visual, other) - Visual + Photographs
ff873624-7bb1-58cd-9e65-32762746ec6d | note | Inspection: Key - A
ba4a9bd9-fd41-5d9d-85b4-40efc743858f | note | Inspection: By - IP
ed33693f-5050-4464-b663-4c31b7f705be | section | SECTION 4 – IN-PROCESS INSPECTIONS
4398457c-53ea-4878-b3f2-05c38dbb46e6 | checkpoint | 4.1 - Removal of Formwork - Penetration 1
81700b0b-2834-547d-a639-62c439fab0ff | note | Inspection Point: Quality Control Activity - Check and verify quality of casting both wet well side and Dry side
a19fa2b4-f00e-5aac-ae07-7f43fba12d91 | note | Acceptance Criteria - Approval from Engineer
0c09195a-9013-572f-b485-d4b6f6636f05 | note | Verifying Document - Drawing M0003 and annotations
e6445a2c-04e9-560a-ba23-8f41776f7998 | note | Frequency - once
1c23c4c9-9d9d-5306-8410-6f8f80072714 | note | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
8e6a1f4b-6c42-5174-9513-1ad7d4a49711 | note | Inspection: Key - H
e4b0b284-d8cd-50c3-a136-f8fefefa4414 | note | Inspection: By - CR
27aad9ec-dddb-4327-82f9-6e481d97e00f | signoff | AUTHORITY HOLDPOINT
fe3fc288-1354-4f7d-ad6d-ced6772537a5 | checkpoint | 4.2 - Removal of Formwork - Penetration 2
1bcb0277-bbea-5c3f-b6d5-4675eb1122fe | note | Inspection Point: Quality Control Activity - Check and verify quality of casting both wet well side and Dry side
8f8ac064-69cf-54e4-baa9-5921c31de038 | note | Acceptance Criteria - Approval from Engineer
0b9df010-81f4-5943-bbd1-aa19d0c4bc5a | note | Verifying Document - Drawing M0003 and annotations
19cf21a7-dad6-5d56-9cda-933c2dc367e3 | note | Frequency - once
04ef2d56-a9b9-5734-b416-9de66b3e7aae | note | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
0826d7a9-8f47-5ec4-b114-ae067da1c8f1 | note | Inspection: Key - H
a6810b6f-a70f-59bc-8b5a-db9636c29f62 | note | Inspection: By - CR
b526b4c1-206e-4f12-9884-73bf700865ff | signoff | AUTHORITY HOLDPOINT
ff744b9f-c905-4283-847e-ce6947edf9b5 | checkpoint | 4.3 - Removal of Formwork - Penetration 3
887ed539-bb4f-5ee0-aa5b-327974690aea | note | Inspection Point: Quality Control Activity - Check and verify quality of casting both wet well side and Dry side
c085d689-1989-5e62-a9f9-6c30de97001f | note | Acceptance Criteria - Approval from Engineer
f7ec5165-5cbc-514f-b2f0-938c3bf17b03 | note | Verifying Document - Drawing M0003 and annotations
424af3f2-734b-5721-a712-857dc7a0d265 | note | Frequency - once
6628437f-3487-5b82-abeb-3bece3e164f5 | note | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
6e3b5c08-6cf3-5bbf-88ce-731af695c479 | note | Inspection: Key - H
b057500b-60f8-51fa-8e7f-ce393267b5e3 | note | Inspection: By - CR
b8e43e6d-9f5d-4384-bb1d-c3dbb1521a14 | signoff | AUTHORITY HOLDPOINT
104aaff7-4e81-4310-bf89-4718162073a7 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
cf3a3214-1823-4c0f-b725-03dc72aeb464 | checkpoint | 5.1 - Clean tank of any Downer construction debris
b98ea6b2-cb7a-5eea-92fa-5b9680b6be1a | note | Inspection Point: Quality Control Activity - Upon removal of boxing and any remedial activities
4ada1e9a-9a4c-5bce-99cf-aecc8c1094e5 | note | Acceptance Criteria - Client Representative acceptance
5f48caee-6e20-59c1-87fe-9c9e844a4b17 | note | Verifying Document - NTC and or other written conformation
2acc671d-940e-5c5d-8fae-152a0a8452c9 | note | Frequency - once
c4421634-8691-5a3f-b840-b0a2df82a5c5 | note | Inspection Type (Visual, other) - Visual Inspection + Photograph
19195ceb-9546-5f78-8959-f716fab30a5c | note | Inspection: Key - H
d50ce20e-2a04-5b93-8167-795a1e60677f | note | Inspection: By - CR
d29e6a87-f5ad-4034-a5d7-4f1a9070e11d | signoff | AUTHORITY HOLDPOINT
b7f75978-2fd3-4215-86b6-e73e8a0bfb7e | checkpoint | 5.2 - Approval to fill Wet well
49c8b265-279c-5837-9b8a-021a862fc6ae | note | Inspection Point: Quality Control Activity - All activities and pre-checks required by client
f4f1b8f0-5849-5b06-af8e-a23c5ce96bb3 | note | Acceptance Criteria - Client Representative acceptance
f4216815-cb23-5beb-9b57-8b52951edb3b | note | Verifying Document - NTC and or other written conformation
88c15c67-3cf1-579e-b988-c0b3424b6dfa | note | Frequency - once
11fd71d4-2b13-5c8c-a2c8-c7b9330b4774 | note | Inspection Type (Visual, other) - Visual Inspection + Photograph
1c45a350-c4fe-5d14-9f0d-97d9dc90250a | note | Inspection: Key - C
ed334922-9caf-5771-8cf5-d8ba726de1a7 | note | Inspection: By - CR
3d8dfc7a-b3b3-46a1-8a94-e96081489568 | checklist | 561482-ITP-009.2 - Pre Commissioning Testing Pump & Valves - Pump 2 | itp | 561482-ITP-009.2 - Pre Commissioning Testing Pump & Valves - Pump 2
a1098b31-6510-491d-9684-4ad4edc650f6 | section | SECTION 3 – RECEIVING INSPECTIONS
d2a874cd-9e62-406c-8585-9e5f5599b2bf | checkpoint | 3.1 - Fill Wet Well
3ac5fcef-359f-53a3-8f95-b0183bc33a9c | note | Inspection Point: Quality Control Activity - Pressure testing between suction and discharge isolation valves
1e2097af-ece9-521d-825c-b1d16c3419da | note | Acceptance Criteria - Completion of 561482- ITP-008
8a8965e0-a87d-5a62-b62e-b13b3455d0c5 | note | Verifying Document - This ITP
43176f61-e08f-51d7-8de5-68524bbdedc8 | note | Frequency - once
9e053bdd-25ce-5126-9e51-a84fca43be84 | note | Inspection Type (Visual, other) - Visual
91bbd7e0-2d59-5649-a0d6-4c027c53fb8a | note | Inspection: Key - Inspection
74b4a376-4a31-54d7-8c08-951e946fb256 | note | Inspection: By - IP
5040c1ef-6230-4865-aa06-37cfe0369223 | section | SECTION 4 – IN-PROCESS INSPECTIONS
9374e418-aa8d-4310-b9d7-7cff8027b3e0 | checkpoint | 4.1 - Filling of pipeline
2fe5bcb6-b04c-51a0-803d-f58a762176c5 | note | Inspection Point: Quality Control Activity - Remove Entrained air
abb4137f-cf2b-5947-bed4-a5f3ac247edb | note | Acceptance Criteria - Bleed until water visible
d11917f4-acd8-5176-8fa5-9ca6240a9217 | note | Verifying Document - None
6852009b-e2b4-52ec-b5cb-79cad68b5baf | note | Frequency - once
557f43a5-5c8a-5158-b901-fa0d87bcce6f | note | Inspection Type (Visual, other) - Visual
713a6a23-681d-5325-b76f-6d5d0433a10a | note | Inspection: Key - Inspection
b811d2c2-c72f-5344-af12-af61bf2ba4bc | note | Inspection: By - IP
05a6818a-db99-4742-b40c-11010c18d8c3 | checkpoint | 4.2 - Visual Check over of Pump 2 and motor
d7a7efb6-efda-55e4-8ce8-e9013726cde3 | note | Inspection Point: Quality Control Activity - Look for any visible leaking
f826f6c8-c50a-5eff-a1ee-fdcdea35a00a | note | Acceptance Criteria - All pipework connections tight All Cable & Terminations secure
3e40ef1a-c8b4-5d55-9ffb-1d126c246a9f | note | Verifying Document - This ITP
ccc3f76e-d099-5cb9-be48-3a46e643b352 | note | Frequency - once
521f7d55-8344-52bd-a81b-a46e92aae8df | note | Inspection Type (Visual, other) - Visual
6ccb898c-88e0-5030-8b47-b19afd69aaef | note | Inspection: Key - Inspection
af22993c-dbcf-5317-ae9a-e04758051d40 | note | Inspection: By - IP
c3deba62-7e30-4987-8d8d-bd7252c03d1f | checkpoint | 4.3 - Bump Start Pump 2
94144506-9038-590c-bdf1-a184ba7c5b67 | note | Inspection Point: Quality Control Activity - Check for correct pump rotation direction
801c0dea-1518-57c9-8b77-518ff3a479e7 | note | Acceptance Criteria - Rotation direction is correct
510d0a52-2dec-5b9b-a135-a92c94feef7e | note | Verifying Document - Pump build sheet literature
7ff05f03-656b-5475-937b-5baba9fabcb1 | note | Frequency - once
f3cd18c6-61e2-5cfa-aa47-48e44bdc258e | note | Inspection Type (Visual, other) - Visual
806263e6-cb4a-5ca5-9558-daa29129d8c2 | note | Inspection: Key - Inspection
530ad8e8-6072-5d57-90c7-11b36e0ec053 | note | Inspection: By - IP
b527b231-5826-4105-9b9f-4b6dd5910a09 | checkpoint | 4.4 - Pressure testing between suction and diacharge isolation valves - Pump 2
824f59a9-67be-59c2-ba5b-e78976182f2c | note | Inspection Point: Quality Control Activity - VSD Energised, water in pump pipelines
bd29f52d-bc91-5a0c-aa3f-1226592687f1 | note | Acceptance Criteria - No visible leaking as per Item 4.2
462dde64-6712-5e0a-a67b-66f5ccb3aa5c | note | Verifying Document - To meet Specification requirements and not to exceed pump manufacturers maximum pressure (Pump flanges 16Bar, Seal max pressure 30Bar)
afa04178-f971-5ac0-ae0d-33379e4b5758 | note | Frequency - once
6a6a99f7-4e99-51ad-83e6-78927d58ed40 | note | Inspection Type (Visual, other) - Visual
6ea0006f-4959-52c5-b8b9-84052a4ab992 | note | Inspection: Key - Inspection
3273caa0-93bc-51af-a03e-bb6a282f9c4d | note | Inspection: By - IP
fa9300a1-abd7-47a3-96f6-51dcb5b4b53b | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
ad72b869-2e80-4b56-914a-1e718baabf1d | checkpoint | 5.1 - Pump 2 rotation direction
e7dc7f2b-e1ea-5185-9383-141739e26899 | note | Inspection Point: Quality Control Activity - Pump rotation direction as per manufacturers technical information
22b93a0f-d8eb-5a9c-aedd-69205e8f1fb6 | note | Acceptance Criteria - Pump rotation direction is correct and matched the technical information
548e4d32-baae-5817-80a0-e5dbb6c50bec | note | Verifying Document - This ITP
87433843-1c71-5933-839f-0984856daf1f | note | Frequency - Once
a1956f7a-a705-568f-b000-d17f7bad8426 | note | Inspection Type (Visual, other) - Record on ITP
d8127cc0-7a40-555c-a796-68aca1be59df | note | Inspection: Key - Inspection
393bd472-385f-5500-b0bd-88384ea145af | note | Inspection: By - IP
c9243a22-49d7-4625-bf3c-a1ae682a8d99 | checkpoint | 5.2 - Pump 2 pressure test pass
919175b7-390b-5269-a0d6-a3da8ce8b4b8 | note | Inspection Point: Quality Control Activity - Record Gauge pressure
95885160-b00e-50f2-802e-1620a8afad41 | note | Acceptance Criteria - Pass - no pressure loss or visible weaping
903ea7dc-1280-5f9c-b1db-c6a3d8960084 | note | Verifying Document - This ITP & Specified Pressure testing document
a7b20dab-57f9-5f54-96c5-c52355a0e660 | note | Frequency - Once
50b9a7c2-12b8-5df0-b7f8-f6a43a6d3550 | note | Inspection Type (Visual, other) - Visual / Photo
b9c15a9d-c45e-5d47-a3dd-35ebaad57ea6 | note | Inspection: Key - Inspection
9c38cb23-ecd7-596f-b3be-946ce35f5a3b | note | Inspection: By - IP
19536531-7646-4390-9028-d15e92b5ca70 | checklist | 561482-ITP-009.3 - Pre Commissioning Testing Pump & Valves - Pump 3 | itp | 561482-ITP-009.3 - Pre Commissioning Testing Pump & Valves - Pump 3
f5ee21e3-c380-489e-a375-c594369abc92 | section | SECTION 3 – RECEIVING INSPECTIONS
e17ed63b-ae10-43f1-83d2-684e8dac5623 | checkpoint | 3.1 - Fill Wet Well
a406d618-3b83-5173-82b7-3199c38966d2 | note | Inspection Point: Quality Control Activity - Pressure testing between suction and discharge isolation valves
4a7132ce-8c36-59ad-a9b3-adbbc4d21d93 | note | Acceptance Criteria - Completion of 561482- ITP-008
ce5262fa-f7a1-5d0c-9a2a-17c5fee017e2 | note | Verifying Document - This ITP
630ec3ab-abdc-54bc-91fd-c1fafe2fa544 | note | Frequency - once
efffccbe-3d19-5d0f-878a-5ba64b284e19 | note | Inspection Type (Visual, other) - Visual
5e8a6cd3-f8e9-5a8e-8e4a-e7373e27185f | note | Inspection: Key - Inspection
6b8ea53a-4422-5cd9-ab56-ef44efbff52e | note | Inspection: By - IP
bb596c2c-fd4d-442f-b6a9-25869e7e04ae | section | SECTION 4 – IN-PROCESS INSPECTIONS
b607cf96-1e75-4457-8a82-0325ff761db3 | checkpoint | 4.1 - Filling of pipeline
7d0a60ce-1f3a-5569-8378-e959cae1d905 | note | Inspection Point: Quality Control Activity - Remove Entrained air
efcb01c9-fac2-5311-92bc-54fc7606bfe7 | note | Acceptance Criteria - Bleed until water visible
930b733d-f40c-5634-a913-93fa0420563a | note | Verifying Document - None
e22d2024-1f19-577e-82d6-58d0c5c23e8a | note | Frequency - once
e60813d2-e120-584a-8772-512a81d7108b | note | Inspection Type (Visual, other) - Visual
40c08716-0dfe-5496-9528-8ece5cf5965f | note | Inspection: Key - Inspection
606b0e20-04f4-5a86-940f-b219c3716b6f | note | Inspection: By - IP
edead84b-52cf-4ea6-8194-31408fc151f6 | checkpoint | 4.2 - Visual Check over of Pump 3 and motor
96587daa-7dee-5405-bd4f-64c4afdbbfba | note | Inspection Point: Quality Control Activity - Look for any visible leaking
16404f5a-a379-5eb0-839f-5b176d1d8d8d | note | Acceptance Criteria - All pipework connections tight All Cable & Terminations secure
f71b6bea-b45c-5ec5-94a1-47a39881f8fd | note | Verifying Document - This ITP
b6e53a4f-ac2a-5006-88f9-4cd221ace649 | note | Frequency - once
9f7fbef1-a875-59f3-af82-ecea3adb4154 | note | Inspection Type (Visual, other) - Visual
11851e23-c3ba-58cd-8d58-9bf68fc05edf | note | Inspection: Key - Inspection
c4e70415-3eb8-50cf-8298-46d548480ddf | note | Inspection: By - IP
99a8e15f-03bb-4080-8790-268b5ffd13f0 | checkpoint | 4.3 - Bump Start Pump 3
796817c6-3b0f-53d5-b8bf-f616a3ffa544 | note | Inspection Point: Quality Control Activity - Check for correct pump rotation direction
fd9d2aca-4847-5c85-9d76-9215d3868e1b | note | Acceptance Criteria - Rotation direction is correct
2f6babda-658d-5cf2-8548-ea2321e111e1 | note | Verifying Document - Pump build sheet literature
28687dc4-beb9-503b-92d2-32317a346fce | note | Frequency - once
924f6a1f-12b2-518e-8a41-1ea32368f3a4 | note | Inspection Type (Visual, other) - Visual
818cb764-33fb-512c-9be2-274e3e462774 | note | Inspection: Key - Inspection
3cd0f972-7954-5855-8745-b22421b6ad18 | note | Inspection: By - IP
9cbb0aa4-b33b-4351-b6eb-adcacd92e9ed | checkpoint | 4.4 - Pressure testing between suction and diacharge isolation valves - Pump 3
c8f2632e-60be-5bbf-9769-f59299f17157 | note | Inspection Point: Quality Control Activity - VSD Energised, water in pump pipelines
be6672df-2dcf-5a74-8d2e-07dd9709d88d | note | Acceptance Criteria - No visible leaking as per Item 4.2
17123f11-5717-5f7a-bc36-d945a1d9b9a6 | note | Verifying Document - requirements and not to exceed pump manufacturers maximum pressure (Pump flanges 16Bar, Seal max pressure
bfdd3f3e-9046-5732-b17f-4a7f51737a90 | note | Frequency - once
55f22676-1eae-5894-ab64-2dab47bb245d | note | Inspection Type (Visual, other) - Visual
801c4350-3d7e-59ef-8871-82d131e74897 | note | Inspection: Key - Inspection
0a84125b-fef9-5b4e-b9ec-69d4e7964080 | note | Inspection: By - IP
0bc61717-8ce2-45e8-a932-a4e18290071d | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
ea26b2fc-32ff-4e05-8717-37e2705b0265 | checkpoint | 5.1 - Pump 3 rotation direction
a62814a2-411e-5d47-b74f-908e396bc6ca | note | Inspection Point: Quality Control Activity - Pump rotation direction as per manufacturers technical information
894e701a-a406-5fdc-b18c-268a71ad34b5 | note | Acceptance Criteria - Pump rotation direction is correct and matched the technical information
e0764d9d-ec62-57bd-a05f-a9036e1d9d4a | note | Verifying Document - This ITP
45d1f1ff-b903-54bb-b313-bff15b18c6d3 | note | Frequency - Once
75b2d8f8-edd1-5504-9056-673b79e3c35a | note | Inspection Type (Visual, other) - Record on ITP
aebc42ab-6f77-568f-aceb-d1cc549ff231 | note | Inspection: Key - Inspection
3275f012-5e19-54f6-a427-1ff725e6adfe | note | Inspection: By - IP
74521f3b-d76a-40da-8e17-019be4ac41d4 | checkpoint | 5.2 - Pump 3 pressure test pass
3382e1f8-c4c4-59d4-9166-9bd6b7374d0a | note | Inspection Point: Quality Control Activity - Record Gauge pressure
5ec863dc-7e4f-579d-8b4b-436fc64d1241 | note | Acceptance Criteria - Pass - no pressure loss or visible weaping
ae198692-e00f-5747-96a7-1345988b49fa | note | Verifying Document - This ITP & Specified Pressure testing document
85980809-1907-567e-8e93-559f15468159 | note | Frequency - Once
70e438a0-314b-5a3a-9791-201c8bfbe6cc | note | Inspection Type (Visual, other) - Visual / Photo
1c7d7cda-188d-57ac-a5c2-3778c80e90aa | note | Inspection: Key - Inspection
6ad5284f-dbf1-5ca9-8fd5-d812cd88feda | note | Inspection: By - IP