## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP-002 - Feeder Conduits and Pits | itp |  |  |  |  | ITP-002 - Feeder Conduits and Pits Rev2
section | Preliminary Works
checkpoint | 1.1 Check for correct documentation
note | FREQUENCY: Prior to commencing any activity
note | ACCEPTANCE CRITERIA: Ensure that all employees and subcontractors are:
note | – using the correct and complete set of drawings
note | – all drawings are the latest revision
note | REFERENCE DOCUMENTS: Drawings and drawing registers
note | INSPECTION/TEST METHOD: Visual inspection
note | RECORD OF CONFORMITY: This ITP signed off
note | HP*
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 1.2 Implementation of all measures and controls
note | FREQUENCY: Prior to commencing any activity
note | ACCEPTANCE CRITERIA: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, JSEA, SWMS & WP
note | REFERENCE DOCUMENTS: PSP, EMP, TMP, JSEA, SWMS, WP
note | INSPECTION/TEST METHOD: Visual Inspection
note | RECORD OF CONFORMITY: This ITP signed off
note | HP*
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 1.3 Materials
note | FREQUENCY: Per batch
note | ACCEPTANCE CRITERIA: Electrical supply conduit to be orange. (Heavy duty 100mm diameter UPVC)
note | • Modula Stakka pits to be used for feeder pit, entries for conduits to be cut with hole saw.
note | • All pit covers to be class D or greater and installed in accordance with manufacturer requirements.
note | REFERENCE DOCUMENTS: CE-019-ST-0033 cl 4.4 AS 2053
note | INSPECTION/TEST METHOD: Verify
note | RECORD OF CONFORMITY: This ITP signed
note | HP*
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
section | Construction Works
checkpoint | 2.1 Survey set-out
note | FREQUENCY: As required
note | ACCEPTANCE CRITERIA: Work is set out in accordance with drawings.
note | • Ensure that pits are placed as shown on drawings and shall align with overhead poles which are suitable for connection with infrastructure from pits
note | REFERENCE DOCUMENTS: Work procedure
note | INSPECTION/TEST METHOD: Verify
note | RECORD OF CONFORMITY: This ITP signed
note | HP*
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 2.2 Excavation and trenching
note | FREQUENCY: Prior to installation
note | ACCEPTANCE CRITERIA: Minimum cover for underground conduits shall be 600mm
note | • Open trenching only permitted in unpaved areas, line of trench to be at right angle to the track
note | • Trench shall maintain a minimum clearance of 300mm from all existing services where possible
note | REFERENCE DOCUMENTS: CE-019-ST-0033 cl 4.2.5 & 4.2.8
note | INSPECTION/TEST METHOD: Verify
note | RECORD OF CONFORMITY: This ITP signed
note | WP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 2.3 Installation of conduits and pits
note | FREQUENCY: Each lot
note | ACCEPTANCE CRITERIA: • Conduits in the same run shall be spaced 50mm by using clean sand to pack voids
note | • Conduit shall be embedded in not less than 50mm sand and covered by >50mm - 75mm sand
note | • Mechanical protection shall be provided by installation of polymeric cable or cover strip of thickness not less than 3mm, and of a material equivalent of UPVC conduit complying to AS 2053. Protective material shall be placed not less than 100mm above the conduit, and shall not be less than 150mm wide.
note | • Conduits shall be joined male to female ends and sealed with approved adhesive immediately prior to joining.
note | • Conduits shall not be subject to construction loadings
note | • Pits shall be constructed as to allow for class D rated covers
note | • Conduits shall be placed a minimum of 100mm above pit floor.
note | • A 50mm gap between conduits shall be maintained as they enter pit face.
note | • Conduits exiting the pit as 'stub ends' shall extend a minimum of 50mm beyond the pit face and shall be fitted with a spigot end and capped with UPVC electrical caps to prevent contamination to internal surface.
note | • Conduits installed for future connections shall be installed to the track margin
note | • 100mm of concrete around and under pit lid to be installed for structural integrity
note | REFERENCE DOCUMENTS: CE-019-ST-0033 cl 4.4
note | INSPECTION/TEST METHOD: Visual inspection
note | RECORD OF CONFORMITY: This ITP signed
note | WP
note | RESPONSIBILITY: Fulton Hogan Engineer/YT
textbox | DATE:
checkpoint | 2.4 Inspection of conduit installation
note | FREQUENCY: Each lot
note | ACCEPTANCE CRITERIA: Laying of conduits and installation of pits shall be inspected by superintendent and conform to design drawings before any backfilling is to commence.
note | REFERENCE DOCUMENTS: Work procedure
note | INSPECTION/TEST METHOD: Visual Inspection
note | RECORD OF CONFORMITY: This ITP Signed
note | HP
note | RESPONSIBILITY: Fulton Hogan Engineer/YT
textbox | DATE:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.5 Back fill of trenches
note | FREQUENCY: Each lot
note | ACCEPTANCE CRITERIA: Backfilling (only to be used for road crossing trenches)
note | – Conduit trench shall be backfilled above marker tape with crushed rock or suitable material and compacted to 90% standard compaction 150mm- 200mm below sub base level, the last 150mm-200mm shall be compacted to 100% standard compaction
note | REFERENCE DOCUMENTS: CE-019-ST-0033 cl 4.2.5
note | INSPECTION/TEST METHOD: Verify
note | RECORD OF CONFORMITY: This ITP signed
note | WP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 2.6 Installation of draw cords
note | FREQUENCY: Each lot
note | ACCEPTANCE CRITERIA: Draw wire shall be provided for each conduit, with extra 3m length at each pit. Material shall be 6mm 'telstra rope'.
note | REFERENCE DOCUMENTS: CE-019-ST-0033 cl 4.4.6.2
note | INSPECTION/TEST METHOD: Verify
note | RECORD OF CONFORMITY: This ITP signed
note | WP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 2.7 Compaction
note | FREQUENCY: Each lot
note | ACCEPTANCE CRITERIA: Bedding and backfill material to be compacted using mechanical plant During compaction optimum moisture content of bedding and select fill is within 85% to 115%
note | REFERENCE DOCUMENTS: CE-019-ST-0033 cl 4.2.8
note | INSPECTION/TEST METHOD: Verify
note | RECORD OF CONFORMITY: This ITP signed
note | IP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 2.8 Feeder pits & pit lids
note | FREQUENCY: Each lot
note | ACCEPTANCE CRITERIA: Feeder pits to be constructed and installed as per drawings
note | • All conduit connections to cable pits shall be neatly made and ends of conduit trimmed off and the area between the conduit and pit wall stopped with cement mortar.
note | • Pits shall be constructed such that the level of the top of the pit lid matches surrounding finished surface level, top of pit wall is finished so that lid fits without movement
note | • Gatic pit lids shall be filled with structural grade concrete.
note | REFERENCE DOCUMENTS: CE-019-ST-0033 cl 4.4.7
note | INSPECTION/TEST METHOD: Verify
note | RECORD OF CONFORMITY: This ITP signed
note | WP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | Final Inspection
note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
textbox | Date: