## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP-003 - Electrical and Communication Conduit | itp |  |  |  |  | ITP-003 - Electrical and Communication Conduit Rev2
section | Preliminary Works
checkpoint | 1.1 Check for correct documentation
note | FREQUENCY: Prior to commencing any activity
note | ACCEPTANCE CRITERIA: Employees and sub contractors shall be issued with the most current and complete construction drawings
note | REFERENCE DOCUMENTS: Drawings and drawing registers
note | INSPECTION/TEST METHOD: Visual inspection
note | RECORD OF CONFORMITY: This ITP signed off
note | HP*
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 1.2 Implementation of all measures and controls
note | FREQUENCY: Prior to commencing any activity
note | ACCEPTANCE CRITERIA: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, JSEA, SWMS & WP
note | REFERENCE DOCUMENTS: PSP, EMP, TMP, JSEA, SWMS, WP
note | INSPECTION/TEST METHOD: Visual Inspection
note | RECORD OF CONFORMITY: This ITP signed off
note | HP*
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 1.3 Materials
note | FREQUENCY: Per Batch
note | ACCEPTANCE CRITERIA: Electrical supply conduit to be Orange and rigid HD UPVC of sizes as required.
note | • Communications conduit to be White and rigid UPVC of either 32 or 50mm size or larger as required.
note | REFERENCE DOCUMENTS: CE-019-ST-0033 cl 4.4.1 AS 2053
note | INSPECTION/TEST METHOD: Verify
note | RECORD OF CONFORMITY: This ITP signed
note | HP*
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
section | Construction Works
checkpoint | 2.1 Survey set-out
note | FREQUENCY: As required
note | ACCEPTANCE CRITERIA: Work is set out in accordance with drawings.
note | REFERENCE DOCUMENTS: Work procedure
note | INSPECTION/TEST METHOD: Verify
note | RECORD OF CONFORMITY: This ITP signed
note | HP*
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 2.2 Excavation and Trenching
note | FREQUENCY: Prior to Installation
note | ACCEPTANCE CRITERIA: Minimum cover for underground conduits shall be 600mm
note | • Open trenching only permitted in unpaved areas, line of trench to be at right angle to the track
note | • Trench shall maintain a minimum clearance of 300mm from all existing services where possible
note | REFERENCE DOCUMENTS: CE-019-ST-0033 cl 4.2.5 & 4.2.8
note | INSPECTION/TEST METHOD: Verify
note | RECORD OF CONFORMITY: This ITP signed
note | WP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 2.3 Installation of Conduits and pits
note | FREQUENCY: Installation of Conduits and pits
note | ACCEPTANCE CRITERIA: • Conduits in the same run shall be spaced 50mm by using clean sand to pack voids
note | • Conduit shall be embedded in not less than 50mm sand and covered by >50mm - 75mm< sand
note | • Mechanical protection shall be provided by installation of polymeric cable or cover strip of thickness not less than 3mm, and of a material equivalent of UPVC conduit complying to AS 2053. Protective material shall be placed not less than 100mm above the conduit, and shall not be less than 150mm wide.
note | • Conduits shall be joined male to female ends and sealed with approved adhesive immediately prior to joining.
note | • Conduits shall not be subject to construction loadings
note | • Bottom of lowest conduit shall maintain a minimum 100mm above pit floor
note | • Conduits shall be capped with UPVC electrical caps
note | REFERENCE DOCUMENTS: CE-019-ST-0033 cl 4.4
note | INSPECTION/TEST METHOD: Visual inspection
note | RECORD OF CONFORMITY: This ITP signed
note | WP
note | RESPONSIBILITY: Fulton Hogan Engineer/ YT
textbox | DATE:
checkpoint | 2.4 Inspection of conduit installation
note | FREQUENCY: Each Lot
note | ACCEPTANCE CRITERIA: Laying of conduits and installation of pits shall be inspection by superintendent and conform to design drawings before any backfilling procedure is to commence
note | REFERENCE DOCUMENTS: Work procedure
note | INSPECTION/TEST METHOD: Visual Inspection
note | RECORD OF CONFORMITY: This ITP Signed
note | HP*
note | RESPONSIBILITY: Fulton Hogan Engineer/YT
textbox | DATE:
checkpoint | 2.5 Back Fill of Trenches
note | FREQUENCY: Each Lot
note | ACCEPTANCE CRITERIA: Backfilling (for trenching or road crossings)
note | – conduit trench shall be backfilled above marker tape with crushed rock or suitable excavated material and compacted to 90% standard compaction 150mm-200mm below sub base level, the last 150mm-200mm shall be compacted to 100% standard compaction using handheld mechanical plant
note | REFERENCE DOCUMENTS: CE-019-ST-0033 cl 4.2.5
note | INSPECTION/TEST METHOD: Verify
note | RECORD OF CONFORMITY: This ITP signed
note | IP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 2.6 Installation of Draw Cords
note | FREQUENCY: Each Lot
note | ACCEPTANCE CRITERIA: Draw wire shall be provided for each conduit, with extra 3m length at each pit, material to be used shall be 6mm 'telstra rope'
note | REFERENCE DOCUMENTS: CE-019-ST-0033 cl 4.4.6.2
note | INSPECTION/TEST METHOD: Verify
note | RECORD OF CONFORMITY: This ITP signed
note | IP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 2.7 Compaction
note | FREQUENCY: Each Lot
note | ACCEPTANCE CRITERIA: During compaction optimum moisture content of bedding and select fill is within 85% to 115% as provided by suppliers
note | REFERENCE DOCUMENTS: CE-019-ST-0033 cl 4.2.8
note | INSPECTION/TEST METHOD: Verify
note | RECORD OF CONFORMITY: This ITP signed
note | HP*
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | Final Inspection
note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
textbox | Date: