## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP-020 - Exothermic Welding | itp |  |  |  |  | ITP-020 - Exothermic Welding
section | Preliminary Works
checkpoint | 1.1 Check for correct documentation
note | FREQUENCY: Prior to commencing any activity
note | ACCEPTANCE CRITERIA: Ensure that all employees and contractors are using the most current and complete set of drawings
note | REFERENCE DOCUMENTS: Drawings and drawing registers
note | INSPECTION/TEST METHOD: Visual inspection
note | RECORD OF CONFORMITY: This ITP signed off
note | HP*
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 1.2 Implementation of all measures and controls
note | FREQUENCY: Prior to commencing any activity
note | ACCEPTANCE CRITERIA: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, JSEA, SWMS & WP
note | • Ensure that all employees and contractors involved in the welding process have been inducted onto the relevant Hotworks permit
note | REFERENCE DOCUMENTS: PSP, EMP, TMP, JSEA, SWMS, WP
note | INSPECTION/TEST METHOD: Visual Inspection
note | RECORD OF CONFORMITY: This ITP signed off
note | IP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 1.5 Materials Check
note | FREQUENCY: Prior to commencing any activity
note | ACCEPTANCE CRITERIA: Ensure the materials and equipment gathered are for the correct type of connection being made.
note | • Inspect the mould ID tag to ensure that it corresponds to the application, indicated by the following parameters:
note | 1. Mould part number:
note | 2. Conductor size:
note | 3. Welding material required
note | • Check to ensure the graphite mould is not worn or broken, which could cause leakage of molten weld metal during the reaction.
note | • Ensure a working fire extinguisher is available within 10 metres of the working area.
note | REFERENCE DOCUMENTS: Eritech CADWELD Exothermic Welding Manual Fig. 2, 3, 4
note | INSPECTION/TEST METHOD: Visual inspection
note | RECORD OF CONFORMITY: This ITP signed off
note | HP*
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
section | Construction Works
checkpoint | 2.1 Preparation
note | FREQUENCY: Each Weld
note | ACCEPTANCE CRITERIA: Ensure the position of the conductors being welded is correct.
note | • Heat mould to ensure it is dry.
note | • Strip & clean conductors, ensure they are dry & clean.
note | REFERENCE DOCUMENTS: Design Drawings and Register
note | INSPECTION/TEST METHOD: Visual inspection
note | RECORD OF CONFORMITY: This ITP signed off
note | IP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | 2.2 Welding
note | FREQUENCY: Each Weld
note | ACCEPTANCE CRITERIA: Ensure conductors are correctly positioned in the mould, allowing the mould to close tightly.
note | • Ensure welding material has been insected and is intact.
note | • Ensure reaction is completed and molten material has solidified (allow 30 seconds post ignition)
note | REFERENCE DOCUMENTS: Eritech CADWELD Exothermic Welding Manual Fig. 2, 3, 4
note | INSPECTION/TEST METHOD: Verify
note | RECORD OF CONFORMITY: This ITP signed off
note | IP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
section | Testing
checkpoint | 3.1 Weld Review
note | FREQUENCY: Each lot
note | ACCEPTANCE CRITERIA: Ensure weld is inspected and that a quality connection has been made.All welds shall be inspected a Fulton Hogan engineer.
note | REFERENCE DOCUMENTS: Eritech CADWELD Exothermic Welding Manual Fig. 2, 3, 4
note | INSPECTION/TEST METHOD: Verify
note | RECORD OF CONFORMITY: This ITP signed off
note | TP
note | RESPONSIBILITY: Fulton Hogan Engineer
textbox | DATE:
checkpoint | Final Inspection
note | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
textbox | Date: