## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | Sprinkler System Commissioning |  |  |  |  | Yes | Sprinkler System Commissioning | 061fb2b1-7206-469d-8249-41c771b76846
checkpoint-group |  |  | section | Visual inspection
checkpoint-status |  |  | checkpoint | Is the area clear, tidy, dry and accessible? (take multiple photos of installation area)
checkpoint-status |  |  | checkpoint | Check Sprinkler Heads & escutcheons for damage/scratches to paint finish (Take a photo of all damaged sprinklers with room/area reference)
checkpoint-status |  |  | checkpoint | Floor inspection to confirm all system works are complete?
checkpoint-status |  |  | checkpoint | Have the correct sprinklers been installed? (Temperature rating, Fast Response, Finish)
checkpoint-status |  |  | checkpoint | Escutcheon plates installed
checkpoint-status |  |  | checkpoint | Joints, connections,position & spacing / obstruction correct
checkpoint-status |  |  | checkpoint | Shields/guards provided (where specified)
checkpoint-status |  |  | checkpoint | Fixings and supports in accordance with AS2118
checkpoint-status |  |  | checkpoint | Sprinkler Support Systems are installed to not impede other services installed
checkpoint-status |  |  | checkpoint | Ancillary equipment installed? (monitored isolation valve, flow switch, pressure switch)
checkpoint-status |  |  | checkpoint | Block Plans installed and reviewed? (take a photo)
checkpoint-status |  |  | checkpoint | Signage & Labelling, Locks & Straps installed (take a photo)
checkpoint-status |  |  | checkpoint | Seismic Restraints & paint assessed
checkpoint-status |  |  | checkpoint | Is the fire sprinkler valve set drain connected to the drain riser? (take a photo)
checkpoint-status |  |  | checkpoint | Is the fire sprinkler drain riser ran into the hydraulic waste drain? (take a photo)
checkpoint-group |  |  | section | Commissioning
checkpoint-status |  |  | checkpoint | Check operation of the monitored isolation valve and record FIP interface (take a photo of both items at the same time)
checkpoint-status |  |  | checkpoint | Inspect and test gauge operation (record a video of the drop in pressure and the pressure re-stabilising to static working pressure)
checkpoint-status |  |  | checkpoint | Check operation of manual test drain confirm flow switch activation to FIP (record a video and take a photo of the FIP when alarm is activated) (note the time delay)
checkpoint-status |  |  | checkpoint | Check operation of the water pressure switch activation to FIP (record a video and take a photo of the FIP when alarm is activated)
checkpoint-status |  |  | checkpoint | Check operation of solenoid test drain confirm FSW activation to FIP (record a video and take a photo of the FIP when alarm is activated)
checkpoint-status |  |  | checkpoint | Check the operation of the water motor alarm (record a video)
checklist-sectioned |  |  | checklist | Fire Detection System Commissioning |  |  |  |  | Yes | Fire Detection System Commissioning | 291a2dd4-a81c-41cd-acc3-58be11aa7117
checkpoint-group |  |  | section | Visual Inspection
checkpoint-status |  |  | checkpoint | Is the area clear, tidy, dry and accessible? (take multiple photos of installation area)
checkpoint-status |  |  | checkpoint | Floor inspect to confirm all system works are complete
checkpoint-status |  |  | checkpoint | All faults and isolations cleared for area
checkpoint-status |  |  | checkpoint | Smoke and Thermal Detectors are installed in correct dimensioned locations as per the ISSUED FOR CONSTRUCTION drawings?
checkpoint-status |  |  | checkpoint | EWIS/OWS speaker are installed in the correct dimensioned locations as per the ISSUED FOR CONSTRUCTION drawings?
checkpoint-status |  |  | checkpoint | WIP/MCP installed as per AS1670 & BCA
checkpoint-status |  |  | checkpoint | Cable joints and terminations correctly completed with no tension on the terminals?
checkpoint-status |  |  | checkpoint | Compliance with AS1670, AS1668, BCA 2015
checkpoint-status |  |  | checkpoint | All devices are fit off as per ISSUED FOR CONSTRUCTION drawings and clear of any obstructions? (Take a photo of all damaged/obstructed devices with room/area reference)
checkpoint-status |  |  | checkpoint | All devices are numbered correctly using labels (NO MARKERS) and in correct location as per the AS BUILT DEVICE numbering markup?
checkpoint-status |  |  | checkpoint | All traffolyte labels are installed to each WIP/MCP and field module?
checkpoint-status |  |  | checkpoint | Smoke detection & EWIS/OWS block plans installed as per AS1670?
checkpoint-group |  |  | section | Commissioning
checkpoint-status |  |  | checkpoint | Test each Smoke Detector in accordance with AS1670, AS1668, BCA using smoke can and record FIP alarm. (take a photo of the device & panel at the same time)
checkpoint-status |  |  | checkpoint | Test each thermal Detector in accordance with AS1670, AS1668, BCA using a heat detector tester kit can and record FIP alarm. (take a photo of the device & panel at the same time)
checkpoint-status |  |  | checkpoint | Test Speakers in accordance with AS1670 & BCA under general fire alarm and record results using a sound probe meter (record video)
checkpoint-status |  |  | checkpoint | Test Visual Alarm Devices in accordance with AS1670 & BCA under general fire alarm (record video)
checkpoint-status |  |  | checkpoint | Test WIP phones in accordance AS1670, BCA (record video)
checkpoint-status |  |  | checkpoint | Test Manual Call Points in accordance with AS1670, BCA and record FIP/EWIS alarm (record video)
checkpoint-status |  |  | checkpoint | Test Field Module Interfaces in accordance with AS1670, AS1668, BCA and record FIP alarm (take a photo of the Interface and FIP the the same time)
checkpoint-status |  |  | checkpoint | Test the activation of smoke/fire door magnetic hold open devices under local fire alarm (record video)
checkpoint-status |  |  | checkpoint | test the activation of mechanical fire trips under general fire alarm (take a photo of the mechanical GFA trip and FIP in alarm at the same time)
checkpoint-status |  |  | checkpoint | Test the activation of security fire trips under general fire alarm (take a photo of the mechanical GFA trip and FIP in alarm at the same time)
checkpoint-status |  |  | checkpoint | Test the EWIS/OWS time delay for cascading and changing from ALERT to EVAC (record a video of the EWIS/OWS Panel)
checkpoint-status |  |  | checkpoint | Test the activation of network monitoring during latching FIP alarm (attach monitoring company report and photos of the alarm on FIP & Monitoring Device)
checkpoint-status |  |  | checkpoint | Test the activation of the external bell under fire trip mode in accordance AS1670, BCA (record video)
checkpoint-status |  |  | checkpoint | Test the activation of the external strobe under fire trip mode in accordance AS1670, BCA (record video)
checklist-flat |  |  | checklist | In Decks |  |  |  |  | Yes | In Decks | 35475cf7-7f60-49a7-b3b0-8547c42adc71
checklist-flat |  |  | checklist | Site Induction |  |  |  |  | Yes | Site Induction | 551ca017-5be9-4370-be33-b29a492a8c76
checkpoint-status |  |  | checkpoint | Summit Fire Employee - Attach document and photos where required
text | 166c208c-24df-5ee4-9134-e69027924b00 |  | textbox | Name
text | 0d7a6672-e32d-5e58-9eaf-e042cc33a8a4 |  | textbox | Contact Number
text | 6c0892bf-3360-5e83-bdf1-119949e09e12 |  | textbox | Date of Induction
label | ad8dd5d1-9dde-5215-897e-aa6bab4b730c |  | note | Tick if the following are understood:
boolean | b2e42100-bcf2-5be9-ab84-9ab6efe4de1c |  | tickbox | How to report to the site and who you report to
boolean | 67165ada-9a45-53fe-9c74-c6b50d33c7b3 |  | tickbox | The working hours on site
boolean | acd1a1ae-9af2-5e26-965e-7a727ea404d6 |  | tickbox | Who the managers and supervisors are on site
boolean | 583d2b55-ad3a-5cda-9428-bb789d9ce811 |  | tickbox | The correct minimum PPE for site
boolean | e861540a-12dc-50ce-8a8e-f660b83f3e5a |  | tickbox | How safety is communicated on site
boolean | 50d62e18-dbf7-5c33-81fd-2251567730bb |  | tickbox | Where to have lunch and where the toilets are
boolean | 0a5065ba-61b7-5393-bfd1-6eda6940dadc |  | tickbox | Where the First Aid Kit is kept and who is the First Aider
boolean | 10addab5-5825-56a1-8acc-dc5d0dcf9633 |  | tickbox | The Emergency Plan and the Assembly Area for Emergency Evacuation
boolean | a4508167-5c3d-554b-9d5f-55ab9a7e7958 |  | tickbox | What the high risk activities and hazards are on site
boolean | ea898840-0990-5db9-8905-a5464666ad31 |  | tickbox | How to report WHS & Environmental hazards & issues
boolean | 89f29677-e695-595f-ae02-11ca34b74a0f |  | tickbox | How to report a safety or environmental accident or incident
boolean | 86386b0c-1803-53c7-9894-3881db7d5679 |  | tickbox | Housekeeping responsibilities
checkpoint-status |  |  | checkpoint | Current Certificates Sighted - Please take a photo & comment on each attached certificate
checkpoint-status |  |  | checkpoint | Summit Fire Employee Signature
checkpoint-status |  |  | checkpoint | Summit Fire Supervisor Signature
checklist-flat |  |  | checklist | Document Attachment |  |  |  |  | Yes | Document Attachment | 59283f2d-19e4-4398-83b3-bf84ddbc784a
checkpoint-status |  |  | checkpoint | Attach relevant documents
checklist-sectioned |  |  | checklist | Fire Detection Installation ITP |  |  |  |  | Yes | Fire Detection Installation ITP | 5afa3549-2098-4827-b2d5-a600f978e846
checkpoint-group |  |  | section | Initial Site Establishment
checkpoint-status |  |  | checkpoint | Is the area clear, tidy, dry and accessible? (take multiple photos of installation area)
checkpoint-status |  |  | checkpoint | Delivery inspection (Take a photo of the delivery taking place and of delivery docket) (*note: list all items not delivered)
checkpoint-status |  |  | checkpoint | Does the delivery/delivery docket match the order?
checkpoint-group |  |  | section | Dry Fire Cable Rough In
checkpoint-status |  |  | checkpoint | Is the area clear, tidy, dry and accessible? (take multiple photos of installation area)
checkpoint-status |  |  | checkpoint | Installation drawings are the most recent revision and are ISSUED FOR CONSTRUCTION? (take a photo)
checkpoint-status |  |  | checkpoint | Room/area layout set out and confirmed with the assistance of building team? (Take a photo/signature from both parties required)
checkpoint-status |  |  | checkpoint | Cable installed to device locations as per the most recent ISSUED FOR CONSTRUCTION drawings?
checkpoint-status |  |  | checkpoint | Cable supports installed correctly? (take multiple photos)
checkpoint-status |  |  | checkpoint | Sufficient slack in cable to reach required fit off location?
checkpoint-status |  |  | checkpoint | Cable tray installed as per AS 3000? (take photos of installed tray)
checkpoint-status |  |  | checkpoint | Fire Detection cable has compliant spacing between Detection, EWIS/OWS and electrical power cable? (take multiple photos)
checkpoint-status |  |  | checkpoint | Fire Rating/acoustic sealing of penetrations completed prior to ceiling sheeting? (Take a photo of each sealed penetration back and front)
checkpoint-status |  |  | checkpoint | Are wires clearly drawn and submitted for AS BUILTS/AS CONSTRUCTED drawings (take a photo of the drawing with line diagram clearly shown)
checkpoint-status |  |  | checkpoint | Are all devices numbered on drawing for AS BUILTS/AS CONSTRUCTED drawings? (take a photo of the drawing with device number clearly shown)
checkpoint-status |  |  | checkpoint | Riser Cable Tray Installation & cables installed in a neat order? (take a photo)
checkpoint-status |  |  | checkpoint | Cable supported to tray
checkpoint-status |  |  | checkpoint | Fire Rating/acoustic sealing of penetrations completed prior to ceiling sheeting? (Take a photo of each sealed penetration top and bottom)
checklist-sectioned |  |  | checklist | Sprinkler System Installation Fit Off ITP |  |  |  |  | Yes | Sprinkler System Installation Fit Off ITP | 65c2d0af-99eb-443e-89ac-d4d0b35cf560
checkpoint-group |  |  | section | Fit Off - Part 1
checkpoint-status |  |  | checkpoint | Is the area clear, tidy, dry and accessible? (take multiple photos of installation area)
checkpoint-status |  |  | checkpoint | Check Sprinkler Heads for damage/scratches to paint finish (Take a photo of all damaged sprinklers with room/area reference)
checkpoint-status |  |  | checkpoint | Check Flexi for damage/kinks (take a photo of any damaged Flexi with room/area reference)
checkpoint-status |  |  | checkpoint | Check the water is drained the water out of the system (take a photo)
checkpoint-status |  |  | checkpoint | Installation drawings are the most recent revision and are ISSUED FOR CONSTRUCTION? (take a photo)
checkpoint-status |  |  | checkpoint | Laser used to fit off to accurate measurements? (Take a photo of each sprinkler in final position)
checkpoint-status |  |  | checkpoint | Sprinklers installed as per AS2118 with no obstructions? (Take multiple photos)
checkpoint-status |  |  | checkpoint | Have the correct sprinklers been installed? (Temperature rating, Fast Response, Finish) (take photos)
checkpoint-status |  |  | checkpoint | Check the water is reinstated into the system at the completion of fit off (take a photo)
checkpoint-group |  |  | section | Fit Off - Part 2
checkpoint-status |  |  | checkpoint | Is the area clear, tidy, dry and accessible? (take multiple photos of installation area)
checkpoint-status |  |  | checkpoint | Check sprinkler heads for damage/scratches to paint finish (Take a photo of all sprinklers required for area of installation)
checkpoint-status |  |  | checkpoint | Check sprinkler heads are straight and parallel to finished surface (Take a photo of each sprinkler in final position with room/area reference if moved or damaged)
checkpoint-status |  |  | checkpoint | Check there is no paint or gyprock setting on sprinkler head (Take a photo of each sprinkler in final position with room/area reference if damaged)
checkpoint-status |  |  | checkpoint | Outer escutcheon plates installed
checkpoint-status |  |  | checkpoint | Check there is no gaps between the outer escutcheon plate and the finished ceiling
checkpoint-status |  |  | checkpoint | Sprinklers installed as per AS2118 with no obstructions? (Take multiple photos)
checkpoint-group |  |  | section | Hydrostatic Pressure Test
checkpoint-status |  |  | checkpoint | 1.6MPa or 400 kpa in excess of the maximum static working pressure (whichever is greater) for a period of 2 hours, with no loss of pressure duration the 2 hour duration.
checkpoint-status |  |  | checkpoint | Are the pipework Joints, connections, position & spacing correct?
checkpoint-status |  |  | checkpoint | Are all open ends plugged off to close up the piping network?
text | 53c940ec-4b96-5f19-aa1d-631519905e18 |  | textbox | Start Time:
text | 52c82cee-4b01-5139-a8ca-59ba74c67cb5 |  | textbox | Test Pressure:
checkpoint-status |  |  | checkpoint | Attach picture of pressure test gauge:
text | a75ab43f-9105-5fa0-b04c-783ccd5d38bf |  | textbox | Finish Time:
text | ac27d9d5-04f5-57bb-af09-da614208f982 |  | textbox | Test Pressure:
checkpoint-status |  |  | checkpoint | Attach picture of pressure test gauge:
checkpoint-status |  |  | checkpoint | Any pressure loss during test?
checkpoint-status |  |  | checkpoint | Summit Fire Representative & Builder Representative to sign prior to closing out
holdpoint |  |  | signoff | Summit Fire Representative & Builder Representative to sign off
checklist-sectioned |  |  | checklist | Sprinkler System Installation ITP |  |  |  |  | Yes | Sprinkler System Installation ITP | 99142f4b-7dcb-43d0-bbc7-0c9a487f0c5c
checkpoint-group |  |  | section | Initial Floor/Area Establishment
checkpoint-status |  |  | checkpoint | Is the area clear, tidy, dry and accessible? (take multiple photos of installation area)
checkpoint-status |  |  | checkpoint | Delivery inspection (Take a photo of the delivery taking place and of delivery docket) (*note: list all items not delivered)
checkpoint-status |  |  | checkpoint | Does the delivery/delivery docket match the order?
checkpoint-status |  |  | checkpoint | Piping & weld quality reviewed?
checkpoint-status |  |  | checkpoint | Fabrication sheets match the pipe delivered to site? (Take a photo of the fabrication check sheet)
checkpoint-status |  |  | checkpoint | Have the correct sprinklers been delivered? (Take a photo of all sprinklers required for area of installation)
checkpoint-group |  |  | section | Initial Installation
checkpoint-status |  |  | checkpoint | Is the area clear, tidy, dry and accessible? (take multiple photos of installation area)
checkpoint-status |  |  | checkpoint | Check sprinkler heads for damage/scratches to paint finish (Take a photo of sprinklers required for area of installation)
checkpoint-status |  |  | checkpoint | Flexi compliant to AS2118 and FM approved? (take a photo of the data sheet)
checkpoint-status |  |  | checkpoint | Sprinklers neatly hemped and soaped (with inner escutcheon plates installed, if required)? (take a photo)
checkpoint-status |  |  | checkpoint | Installation drawings are the most recent revision and are ISSUED FOR CONSTRUCTION? (take a photo)
checkpoint-status |  |  | checkpoint | Grid lines marked out and confirmed with the assistance of building team? (Take a photo/signature from both parties required)
checkpoint-status |  |  | checkpoint | Pipework installed as per the ISSUED FOR CONSTRUCTION drawings? (correct heights, measurements off grid lines)
checkpoint-status |  |  | checkpoint | Pipework hangers/supports installed correctly? (take multiple photos)
checkpoint-status |  |  | checkpoint | Concealed space sprinklers installed as per AS2118 with no obstructions? (Take multiple photos)
checkpoint-status |  |  | checkpoint | Flexi installed to manufacturers specs and tied up away from possible damage? (Take multiple photos)
checkpoint-status |  |  | checkpoint | Have the correct sprinklers been installed? (Temperature rating, Fast Response, Finish) (take photos)
checkpoint-status |  |  | checkpoint | Riser pipework installed as per the ISSUED FOR CONSTRUCTION drawings?
checkpoint-status |  |  | checkpoint | Riser hangers/supports installed correctly? (take photos)
checkpoint-status |  |  | checkpoint | Fire sprinkler control valve installed and connected to system, riser and drain pipework? (take a photo when installation complete)
checkpoint-status |  |  | checkpoint | Fire Rating/acoustic sealing of penetrations completed prior to ceiling sheeting? (Take a photo of each sealed penetration back and front)
checkpoint-status |  |  | checkpoint | Fire Rating/acoustic sealing of riser penetrations completed? (Take a photo of each sealed penetration above and below)
checkpoint-status |  |  | checkpoint | Exposed fire sprinkler pipework completely painted to required colour? (Take multiple photos)
checkpoint-status |  |  | checkpoint | Any changes to installation recorded for AS BUILT DRAWINGS (Mark up most recent plans and take a photo of each change)(make a note as why the change was made)
checklist-flat |  |  | checklist | Toolbox Meeting |  |  |  |  | Yes | Toolbox Meeting | 9ad6043a-f4f8-47ec-a24f-775d9de958d0
checkpoint-status |  |  | checkpoint | Toolbox signed off - Attach an forms
text | b4cdaa08-86a1-5cf6-97b6-3dfdf18d86dc |  | textbox | Toolbox Talk Location
text | 75f7cdf5-48c1-57e5-9012-ae190e59b10d |  | textbox | Person Conducting Toolbox Talk
text | 771892ef-4c8e-5f1a-bfbb-dbf9f72e36f5 |  | textbox | Date
text | 4a0c758d-82e0-5fff-8130-879b6649fdf6 |  | textbox | Time am / pm
text | d95a07de-601f-5ac0-b9b7-6178bf7dc473 |  | textbox | Actions from last meeting
text | 7f7b14dc-7920-5f96-b7fa-15a4a58bc0e2 |  | textbox | Injuries last week
text | 77f1d0dd-d755-58f8-9cbe-8e5d469e8146 |  | textbox | Near misses last week
text | 0d306f73-afcc-51f6-9976-ec5f080a123a |  | textbox | Safety Items discussed
text | 51dfe15d-86c1-5f63-923f-784119be9fc7 |  | textbox | Comments from the floor
text | cde1319e-dab5-5aa4-b47e-f374a7c02a58 |  | textbox | Upcoming works for the week
text | 85cf087b-44a9-5ec1-ab29-ee0bd66cb5b6 |  | textbox | New Business items to discuss
text | 78ac67f1-102b-51e8-9ca3-7f575e46836a |  | textbox | Attendees
checkpoint-status |  |  | checkpoint | Attendance verified
checklist-flat |  |  | checklist | Smoke Detection & EWIS/OWS Fit Off |  |  |  |  | Yes | Smoke Detection & EWIS/OWS Fit Off | 9fd43d0c-5623-4144-8748-20f5e664abe8
checkpoint-status |  |  | checkpoint | Is the area clear, tidy, dry and accessible? (take multiple photos of installation area)
checkpoint-status |  |  | checkpoint | Installation drawings are the most recent revision and are ISSUED FOR CONSTRUCTION? (take a photo)
checkpoint-status |  |  | checkpoint | Excess slack in cable removed?
checkpoint-status |  |  | checkpoint | Smoke and Thermal Detectors are installed in correct dimensioned locations as per the ISSUED FOR CONSTRUCTION drawings?
checkpoint-status |  |  | checkpoint | Check Thermal and Smoke Detectors installed in accordance with AS1670, AS1668, BCA (take photo of data sheet for devices being installed)
checkpoint-status |  |  | checkpoint | EWIS/OWS speaker are installed in the correct dimensioned locations as per the ISSUED FOR CONSTRUCTION drawings?
checkpoint-status |  |  | checkpoint | Laser used to fit off to accurate measurements? (Take a photo of each detector/speaker in final position)
checkpoint-status |  |  | checkpoint | WIP/MCP installed as per AS1670 & BCA (take photo of each device after installation)
checkpoint-status |  |  | checkpoint | All devices are numbered correctly using labels (NO MARKERS) and in correct location as per the AS BUILT DEVICE numbering markup?
checkpoint-status |  |  | checkpoint | All devices are fit off as per ISSUED FOR CONSTRUCTION drawings and clear of any obstructions? (Take a photo of all damaged/obstructed devices with room/area reference)
checkpoint-status |  |  | checkpoint | Cable joints and terminations correctly completed with no tension on the terminals?
checkpoint-status |  |  | checkpoint | All traffolyte labels are installed to each WIP/MCP and field module?
checklist-flat |  |  | checklist | Daily Pre Start/Works Checklist |  |  |  |  | Yes | Daily Pre Start/Works Checklist | b26da6bf-c2b2-4d55-928e-ce6df591e62e
checkpoint-status |  |  | checkpoint | Daily pre start meeting completed
text | c8892e97-a7a4-5f3f-a0cb-4c50c3b15e91 |  | textbox | Date
text | a2079501-1c48-5651-b34f-1b21f67338b4 |  | textbox | Time
text | 95e56cf1-de54-5ce9-b828-4c5a13075a3b |  | textbox | Location of work being performed
checkpoint-status |  |  | checkpoint | Is the area clear, tidy, dry, accessible and well lit? (take multiple photos of installation area)
checkpoint-status |  |  | checkpoint | Delivery inspection (Take a photo of the delivery taking place and of delivery docket) (*note: list all items not delivered)
checkpoint-status |  |  | checkpoint | Does the delivery/delivery docket match the order placed? (*note: list all items not delivered)
checkpoint-status |  |  | checkpoint | Are the correct tools ready for today's tasks?
checkpoint-status |  |  | checkpoint | Are Power tool batteries on charge?
checkpoint-status |  |  | checkpoint | Is the threading machine, drop saw and pipestand set up and ready for use?
checkpoint-status |  |  | checkpoint | Are all leads suspended off the ground, plugged into an RCD and test & tagged in date?
checkpoint-status |  |  | checkpoint | Are the correct height ladders being used for today's tasks?
checkpoint-status |  |  | checkpoint | Do you have the correct mandatory PPE on? (Hard Hat, Hi Vis shirt/jumper/jacket, Steel toe Boots, Safety Glasses, Safety gloves and Ear Plugs?
text | c5ffff0d-d81f-5930-95ad-7c822d8700cf |  | textbox | Project Manager
text | 79c3763b-b9ba-5661-ad52-50a5b90dd551 |  | textbox | Any issues from the previous day
text | 7d3269c0-9fd9-5e57-8e58-a560c730bdd6 |  | textbox | Any unfinished works from the previous day in the area of works?
text | 482f4e2b-32f3-5c45-aa27-9b5db3f6b410 |  | textbox | First aiders on site today
text | 10e79688-1038-57d8-b27b-2cec681d2678 |  | textbox | Who are you working with today?
text | 9d11e1ee-99c5-5ec4-a18c-db570749ed7f |  | textbox | today's tasks / jobs
text | b0d2c6f6-eb64-5541-8fb9-77f4165d0e18 |  | textbox | Any unfinished tasks / jobs from today's items? (list the items unfinished & explain why the tasks were not finished)
text | 20d58dc9-e04e-5afc-9e0c-3d26c18bd7e1 |  | textbox | Attendees
checkpoint-status |  |  | checkpoint | Summit Fire Supervisor Signature
checklist-flat |  |  | checklist | Injury Form |  |  |  |  | Yes | Injury Form | d8db398c-a0f2-4597-aa13-040d0c939237
checkpoint-status |  |  | checkpoint | Injury form completed
text | c034e62a-f270-5e8e-851d-a96cf80dd6df |  | textbox | Date of incident
text | 39c7067d-af2f-58c7-b369-6cbe934e447f |  | textbox | Time
text | 028a4c6d-9e90-5688-ad16-0a24c40a9662 |  | textbox | Site location of the accident / incident (take multiple photo of area of incident)
text | 99d260d7-f1d6-5d08-92b2-308ab6837724 |  | textbox | Detail of how the accident / incident happened
label | 97ed0e9e-0e88-5684-8c58-3d2e0ccf9974 |  | note | Details of injured person
text | 55b44264-8ce4-5817-b7f7-6261d4578eda |  | textbox | First name
text | 6b587e61-a2f3-589c-9a49-5546a9d4c05d |  | textbox | Last name
text | aa379057-e2af-5c72-be44-a862b1b5d733 |  | textbox | DOB
text | c1fd00e2-f6b6-5916-97ca-dc7d72f14504 |  | textbox | Contact No
text | 5afb922a-eee7-5773-acaa-87902e9baccb |  | textbox | Address
text | a9318e72-fe54-57d4-9a31-d857afd3ab23 |  | textbox | Company
text | c5548bb4-30f2-5b3e-97e3-abe01fdd7b39 |  | textbox | Trade
text | db3a9839-6cbc-5683-8ccd-387d455273e7 |  | textbox | Date Inducted
select | b2c712ec-0d7a-5c03-ac9e-11cc19424a13 |  | dropdown | Type of injury | Electrocution
text | 218953ab-2030-574e-b463-2d5cd053e044 |  | textbox | Location on body
text | de2d5a17-a05b-592e-ad42-6c82ca1f9126 |  | textbox | Treatment
text | 24d93ad4-e5ec-541e-bef6-9103feb5837d |  | textbox | Initial treatment given
text | f306e274-d40b-5141-aa08-1a02a7608639 |  | textbox | Was follow up treatment provided
text | d044495c-8c6e-5f5e-a1d8-3f0ad9f5871e |  | textbox | Medical centre / Doctor / Hospital attended
text | 1fab7e40-3b44-5a9d-9891-ea4b4980c0c8 |  | textbox | Date / time attended
label | eba5c23f-d855-53c4-877b-1ce4754ca569 |  | note | Witness details
text | a39e2eab-4d27-5e28-8a55-73de4a9f7782 |  | textbox | Witness name & contact details
text | df34d1e7-5f83-5e12-a109-f85e5e5e59be |  | textbox | Witness name & contact details
text | 583c4740-8481-5704-81b8-e8b247b89d5f |  | textbox | Event details / cause
text | e87ed791-3e7c-5297-8f05-3668f73ed3e6 |  | textbox | Other
checkpoint-status |  |  | checkpoint | Signature of injured worker
checkpoint-status |  |  | checkpoint | Person completing this form
checkpoint-status |  |  | checkpoint | Signature of person completing this form
checkpoint-status |  |  | checkpoint | Builder Representative Witness
checkpoint-status |  |  | checkpoint | Signature of Builder Representative Witness
checklist-flat |  |  | checklist | Variation |  |  |  |  | Yes | Variation | db9c0173-a28f-45cb-99bc-76b06c1c9187
checkpoint-status |  |  | checkpoint | Variation / SI Details Entered
label | be9683e7-e5d2-5edb-b9d7-657ea95afc4e |  | note | Please take before photos
text | a6cf0f57-cbe2-5388-bb7f-c4eb54127d57 |  | textbox | Work type:
text | 53952469-190f-5ef5-afd9-1aa601582aa4 |  | textbox | Attention:
text | be19bbb4-b39d-5d01-8b9e-b631de72c2d0 |  | textbox | Area/Location
text | b72c9ac0-f0f3-5e37-b08d-d7bd941fd18a |  | textbox | Date
text | 8906f05a-9e5e-5dde-abd2-94f3d33ce919 |  | textbox | Scope of work
text | 89e84c52-d294-53bf-8987-2dbd068fece9 |  | textbox | Normal Hours
text | b505eda0-8da2-5fcf-946e-1bd08d099480 |  | textbox | Overtime Hours
text | 2e895b7e-9a5b-5086-8d4b-72ab6db3f44c |  | textbox | Material to complete task
checkpoint-status |  |  | checkpoint | Reference/SI Number Entered
text | acd3fc8f-3055-5302-a616-01177183d79c |  | textbox | Reference/SI Number
checkpoint-status |  |  | checkpoint | Variation / SI Work Completed
checkpoint-status |  |  | checkpoint | Values added (Office use only)
text | a7b88a23-f9bd-5c9e-9a1f-9518677ffbfd |  | textbox | Labour Value
text | 72572ce5-7a0a-5bde-94ed-bf43e8074b0b |  | textbox | Material Value
text | a535fa94-8076-513f-b628-d2bed0c97df2 |  | textbox | Measured Items
text | 93082168-9648-5dde-9211-06f7b9d209ec |  | textbox | Total Variation Value
checklist-flat |  |  | checklist | Fire Pump Commissioning |  |  |  |  | Yes | Fire Pump Commissioning | f8799ca4-0f36-4750-b4ae-f4bbce649e1e
checkpoint-status |  |  | checkpoint | Floor inspect to confirm all system works are complete
checkpoint-status |  |  | checkpoint | Confirm schematic design reference & pump room design drawings reference
checkpoint-status |  |  | checkpoint | Installation of only approved sample equipment & to approved drawing
checkpoint-status |  |  | checkpoint | Confirm factory acceptance testing documents from supplier
checkpoint-status |  |  | checkpoint | Complete pump room hydrostatic test
checkpoint-status |  |  | checkpoint | Confirm/witness Axis Hydrostatic testing of pipework system
checkpoint-status |  |  | checkpoint | Check pump area for obstructions
checkpoint-status |  |  | checkpoint | Check pump discharge drains
checkpoint-status |  |  | checkpoint | Check signage and ID plates on engine & pump
text | 1df1d52f-3cc4-55d2-a847-74bbfad3cf50 |  | textbox | Check and record number of water supply valves are secured
text | b6d6e98c-e6ff-5945-b28f-e8ec602fdbaa |  | textbox | Record and verify pressure gauge readings suction kPa
checkpoint-status |  |  | checkpoint | Check general condition of Pump
checkpoint-status |  |  | checkpoint | Check Pump controller
checkpoint-status |  |  | checkpoint | Check monitor and engine start batteries and record
checkpoint-status |  |  | checkpoint | Check controller safety functions, alarms, set point validation and measurement of fuel consumption
checkpoint-status |  |  | checkpoint | Pump Run Operation, Run for 10 mins @ 0 flow (record)
label | 3fab7df7-6aa8-5964-8bb2-a1c4ad8505a3 |  | note | Check Pump Starting devices and record
text | 2958e36d-3007-5d28-a874-5143efd241cb |  | textbox | Starting pressure (kpa)
text | b3c57d18-926b-5123-ac97-8633ed81e6b8 |  | textbox | Run time
text | 2eaa8cfc-ec89-5df6-8c1d-2dc59ba19cac |  | textbox | Hour meter
label | e958e74e-cf33-5460-8108-5344b55fab2a |  | note | Check and verify pump operation and record in comments
text | c6478c64-a7fd-578c-89d2-6f1cd978671c |  | textbox | Suction (kPa)
text | a1331513-5aef-5f61-9bcf-130d54e9f4e4 |  | textbox | Discharge (kPa)
text | 384f553b-056c-5428-a341-c7f2a5dd513c |  | textbox | Charger Voltage (V)
text | 1fc4d4b4-9f58-59c6-990e-a260db0d2912 |  | textbox | Oil Pressure (kPa)
text | fd5fcc8b-4e5f-521d-a857-e355c60dc5bf |  | textbox | Engine Temp (C)
checkpoint-status |  |  | checkpoint | Pump Run Operation, Run for 10 mins @ 130% flow (record)
label | 3041b2bd-c6b4-5bc4-9c81-b168a4b62ee3 |  | note | Check Pump Starting devices and record
text | 861b64c0-e37a-50fa-b8c4-b1c9b60d6257 |  | textbox | Starting pressure (kpa)
text | f2ed6482-682f-5036-8482-859b7391b5ca |  | textbox | Run time
text | fae4c683-a0e3-5e11-9e03-2bb9923fd804 |  | textbox | Hour meter
label | acc5eb81-41d3-53bd-9d98-1bf1b2938f82 |  | note | Check and verify pump operation and record in comments
text | 4867da45-f7f3-5dda-ad73-a863bf01f841 |  | textbox | Suction (kPa)
text | b7c73caf-c7ad-5880-9a09-c7d1d1c5cc18 |  | textbox | Discharge (kPa)
text | 61848661-d87c-532b-92f1-3dad1f7a94fb |  | textbox | Charger Voltage (V)
text | 60d80e4c-a24e-5ae7-9920-b892b4f29710 |  | textbox | Oil Pressure (kPa)
text | 82400243-d618-5cf9-bb93-371714be4e12 |  | textbox | Engine Temp (C)
checkpoint-status |  |  | checkpoint | Pump Run Operation, Run for 10 mins @ reduce flow to duty (record)
label | 1e74f7fc-020d-5813-af65-fbf7ca886a35 |  | note | Check Pump Starting devices and record
text | 65cecf0d-093e-5195-8ec1-3f297cb73fc2 |  | textbox | Starting pressure (kpa)
text | 1c28988e-e040-5b7b-9540-06b33ae0fb0b |  | textbox | Run time
text | 708bf40e-26fe-55d4-a13a-620e11c984fa |  | textbox | Hour meter
label | f8a372a2-a7ac-5057-88b6-3597632bdf02 |  | note | Check and verify pump operation and record in comments
text | 1320101b-e651-5068-8509-84ba0ecfb7a1 |  | textbox | Suction (kPa)
text | d331109e-98ee-5533-9f17-73aeb0b3d6bf |  | textbox | Discharge (kPa)
text | 54ed0291-991f-55ea-ba55-2a10c3a333b2 |  | textbox | Charger Voltage (V)
text | fdb5123a-0b79-577f-af64-a129d2f0959c |  | textbox | Oil Pressure (kPa)
text | 2839844c-4e58-53d6-9719-57a6081a98ef |  | textbox | Engine Temp (C)
checkpoint-status |  |  | checkpoint | Pump Run Operation, Run for 10 mins @ 0 flow until the pump has run for 30 mins
label | 9b0ac51d-909f-52d2-9477-243a239ab66a |  | note | Check Pump Starting devices and record
text | 1f6a69f9-8f4f-5a6d-879d-c72f63a6adb0 |  | textbox | Starting pressure (kpa)
text | 595d2ce1-a991-5b8d-a49a-675f187c6f53 |  | textbox | Run time
text | bfdd476f-b021-5b5c-a242-6cfe15146c00 |  | textbox | Hour meter
label | badb9479-2db9-552e-ac96-a8130e7d64a2 |  | note | Check and verify pump operation and record in comments
text | a95d8f84-281c-5e49-9b13-eba71449cd46 |  | textbox | Suction (kPa)
text | f1b224f8-32f0-5c72-b5e6-20c42bef8fd9 |  | textbox | Discharge (kPa)
text | 73d3a620-9ce9-529e-9778-8fb4879eca1c |  | textbox | Charger Voltage (V)
text | 739bd866-ef27-5e2e-b845-80228fce9e0c |  | textbox | Oil Pressure (kPa)
text | 7a0acbc2-ab35-5ac7-9a88-a6940b82b4d7 |  | textbox | Engine Temp (C)
label | 1fb92a62-2b77-560d-b835-de07aa3380e2 |  | note | Basement & Podium
label | e1169fd2-bb56-58c0-a8b9-1151d7a755f7 |  | note | Pressure Zone / Level Reference of Test