## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
e4529af1-4d14-4a6d-94e4-e7f1f09cb258 | checklist | Builder |  | Builder
28c97fd7-2527-4fd4-baf8-4d0c2fccb8b7 | section | Details
14a202cf-8f7a-40cd-a667-aa9bf85b636d | checklist | Commissioning |  | Commissioning
7a261420-2f34-4e4a-85fd-4cf8bc9d33c7 | section | Details
9cd234b4-4b75-4362-9050-d4f712f09358 | checkpoint | SCV-Locks/chain/labels/pipework stickers/sprinkler spares & spanner/block plans
ef49ed03-1902-42de-a8c7-c164e965ffa9 | checkpoint | Booster Cupboard-Signage/Locks/chain/labels/plan sleeve+block plans label/block plans
f341e1d1-81b5-41ae-92ba-2718d4e28c53 | checkpoint | Hydrant Mains/Isolation Valves-Locks/chain/labels/pipework stickers
2988230d-be66-4888-9696-dd75e34a3b27 | checkpoint | Water Meter Assembly-Locks/chain/labels
c9120805-7e2f-43cf-b7c6-33f27bc52b47 | checkpoint | Check sluice valves & water meter valves are open
ceaf4774-1cdb-4502-b9aa-9ca437d2d4d3 | checkpoint | Fire Pump/Tank-Fuel full, Exhaust piped, Mains power, Drains/Relief Valve piped, Water Supply on, Locks/chain/labels/pipework stickers
8c9f6fa2-abe7-4121-bc6f-1b81cc3a7b34 | checkpoint | Adjust Bermads & float Valves to fire tanks
8c7772ae-c777-4cea-a24a-00309136dc3e | checkpoint | Pump Room-Block Plans
718b3be4-223b-43ca-8582-a06029820045 | checkpoint | FIP-Block plans/test all alarm devices
7ac428d0-cc12-4ac3-af31-bf8472a5e9fa | checkpoint | Test all Valves & Flow switches to ensure correct operation
c36fa758-fb6f-44a8-8a6f-868cd21a9569 | checkpoint | Set Pressure switches to Jacking pump & alarm line
a654b5d7-6ac9-4d62-869a-bd807a45d32a | checkpoint | Block plans/Tactical Fire plans/FRV way finding plan
ff6d8d7a-5669-40c5-844e-3ba0b310faf8 | checkpoint | FRV Shortfall drawings & FRV stat signage ie: x2 30m hose
54d5b476-a428-4e80-922d-ce5797e84248 | checkpoint | Individual Floor Block plans (If applicable)
2c46fd76-00ad-4a40-adef-0822e2cbaeaa | checklist | Fire Booster Cupboard |  | Fire Booster Cupboard
a0c5ce41-65c3-4824-9e3e-62adaf498fe3 | section | Details
59f74c38-fcf5-4249-b2d7-8ba49a28501d | checkpoint | Install Suction/ Millcocks & Hydrant, Sprinkler Boosters
d03ef1b7-7add-47f6-8fbd-b63fd2e11fe0 | checklist | Fire Extinguishers/Blankets |  | Fire Extinguishers/Blankets
12c59d2f-c068-49c0-b205-fa012b3e14e4 | section | Details
c390e3c0-ed75-4356-92c0-9be32ee2cfa2 | checkpoint | Install Extinguishers
76087e22-d3ef-4ad3-9b47-5d40cb710b99 | checkpoint | Install appropriate signage
47881aad-ef2c-4a33-8c30-70d409275e8c | checkpoint | Install Fire Blankets
8c312f86-d071-4442-a7b2-a1d04c954c6c | checkpoint | Fire Hose Reel signs
6cde9721-e138-4ece-a2e7-66f28ebdeff6 | checklist | Fire Penetrations checklist |  | Fire Penetrations checklist
a0a728a3-f8db-4876-a1d1-8718bbcd30b1 | section | Details
8f6c8ab4-d800-4eb6-b642-b1cdbfa4f5dc | checkpoint | Fire Penetration labelled & caulked in accordance with AS 4072.1 - refer to penetration matrix for fire sealing requirements
54aa107b-ee98-4ff1-b51a-9b9bd5911a61 | checklist | Fire Pumps/Tanks |  | Fire Pumps/Tanks
522cfbf5-c97e-474a-bf94-86bfc4155713 | section | Details
ebb4c0df-4dc4-4b27-8e95-ef0fc124f18e | checkpoint | Install Plinth & secure
7326c165-cdcb-4b18-91ae-df6df68aa2f8 | checkpoint | Install Pumps & secure to plinths
ca2a8763-1866-4602-8b0a-4dab7be9b5e7 | checkpoint | Install all pipework/isolation valves to pumps
ff4d895c-d645-4db1-b3f0-6f00e1ed04b0 | checkpoint | Install Annubar/coolant drains
195eec10-c6a1-43d9-be1d-a45cc1a8a928 | checkpoint | Install Pump Exhaust to designated point
21dbe8e7-4477-41dd-9db9-22fa694bf2a0 | checkpoint | Water Test all Pipework to pumps
121f7cb3-d820-42c9-a378-052ccab360c3 | checkpoint | Install all Pipework and Valves to Fire Tank
bd604203-bf6a-44e9-8f20-b3979480d2ab | checkpoint | Water test all pipework to and from Water Tank
830504c2-3c8e-4c67-81da-b9f6aa1c1e3c | checklist | Hydrant/ Sprinkler Mains / Risers / Hose Reel checklist |  | Hydrant/ Sprinkler Mains / Risers / Hose Reel checklist
c75b3e2b-23d9-4d3c-a8ec-c7f7ce08930c | section | Details
db7a040b-8d0c-4ff2-a4f0-8ab0526a0686 | checkpoint | Rough In: All Mains & isolation valves installed
17aabfcc-c1ee-4424-a9b2-a83bd0475550 | checkpoint | Install Hydrant/ Sprinkler/Test Drain Risers & Mill Cocks
e081fb5e-aa13-4404-9f85-1ab18b2c02a7 | checkpoint | Sprinkler Floor Control Valves installed and secured
aa876a69-f979-4393-8ef2-b0a93d6b5447 | checkpoint | Fit Off: Check all millcock clearances/angles/Mill cocks in closed position & Install 2400kPa pressure gauge to top of risers
426c90ea-3b85-41ac-8879-de5dbf76e646 | checkpoint | Install Fire Hose Reels & pipework
1c89c732-c41f-4544-a345-8bd6db6912a7 | checkpoint | Air Test: Pressurized air test for a period of 30 mins (if applicable)
2f2d2e3e-49da-56a6-96ed-29f83a7271b3 | textbox | Start time:
ea765a8a-34ec-5025-881a-7cacda98d29e | textbox | Completion time:
b9648d67-28ad-4731-a895-d0d006cb95d6 | checkpoint | Water Test: Pressure test to 1700Kpa for duration of 2 hours
c5bbf0b4-becb-5dfe-8aa5-ec91d75fc0c7 | textbox | Start time:
4b2e637f-b769-5036-98ff-c8b1f325391f | textbox | Completion time:
7f276d88-7c4d-4071-bcf1-acfdd505de5c | checkpoint | FHR: All FHR been bled from excess air & proof of water
cc2d2295-e2b7-4c73-bf81-10be33a66f53 | checkpoint | PFP Foreman signature
d670d81e-efbe-43c3-a448-aca9f703c1b1 | checklist | Incident Reports |  | Incident Reports
25883ae8-acfd-4baf-b35f-ead5150780bd | section | Details of accident/incident
aa691bf8-d38b-426c-9f3e-f2a93d74db41 | checkpoint | Please attach any relevant photos & documents
5e96180c-d5cf-56e9-ab11-610441d864f6 | textbox | Date of incident
1d2942b0-80cf-5d1a-913b-9cdfba075124 | textbox | Time of incident:
e6149fed-9c41-5dba-b9b7-077313fe5270 | textbox | Time of report:
553ccfab-8304-4e72-abe1-9cffd29ef851 | checkpoint | Nature of incident
223d57d6-f06c-5618-bac3-7397fe625f59 | tickbox | injury (attach completed WHSE Form 01 Injury report)
25c3980a-c410-5104-953f-7971621f3c09 | tickbox | environmental (pollution)
b750b4d6-91c0-5102-bad2-440810164e63 | tickbox | damage to property/assets/services
972c5433-8314-5c5a-866f-254032fc6c7f | tickbox | incident
fdc46304-1e85-4ebf-9d2d-ef5681b19c14 | section | Names of person(s) involved
73563273-1eb5-40b6-9217-f03d126d5188 | checkpoint | Please attach any relevant photos & documents
dc9be4f0-25ab-5c29-a7d3-718b7015a35d | textbox | Name
0268b2c7-1f7f-5ebe-9d59-1eb11192669a | textbox | Phone Number
cef30ec7-5b3f-5c27-a280-90e1d6b2041a | note | (home, mobile & work)
ee6b7e83-caf8-5efc-aabd-40c33b2321a5 | textbox | Address
0b5f9aee-7f5e-5a6d-b3be-3a3512cf536e | textbox | D.O.B
8ea88fd1-26db-52dd-ab69-4947a9080b0a | textbox | Email
a5979bbc-e71a-5733-92b7-d262e91be22d | textbox | Activity in which the person(s) was engaged at the time:
44ac1026-a3b7-5d83-9ee4-9fd11c9a2834 | textbox | Exact site location where injury/incident occurred:
2c8e0b31-5374-5baf-8ce8-45210709618e | textbox | Type of injury/pollution/damage/ incident:
456a8102-2978-5520-8cab-d4f81e2251cd | textbox | Describe the accident/incident in detail:
fc2d3e5c-66fe-436b-8f46-3273f0495270 | section | Witness to incident (each witness may need to provide an account of what happened
6086bc09-e730-40a5-a055-a9da97fd0682 | checkpoint | Please attach any relevant photos & documents
2fefa896-357a-54da-be1b-45a49ec8936f | textbox | Witness Name
5311898e-1287-51c2-8178-a788c8dfa93e | textbox | Witness Contact
5f3b4e9c-65c1-5024-a7e6-e89eefc5069e | textbox | Witness Name
930665a6-3690-5afd-bf8c-e69d0cef21b8 | textbox | Witness Contact
b675f66f-d0ef-4a09-9af5-1fa3bde0b5a4 | section | Are there any notable/significant factors relevant to the accident/incident?
85ed0557-3c4b-4822-adaa-7f5973c0c3b6 | checkpoint | Please attach any relevant photos & documents
6a291423-d651-5077-9d35-b7d2001c0ed5 | textbox | Details
970675f9-86a1-4c0f-b89d-6c47a76e9673 | section | Arrangements made to store any equipment that believed to have contributed to injury/incident?
fdedade8-3b3a-44c5-a3ea-3228179f441f | checkpoint | Please attach any relevant photos & documents
e4a82348-b5c5-50e0-b616-5d56a5df9050 | textbox | Details
8135f1d4-b61c-4c5e-b1aa-5d16ff65a0a8 | section | Did any third parties (subcontractors, visitors, etc.,) contribute to the incident? If so, how?
f3fcb7bb-70da-4f0c-a871-3c45b34aac56 | checkpoint | Please attach any relevant photos & documents
9e9b1857-8d41-5c5a-a666-77a7953c4134 | textbox | Details
470a88cd-0f6c-4d83-9aa1-c6a3889e0707 | section | Immediate corrective actions taken? (e.g., works ceased, area made safe, barriers erected, etc.,)
ca398a97-721f-4135-ba67-219bed59b5f9 | checkpoint | Please attach any relevant photos & documents
acd5087a-6e90-5250-a92b-3bebf30494ed | textbox | Details
b2c5321c-f37a-4589-bd83-6f0447c5ea7e | section | Future actions taken (e.g., engineering solutions, training, toolbox talk, etc.,)
1993f152-5eb9-4e0f-839f-41c79a8d545c | checkpoint | Please attach any relevant photos & documents
3d06ea25-b08c-5d7c-91d0-ab7866c04b58 | textbox | Details
fa292cb6-7359-430e-8c2a-232fbecef7f0 | section | Review & Sign off
24957181-6e10-4f0d-a8bc-274a14fb385c | checkpoint | Have all actions been completed and reviewed as effective?
f8ee9327-7ec5-4214-87d3-4cb182b521d5 | checkpoint | Have all documents relating to the incident, including corrective action evidence been completed
5d815edc-e82f-4bc5-9c2a-fae93a6789fa | signoff | Signed Off
f590cbd8-2480-42e9-9b95-64c1f6f27c98 | checklist | Project Drawings |  | Project Drawings
fa9d352f-352e-44b4-9789-8eb9b991f3cc | section | Details
9a435d4e-30bd-497f-aeb2-5a9db6dec1fb | checkpoint-no-value | Attach drawings here
320ce78c-2bbc-434a-b7ba-ff55b77a62e1 | checklist | Site Diary Checklist |  | Site Diary Checklist
a04326f6-1ea4-4b3f-ae22-ab06c44c9f65 | section | Details
1aa0c638-3c6b-4338-b15d-51571bf3ce39 | checkpoint-no-value | Comment/notes
4c1fc565-4767-59b8-aae4-3f1551f10f24 | textbox | Add notes
39570879-27c2-4642-a67f-76a9052e90ce | checklist | Sprinkler Control Valves |  | Sprinkler Control Valves
776796f9-0a5b-4231-837f-fd1575308488 | section | Details
5d4a5a85-e67b-45a0-8f64-75f772143331 | checkpoint | Install Sprinkler Control Valves/ Jacking Pump
c36df99a-d5db-4748-90b6-7b8f0e2b7b31 | checkpoint | Test full operation of Control Valves
bdf020ea-402e-4b00-9a00-0db3db863bde | checkpoint | Install Sprinkler Spares box, spare sprinklers & spanner
21e3d510-46b2-4f73-9fc3-05e9b3b5c8fc | checkpoint | Set Jacking Pump pressure switch min 150 kPa above towns main/manifold pressure
37ff69ec-bbb9-4749-ae43-48408afe41d4 | checkpoint | Install Gong/Electric Bell & test operation
225bdda6-274e-4258-8402-0761e82e194a | checkpoint | Check for adequate drainage and test
1453eaa9-a0aa-4ab5-a262-aa56bfe0e9ae | checklist | Sprinkler Fit Off checklist |  | Sprinkler Fit Off checklist
c6d1b50c-f282-4125-9c0c-983f9f73a9c2 | section | Details
fcd8bb88-7f4f-4206-9225-0977fea1abc0 | checkpoint | Fit Off: Check all sprinklers have been fit off
3050a3a1-d86f-4c9f-a8e8-fc3c39d8e278 | checkpoint | Check sprinkler heights pre paint
3c6f074b-af15-41b8-b9ef-b66603471e04 | checkpoint | Fit off Escutcheon plates
a926107e-7556-4520-b213-b84f39075af4 | checkpoint | Air Test: Pressurized air test for a period of 30 mins (if applicable)
67833f5d-1a06-5c60-b9c4-f850569a8ca6 | textbox | Start time:
86a61fb1-6c25-510d-bfae-ff84b509dae5 | textbox | Completion time:
49df82dc-9165-41bf-8b76-d70ca83aee49 | checkpoint | Water Test: Pressure test to 1600Kpa for duration of 2 hours
8659b681-8763-5dfa-b71e-64ea36d3b47a | textbox | Start time:
7db15423-4ad3-581f-8374-dc726c318369 | textbox | Completion time:
c8e25a30-aff8-4e7d-9b30-c7a9d7cc8e27 | checkpoint | PFP Foreman signature
d4387ed1-6fca-4263-8390-17ddb86762de | checklist | Sprinkler Rough In checklist |  | Sprinkler Rough In checklist
e427efbb-1f90-41c3-8d0f-7efea563070a | section | Details
704a57f8-fdad-4acc-aff2-3789dcb40ba3 | checkpoint | Rough In: All Mains, range pipes, clips installed & secured
a71b5bea-6b70-47a5-9eb9-c5de07eca382 | checkpoint | Concealed Space Sprinklers & Flexible droppers Installed
9ea57173-6efa-4343-a97c-9da8ef67af4d | checkpoint | Arm pieces / Under Duct pipework installed and secured
fda9294a-6bea-4e68-8f89-1b1308c00944 | checkpoint | Balcony Sprinklers installed
ab7db484-5102-444d-ac96-ee4f203cfe74 | checkpoint | Car Park Sprinklers Installed
2f8b8665-631f-4e63-9884-6dfa982bb5ac | checkpoint | Car Stackers pipework installed & secured (if applicable)
35be9c49-8fc5-4fbf-b957-1f4a9fc82e33 | checkpoint | Install Remote Test drain pipework
478ad41f-eae3-4909-b523-269b665453a3 | checkpoint | Air Test: Pressurized air test for a period of 30 mins (if applicable)
a5e11ba1-c81a-5fa3-8e89-3a4f6fc1777b | textbox | Start time:
ffd23283-be25-58ec-887d-dc5789b283a8 | textbox | Completion time:
85c46cd5-97bd-4a47-9268-58f35398b6d3 | checkpoint | Water Test: Pressure test to 1600Kpa for duration of 2 hours
09aca2f3-337f-567d-8ab1-241137e57626 | textbox | Start time:
25d0efe1-b3af-5c9d-8afa-8dd35929d3d3 | textbox | Completion time:
4c3b6709-0ced-496c-b22c-39764686c47e | checkpoint | PFP Foreman signature
66c6e790-af0b-404c-a487-80996c0c1684 | checklist | Sub Contractors |  | Sub Contractors
0ff3b8a1-3ac4-42f4-9d37-94ee8d5f4746 | section | Details
4f66d8ce-d6c3-4955-a415-dc6b6416e6ed | checklist | Toolbox Meeting Checklist |  | Toolbox Meeting Checklist
551723f3-a941-429c-8045-7e8ac5db2b4b | section | Attendance
4d2dae10-8b0d-40a9-8ab5-d5b9c85e49c6 | checkpoint | Attendance
c10a9914-b093-5033-8c45-02bcecb50add | tickbox | Ryan Selvarajoo
ccf47ca1-bf6d-5f3b-adc7-f5827171169f | tickbox | Simon Faasalele
02a4f111-7956-5834-8aec-52d8440dca76 | tickbox | Ben Collard
c0d5b6b0-537f-5c40-88c9-b3d13654cabb | tickbox | Justin Dainer
d22cb6b8-9050-5a09-9dcd-ef9b5b588097 | tickbox | Marcus Brownlie
c20f7b19-287d-5daf-bff3-072e437defa6 | tickbox | Salvatore Cunsolo
ce429cd1-eadd-501e-8c8e-f9414edcf0cd | tickbox | Mitchell Smith
a287b668-87e7-5a30-9218-b6f8da0c841d | tickbox | Mouhamed Fattal
b1861a9d-1aec-5ae0-b5df-cf5bb4349437 | tickbox | Alister Smart
be6f3c80-33b5-52c4-a9a7-82d332b67551 | tickbox | Dylan Curtain
752fc64b-203c-5c0f-902d-329f2d02aab3 | tickbox | Matthew Salmon
ac189e20-8b0f-5c54-8247-033730cc5caa | tickbox | Jordan Partridge
8c5fafb9-2350-5287-b731-b67b7307f82e | tickbox | Jordan Buono
5d922b9d-6146-5e08-9a1c-744b4be6d323 | tickbox | Shaun Murphy
514477df-34dd-4c79-aaa9-15ea5c8f23a1 | section | Minutes
a689de5c-1aa7-4036-87ef-c12907513b16 | checkpoint | Actions from last meeting
624f5c69-175d-44e4-84c7-d3f8a56f54c4 | checkpoint | Safety: (including hazards / near misses / controls / site specific)
e086f9da-39b3-4798-8b9c-9b7ad9c8c079 | checkpoint | Plant, tools & Equipment all in good working order?
c9b1fb25-1d47-4295-8dad-8dbe8f7df4ab | checkpoint | PPE-ensure everyone has PPE
f633bd3d-6c3f-491c-9703-1901cfb61cc8 | checkpoint | Housekeeping to be maintained
77fe83a1-1074-4de2-b6a1-9e5b842459fc | checkpoint | Ensure Electrical equipment test and tagged
9bf91ce5-232d-4dee-b09c-34c8ee9be9d5 | section | New Business / Other
ea4d8435-b4e9-41f0-85b7-7dba65bf22ec | checkpoint | Any new comments added below
ba9e1a7c-00d1-4b16-8a80-260bc08f5b44 | section | Meeting Closure
270c586d-57f6-4ec8-8acc-0c269dce5fa1 | checkpoint | Meeting Closed
3f2d2e3a-39d2-5c61-9209-ba77cdfd5d9d | textbox | Meeting Closed time
524b6155-2d7d-5f5d-93ff-6d236ebbe715 | textbox | Minutes taken by (Name)
568cdcc8-217b-55ea-8542-1520d9d9f82e | dropdown | Employee Sign off with drop down link to show all employees | Ryan Selvarajoo, Simon Faasalele, Ben Collard, Justin Dainer, Marcus Brownlie, Salvatore Cunsolo, Mitchell Smith, Mouhamed Fattal, Alister Smart, Dylan Curtain, Matthew Salmon, Jordan Partridge, Jordan Buono, Shaun Murphy
06b6bd02-ced0-42a9-b79c-7d582c912bca | checklist | Undocumented variations |  | Undocumented variations
a642be7b-38bd-433e-abcc-99c65638a7c2 | section | Details