## Folder Structure
QA Folder Structure |  |  |  |  | Checklists
Documentation
Leemark - Site QA
Wet Fire
Infrastructure (Wet and Dry Fire)
|  |  | Tank Installation | Fire Tank 01 | LM-FOR-40-ITR-302.4 Tank Installation
|  |  |  | Fire Tank 02 | LM-FOR-40-ITR-302.4 Tank Installation
|  |  | Fire Panel Installation | FDCIE NODE 1 | LM-FOR-50-ITR-303.1 Fire Panel Installation
|  |  |  | BOWS | LM-FOR-50-ITR-303.1 Fire Panel Installation
|  |  | Fire Pump Installation | Electric Pump | LM-FOR-40-ITR-302.1 Fire Pump Installation
|  |  |  | Diesel Pump | LM-FOR-40-ITR-302.1 Fire Pump Installation
Booster cupboard (FSW-ITR-500)
|  |  | Booster Assembly Installation |  | LM-FOR-40-ITR-302.5 Booster Assembly Installation
|  |  | Sprinkler & Hydrant Hydrostatic Test |  | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test
Pre-Action Sprinkler Conrol Valve Assembly 2 (West)
|  |  | PAV.DH3 | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  | PAV.LV3 | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  | PAV.DH6 | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  | PAV.LV6 | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  | PAV.DH9 | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  | PAV.LV9 | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  | PAV.STO | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  | PAV.LV8 | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  | PAV.LV5 | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  | PAV.H | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  |  | Sprinkler Installation/Fitoff | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff
|  |  |  | Sprinkler & Hydrant Hydrostatic Test | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test
|  |  | PAV.LV2 | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  |  | Sprinkler Installation/Fitoff | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff
|  |  |  | Sprinkler & Hydrant Hydrostatic Test | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test
Pre-Action Sprinkler Conrol Valve Assembly 1 (East)
|  |  | SCV | Sprinkler Control Valve | LM-FOR-30-ITR-301.1 Sprinkler Control Valve
|  |  | PAV.DH2 | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  |  | Sprinkler Installation/Fitoff | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff
|  |  |  | Sprinkler & Hydrant Hydrostatic Test | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test
|  |  | PAV.DH5 | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  | PAV.DH8 | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  | PAV.LV7 | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  | PAV.DH7 | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  | PAV.LV4 | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  | PAV.DH4 | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  | PAV.LV1 | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  |  | Sprinkler Installation/Fitoff | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff
|  |  |  | Sprinkler & Hydrant Hydrostatic Test | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test
|  |  | PAV.DH1 | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  |  | Sprinkler Installation/Fitoff | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff
|  |  |  | Sprinkler & Hydrant Hydrostatic Test | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test
|  |  | PAV.MMR120 | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  | PAV.MMR110 | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  | PAV.MMR220 | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
|  |  | PAV.MMR210 | Pre-Action Valve | ITP/R TEST REPORT PRE-ACTION SYSTEM (V.260521)
Ground Floor (FSW-ITR-100)
|  |  | Hydrant Installation |  | LM-FOR-40-ITR-302.2 Hydrant Installation
|  |  | Circulation (Wet) | Sprinkler Installation/Fitoff | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff
|  |  |  | Sprinkler & Hydrant Hydrostatic Test | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test
|  |  |  | Sprinkler Control Valve | LM-FOR-30-ITR-301.1 Sprinkler Control Valve
|  |  | Office | Sprinkler Installation/Fitoff | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff
|  |  |  | Sprinkler & Hydrant Hydrostatic Test | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test
|  |  |  | Sprinkler Control Valve | LM-FOR-30-ITR-301.1 Sprinkler Control Valve
Level 1 (FSW-ITR-101)
|  |  | Hydrant Installation |  | LM-FOR-40-ITR-302.2 Hydrant Installation
|  |  | Circulation (Wet) | Sprinkler Installation/Fitoff | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff
|  |  |  | Sprinkler & Hydrant Hydrostatic Test | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test
|  |  |  | Sprinkler Control Valve | LM-FOR-30-ITR-301.1 Sprinkler Control Valve
|  |  | Office | Sprinkler Installation/Fitoff | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff
|  |  |  | Sprinkler & Hydrant Hydrostatic Test | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test
|  |  |  | Sprinkler Control Valve | LM-FOR-30-ITR-301.1 Sprinkler Control Valve
Level 2 (FSW-ITR-102)
|  |  | Hydrant Installation |  | LM-FOR-40-ITR-302.2 Hydrant Installation
|  |  | Circulation (Wet) | Sprinkler Installation/Fitoff | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff
|  |  |  | Sprinkler & Hydrant Hydrostatic Test | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test
|  |  |  | Sprinkler Control Valve | LM-FOR-30-ITR-301.1 Sprinkler Control Valve
|  |  | Office | Sprinkler Installation/Fitoff | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff
|  |  |  | Sprinkler & Hydrant Hydrostatic Test | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test
|  |  |  | Sprinkler Control Valve | LM-FOR-30-ITR-301.1 Sprinkler Control Valve
Level 2a (FSW-ITR-102a)
|  |  | Office | Sprinkler Installation/Fitoff | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff
|  |  |  | Sprinkler & Hydrant Hydrostatic Test | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test
|  |  |  | Sprinkler Control Valve | LM-FOR-30-ITR-301.1 Sprinkler Control Valve
Level 2b (FSW-ITR-102b)
|  |  | Office | Sprinkler Installation/Fitoff | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff
|  |  |  | Sprinkler & Hydrant Hydrostatic Test | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test
|  |  |  | Sprinkler Control Valve | LM-FOR-30-ITR-301.1 Sprinkler Control Valve
Level 3 (FSW-ITR-103)
|  |  | Hydrant Installation |  | LM-FOR-40-ITR-302.2 Hydrant Installation
|  |  | Circulation (Wet) | Sprinkler Installation/Fitoff | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff
|  |  |  | Sprinkler & Hydrant Hydrostatic Test | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test
|  |  |  | Sprinkler Control Valve | LM-FOR-30-ITR-301.1 Sprinkler Control Valve
|  |  | Office | Sprinkler Installation/Fitoff | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff
|  |  |  | Sprinkler & Hydrant Hydrostatic Test | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test
|  |  |  | Sprinkler Control Valve | LM-FOR-30-ITR-301.1 Sprinkler Control Valve
Roof (FSW-ITR-105)
|  |  | Office | Sprinkler Installation/Fitoff | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff
|  |  |  | Sprinkler & Hydrant Hydrostatic Test | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test
|  |  |  | Sprinkler Control Valve | LM-FOR-30-ITR-301.1 Sprinkler Control Valve
Dry Fire
MASDS
|  |  | Data Hall 01 | System 01 | LM-FOR-50-ITR- 303.7 Fire Aspirated Smoke Detection
|  |  |  | System 02 | LM-FOR-50-ITR- 303.7 Fire Aspirated Smoke Detection
|  |  |  | System 03 | LM-FOR-50-ITR- 303.7 Fire Aspirated Smoke Detection
|  |  |  | System 04 | LM-FOR-50-ITR- 303.7 Fire Aspirated Smoke Detection
|  |  |  | System 05 | LM-FOR-50-ITR- 303.7 Fire Aspirated Smoke Detection
|  |  |  | System 06 | LM-FOR-50-ITR- 303.7 Fire Aspirated Smoke Detection
|  |  |  | System 07 | LM-FOR-50-ITR- 303.7 Fire Aspirated Smoke Detection
|  |  |  | System 08 | LM-FOR-50-ITR- 303.7 Fire Aspirated Smoke Detection
|  |  | Data Hall 02 | System 09 | LM-FOR-50-ITR- 303.7 Fire Aspirated Smoke Detection
|  |  |  | System 10 | LM-FOR-50-ITR- 303.7 Fire Aspirated Smoke Detection
|  |  |  | System 11 | LM-FOR-50-ITR- 303.7 Fire Aspirated Smoke Detection
|  |  |  | System 12 | LM-FOR-50-ITR- 303.7 Fire Aspirated Smoke Detection
|  |  |  | System 13 | LM-FOR-50-ITR- 303.7 Fire Aspirated Smoke Detection
|  |  |  | System 14 | LM-FOR-50-ITR- 303.7 Fire Aspirated Smoke Detection
|  |  |  | System 15 | LM-FOR-50-ITR- 303.7 Fire Aspirated Smoke Detection
|  |  |  | System 16 | LM-FOR-50-ITR- 303.7 Fire Aspirated Smoke Detection
|  |  | LV SWITCHROOM 1A |  | LM-FOR-50-ITR- 303.7 Fire Aspirated Smoke Detection
|  |  | LV SWITCHROOM 1B |  | LM-FOR-50-ITR- 303.7 Fire Aspirated Smoke Detection
|  |  | LV SWITCHROOM 2A |  | LM-FOR-50-ITR- 303.7 Fire Aspirated Smoke Detection
|  |  | LV SWITCHROOM 2B |  | LM-FOR-50-ITR- 303.7 Fire Aspirated Smoke Detection
|  |  | PAHU L3 |  | LM-FOR-50-ITR- 303.7 Fire Aspirated Smoke Detection
Ground Floor (FSD-ITR-100)
|  |  | Ewis Installation |  | LM-FOR-50-ITR-303.2 Ewis Installation
|  |  | Ewis Installation Fit Off |  | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off
|  |  | Fire Detection Installation |  | LM-FOR-50-ITR-303.4 Fire Detection Installation
|  |  | Fire Detection Fit Off |  | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V160421)
|  |  | SUB FIP'S | SFDCIE NODE 2 | LM-FOR-50-ITR-303.1 Fire Panel Installation
|  |  |  | SFDCIE NODE 3 | LM-FOR-50-ITR-303.1 Fire Panel Installation
|  |  |  | SFDCIE NODE 4 | LM-FOR-50-ITR-303.1 Fire Panel Installation
|  |  | MIMIC Panel |  | LM-FOR-50-ITR-303.1 Fire Panel Installation
Level 1 (FSD-ITR-101)
|  |  | Ewis Installation |  | LM-FOR-50-ITR-303.2 Ewis Installation
|  |  | Ewis Installation Fit Off |  | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off
|  |  | Fire Detection Installation |  | LM-FOR-50-ITR-303.4 Fire Detection Installation
|  |  | Fire Detection Fit Off |  | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V160421)
Level 2 (FSD-ITR-102)
|  |  | Ewis Installation |  | LM-FOR-50-ITR-303.2 Ewis Installation
|  |  | Ewis Installation Fit Off |  | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off
|  |  | Fire Detection Installation |  | LM-FOR-50-ITR-303.4 Fire Detection Installation
|  |  | Fire Detection Fit Off |  | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V160421)
Level 2a (FSD-ITR-102a)
|  |  | Ewis Installation |  | LM-FOR-50-ITR-303.2 Ewis Installation
|  |  | Ewis Installation Fit Off |  | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off
|  |  | Fire Detection Installation |  | LM-FOR-50-ITR-303.4 Fire Detection Installation
|  |  | Fire Detection Fit Off |  | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V160421)
Level 2b (FSD-ITR-102b)
|  |  | Ewis Installation |  | LM-FOR-50-ITR-303.2 Ewis Installation
|  |  | Ewis Installation Fit Off |  | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off
|  |  | Fire Detection Installation |  | LM-FOR-50-ITR-303.4 Fire Detection Installation
|  |  | Fire Detection Fit Off |  | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V160421)
Level 3 (FSD-ITR-103)
|  |  | Ewis Installation |  | LM-FOR-50-ITR-303.2 Ewis Installation
|  |  | Ewis Installation Fit Off |  | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off
|  |  | Fire Detection Installation |  | LM-FOR-50-ITR-303.4 Fire Detection Installation
|  |  | Fire Detection Fit Off |  | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V160421)
Roof (FSD-ITR-104)
|  |  | Ewis Installation |  | LM-FOR-50-ITR-303.2 Ewis Installation
|  |  | Ewis Installation Fit Off |  | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off
|  |  | Fire Detection Installation |  | LM-FOR-50-ITR-303.4 Fire Detection Installation
|  |  | Fire Detection Fit Off |  | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V160421)

## Checklists
type | name | values
checklist | LM-FOR-30-ITR-301 Sprinkler Installation/Fitoff
section | Sprinkler Rough-In
checkpoint | Latest consented drawings checked & referenced
text | Drawing & Revision #
bool | Area clear, tidy and accessible
label | Attach Photos/Comments below if any issues & send report to Builder
checkpoint | Supports spacing & fixing as per AS2118
checkpoint | Pipework installed as per drawings
checkpoint | Concealed space sprinklers installed
checkpoint | All ends blanked off/plugged for testing
checkpoint | Pipes left out
label | Fail=Missing, Pass=Complete
button | Pipes left out - installed | Yes, No
section | Sprinkler Fit-Off
checkpoint | Latest consented drawings checked & referenced
text | Drawing & Revision #
bool | Area clear, tidy and accessible
label | Attach Photos/Comments below if any issues & send report to Builder
checkpoint | Ceiling grid levelled
checkpoint | Sprinklers installed as per drawings
checkpoint | Sprinkler Type & temperature as per drawings
checkpoint | All escutcheon plates installed
checkpoint | Areas not fitted-off
label | Fail=Missing, Pass=Complete
button | Areas not fitted-off - completed | Yes, No
checkpoint | Client Sign Off Sheets Complete
checkpoint | Painting carried out
checkpoint | Pressure Tested (refer ITR 401) - Completed
section | Completion
checkpoint | Works completed to specification/drawings - Attach photos of work below
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Area left clean & tidy | Yes, No
bool | Leemark Sign-Off
bool | Builder Sign-Off
holdpoint | Sign-Off - click to Add signature(s)
checklist | LM-FOR-30-ITR-301.1 Sprinkler Control Valve
section | Installation
checkpoint | Latest consented drawings checked & referenced
text | Drawing & Revision #
bool | Area clear, tidy and accessible
label | Attach Photos/Comments below if any issues & send report to Builder
checkpoint | Supply and Installation pipe works are installed in the correct position and alignment in accordance with the approved drawing/plan
checkpoint | All supports are completely installed, spaced and bolted down box / assembly secured
checkpoint | All roll grooved couplings / flanges are properly tightened
checkpoint | Valve station drain is properly connected to risers drain and building hydraulic drainage
checkpoint | Approved type of Monitored Main Stop Valve is fitted and operational
checkpoint | All specific signage is installed lock shut / lock open including FSV number of M/V’s
checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
checkpoint | Correct type solenoid, flow switch, couplings etc installed
checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
checkpoint | Confirm GFA on solenoid activation/ flow switch/ MV activation
checkpoint | Control Valve is positioned between 1150mm to 1800mm
section | Completion
checkpoint | Works completed to specification/drawings - Attach photos of work below
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Area left clean & tidy | Yes, No
bool | Leemark Sign-Off
bool | Builder Sign-Off
holdpoint | Sign-Off - click to Add signature(s)
checklist | LM-FOR-30-ITR-301.2 Alarm Control Valve
section | Installation
checkpoint | Latest consented drawings checked & referenced
text | Drawing & Revision #
bool | Area clear, tidy and accessible
label | Attach Photos/Comments below if any issues & send report to Builder
checkpoint | Supply and Installation pipe works are installed in the correct position and alignment in accordance with the approved drawing/plan
checkpoint | All supports are completely installed, spaced and bolted down
checkpoint | All roll grooved couplings / flanges are properly tightened
checkpoint | Correct size and specification of Alarm Valve is installed in accordance with the approved drawing/plan
checkpoint | Approved type of Monitored Main Stop Valve is fitted and operational
checkpoint | Correct size of alarm line is installed, adequately supported and alarm gong is properly piped to drain
checkpoint | Correct size of orifice is fitted and piped to drain when system is with retard chamber
checkpoint | Main waste & test valve is fitted and piped to drain
checkpoint | Correct type and model of Direct Brigade Alarm device is fitted
checkpoint | Correct model and range of Pressure Switch is fitted
checkpoint | Correct size and range of supply and installation pressure gauges with shut-off cocks are fitted
checkpoint | All signalling devices (Monitored Stop Valve, DBA, Low Pressure Switch), are wired back to FIP
checkpoint | Control Valve associated pipe works paint touch-up repair is completed
section | Completion
checkpoint | Works completed to specification/drawings - Attach photos of work below
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Area left clean & tidy | Yes, No
bool | Leemark Sign-Off
bool | Builder Sign-Off
holdpoint | Sign-Off - click to Add signature(s)
checklist | LM-FOR-33-ITR-401 Sprinkler & Hydrant hydrostatic test
section | Guidelines
checkpoint | Guidelines understood - Pass once read
label | Guidelines: Fire Sprinkler Systems – 1400kPa or 400kPa above the maximum static pressure for a duration of 2 hours (Check notes on Construction Drawing for nominated test pressure)
label | Fire Hydrant Systems (Low Rise) – 1700kPa or 15 times the design pressure for a duration of 2 hours (Check notes on Construction Drawing for nominated test pressure)
label | Fire Hydrant Systems (High Rise) – 1050kPa at the highest hydrant in the pressure stage being tested If pressure reading is being taken at the booster, determine the height difference in metres between the top hydrant and the booster and add 10kPa per metre of static pressure to this figure with a minimum test pressure of 1700kPa If in doubt please seek clarification from the Construction Supervisor or the Design Manager
section | Rough In Only OR Rough In & Fit Off Together
checkpoint | First Sighting - Pass once entered
text | Date
text | Time
text | Pressure
button | Photo(s) taken | Yes, No
button | Leemark Sign-Off - Attach below | Pass, Fail
button | Builder Sign-Off - Attach below | Pass, Fail, N/A
checkpoint | Second Sighting - Pass once entered
text | Date
text | Time
text | Pressure
button | Photo(s) taken | Yes, No
button | Leemark Sign-Off - Attach below | Pass, Fail
button | Builder Sign-Off - Attach below | Pass, Fail, N/A
section | Fit Off (if required ie if not covered by the above section)
checkpoint | Subsequent Sighting - Pass once entered
text | Date
text | Time
text | Pressure
button | Photo(s) taken | Yes, No
button | Leemark Sign-Off - Attach below | Pass, Fail
button | Builder Sign-Off - Attach below | Pass, Fail, N/A
section | Completion
checkpoint | Works completed to specification/drawings - Attach photos of work below
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Area left clean & tidy | Yes, No
bool | Leemark Sign-Off
bool | Builder Sign-Off
holdpoint | Sign-Off - click to Add signature(s)
checklist | LM-FOR-40-ITR-302.1 Fire Pump Installation
section | Installation
checkpoint | Latest consented drawings checked & referenced
text | Drawing & Revision #
bool | Area clear, tidy and accessible
label | Attach Photos/Comments below if any issues & send report to Builder
checkpoint | Pump installation arrangement including suction and discharge pipe works are in accordance with the approved drawing/plan
checkpoint | Pump clearance is 1000 mm on all four sides and 600 mm between pumps
checkpoint | Concrete plinth/foundation height is minimum 150 mm from FFL and 150 mm wider on all four sides of pump base
checkpoint | Pump base is sitting squarely and bolted down Vibration mounts are properly anchored on plinth or inertia plinth
checkpoint | Pump suction and discharge pipework are completely installed and connected Supports are adequately provided
checkpoint | Control panels installed and bolted down, MFB have clear access around pump controller 1000mm Arc
checkpoint | Suction isolation valve installed is OS & Y type
checkpoint | Non-return valve is installed and located upstream of the isolation valve in pump discharge line
checkpoint | Pump circulation-relief valve for electric driven pump is installed and piped to drain or tank return line
checkpoint | Heat exchanger cooling water harness for diesel driven pump is installed and piped to drain or tank return line
checkpoint | Pressure gauge with gauge cock is installed min 2Ø downstream of discharge flange or reducer
checkpoint | Pressure reductions installed on manifold x2 for each stage with M/V’s and Annubar for each stage
checkpoint | Exhaust connected to pump and installed to approved discharge location
checkpoint | Full tanks have been filled with Diesel; Electric Pumps AND Controls ready for energisation
section | Completion
checkpoint | Works completed to specification/drawings - Attach photos of work below
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Area left clean & tidy | Yes, No
bool | Leemark Sign-Off
bool | Builder Sign-Off
holdpoint | Sign-Off - click to Add signature(s)
checklist | LM-FOR-40-ITR-302.2 Hydrant Installation
section | Installation
checkpoint | Latest consented drawings checked & referenced
text | Drawing & Revision #
bool | Area clear, tidy and accessible
label | Attach Photos/Comments below if any issues & send report to Builder
text | Hydrant No.
checkpoint | Hydrant supply pipe works completely installed of correct size, position, elevation, alignment and adequately supported in accordance with approved drawing/plan
checkpoint | Hydrostatic pressure testing of installed supply pipe works completed and accepted
checkpoint | Hydrant valves and associated pipes and fittings used are in accordance with the approved specifications and applicable codes/standards
checkpoint | Fire Hydrant and associated fire water main isolation valves locations are in accordance with the approved drawing/plan
checkpoint | Hydrants stand pipe is adequately supported and bolted down. Concrete surround block provided for external hydrant
checkpoint | Hydrant valve is between 750 to 1200 mm from finish floor/grade level
checkpoint | Valve outlet is facing away from the wall and not more than 35O below its horizontal axis. Minimum 300 mm clearance around the valve outlet
checkpoint | Minimum 1000 mm clear space in front of valve outlet is provided
checkpoint | Valve handwheel clearance is minimum 100 mm clear of any obstruction at fully open
section | Completion
checkpoint | Works completed to specification/drawings - Attach photos of work below
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Area left clean & tidy | Yes, No
bool | Leemark Sign-Off
bool | Builder Sign-Off
holdpoint | Sign-Off - click to Add signature(s)
checklist | LM-FOR-40-ITR-302.3 Hose Reel Installation
section | Installation
checkpoint | Latest consented drawings checked & referenced
text | Drawing & Revision #
bool | Area clear, tidy and accessible
label | Attach Photos/Comments below if any issues & send report to Builder
text | Hose Reel No.
checkpoint | Hose Reel supply pipe works completely installed of correct size, position, elevation, alignment and adequately supported in accordance with approved drawing/plans
checkpoint | Hydrostatic pressure testing of installed pipe works completed and accepted
checkpoint | Hose Reel and associated valves, pipes and fitting used are in accordance with the approved specifications and applicable codes/standards
checkpoint | Hose Reel located along normal path of travel to nearest exit and readily accessible
checkpoint | Verify and confirm hose length to be 36-metres or 40-meters
checkpoint | Hose reel spindle is 1400 mm minimum to 2400 mm maximum above floor level. Stop valve is 1000 + 100 mm above floor level
checkpoint | Minimum radial clearance of 100 mm between the reel rim and cabinet/cavity to the sides, above and below
checkpoint | Minimum 100 mm clearance around the stop valve handwheel/handle
checkpoint | Any defects found on the hose reel assembly have been corrected
section | Completion
checkpoint | Works completed to specification/drawings - Attach photos of work below
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Area left clean & tidy | Yes, No
bool | Leemark Sign-Off
bool | Builder Sign-Off
holdpoint | Sign-Off - click to Add signature(s)
checklist | LM-FOR-40-ITR-302.4 Tank Installation
section | Installation
checkpoint | Latest consented drawings checked & referenced
text | Drawing & Revision #
bool | Area clear, tidy and accessible
label | Attach Photos/Comments below if any issues & send report to Builder
checkpoint | Tank installation/construction is completed including associated pipe works in accordance with the approved drawing/plan
checkpoint | Tank is free from dents, buckling, cracks, and internal is clean and free of any debris and construction materials
checkpoint | Tank internal liner (if provided) is complete and properly bonded to tank wall/shell
checkpoint | Tank quick infill line including associated infill valve and isolation valve installed and adequately supported
checkpoint | Tank suction isolation valve is fitted in the correct position and operational in accordance with the approved drawing/plan
checkpoint | Tank suction vortex inhibitor is fitted in the correct position and elevation in accordance with the approved drawing/plan
checkpoint | Tank overflow is fitted in the correct position, elevation and properly piped to drain Adequate drain available
checkpoint | Tank drain/sludge isolation valve is fitted and blank off
checkpoint | Tank external water level indicator is fitted and operational
checkpoint | Tank internal and external access ladders are fitted & secured
checkpoint | Tank access hatch is fitted and provided with lockable cover
checkpoint | Ball float for infill pilot line is fixed tightly, close to the manhole and away from the discharge path of tank infill
checkpoint | Tank is located with minimum of 600 mm clearance around tank perimeter and roof line
section | Completion
checkpoint | Works completed to specification/drawings - Attach photos of work below
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Area left clean & tidy | Yes, No
bool | Leemark Sign-Off
bool | Builder Sign-Off
holdpoint | Sign-Off - click to Add signature(s)
checklist | LM-FOR-40-ITR-302.5 Booster Assembly
section | Installation
checkpoint | Latest consented drawings checked & referenced
text | Drawing & Revision #
bool | Area clear, tidy and accessible
label | Attach Photos/Comments below if any issues & send report to Builder
checkpoint | All pipework are installed in the correct position and alignment in accordance with the approved drawing/plan
checkpoint | All pipework have been pressure tested and accepted in accordance to approved pressure testing procedure
checkpoint | Fire Brigade Booster is located within sight of the main entrance to the building
checkpoint | Concrete plinth provided for the booster location and hard stand for fire brigade pumping appliance
checkpoint | Feed Hydrant is located within 8 metres from fire brigade appliance hard stand
checkpoint | Fire water storage tank suction point (Storz) is located within 4 metres from fire brigade appliance hard stand
checkpoint | Fire water storage tank suction point (Storz) is located within 10 metres from fire brigade booster inlet connection
checkpoint | Centre distance between feed hydrant and booster inlet connection is 450 mm minimum and 5 m maximum
checkpoint | The height of Feed Hydrant Outlet and Booster Inlet Connection is minimum 750 mm and maximum 1200 mm from FFL
checkpoint | Valves face minimum 150-mm from door and valve handles are 100-mm from cabinet sides
checkpoint | The number of feed hydrant outlet installed is equal to number of fire brigade booster assembly inlets
checkpoint | The required number of fire brigade booster inlets installed is suitable for the system requirement or minimum of 2 inlets
checkpoint | Full flow non-return valve of correct size is installed in the proper location
checkpoint | Approved type of cabinet enclosure is installed as required
section | Completion
checkpoint | Works completed to specification/drawings - Attach photos of work below
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Area left clean & tidy | Yes, No
bool | Leemark Sign-Off
bool | Builder Sign-Off
holdpoint | Sign-Off - click to Add signature(s)
checklist | LM-FOR-50-ITR-303.1 Fire Panel Installation
section | Fire Indicator Panel
checkpoint | Latest consented drawings checked & referenced
text | Drawing & Revision #
bool | Area clear, tidy and accessible
label | Attach Photos/Comments below if any issues & send report to Builder
checkpoint | Are visual indicators and controls not less than 750 mm from the floor
checkpoint | Are visual indicators and controls not more than 1850 mm from the floor
checkpoint | Connected to Brigade - Is the fire indicator panel clearly visible and readily accessible within the designated building entry point or the fire control room
checkpoint | Not Connected to Brigade - Is the fire indicator panel in a secure location and clearly visible and readily accessible to authorized personnel
section | Accessibility
checkpoint | Is the fire indicator panel obscured by a door (if No, continue to CLEARANCE)
checkpoint | Is the door marked in a contrasting colour to the general colour scheme with the words “FIRE PANEL” in letters not less than 50mm high
checkpoint | Is the door absent of locks
checkpoint | Where the door reduces the CIE sounder sound level below the CIE requirement, means are provided to give the required sound level outside the covering door
checkpoint | A minimum clearance is maintained from the enclosure as shown
section | Power sources
checkpoint | Is the battery enclosure located such that the batteries are readily accessible for inspection
checkpoint | Are the connecting leads to the battery clearly labelled to reduce the possibility of reverse connections to the battery
checkpoint | The battery is not be tapped for intermediate voltages
checkpoint | All connections are made using suitable connectors
section | Sub-Indicator Panels
checkpoint | The SIP shall only serve areas on one level of a building unless - Pass once below considered
button | (a) The SIP serves the entire building | Yes, No, N/A
button | (b) All zones connected to the SIP are readily accessible without leaving the area served by the SIP; or | Yes, No, N/A
button | (c) The location of each zone in alarm at the SIP can be identified at the designated building entry point | Yes, No, N/A
button | Where the SIP serves the entire building, it shall be installed in accordance with the requirements for an FIP | Yes, No, N/A
button | If the SIP serves a specific area, is it located at the main point of entry into that area | Yes, No, N/A
section | Wiring
checkpoint | The extra low voltage wiring of the fire detection and alarm system is be kept separate and distinct from all other systems
checkpoint | The extra low voltage wiring of the fire detection and alarm system is installed in accordance with the requirements of AS/ACIF S009
checkpoint | Other wiring is installed in accordance with the electrical safety requirements of AS/NZS
checkpoint | Externally energized circuits at voltages in excess of extra low voltage, except the power source for CIE, do not enter any CIE enclosure
section | Completion
checkpoint | Works completed to specification/drawings - Attach photos of work below
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Area left clean & tidy | Yes, No
bool | Leemark Sign-Off
bool | Builder Sign-Off
holdpoint | Sign-Off - click to Add signature(s)
checklist | LM-FOR-50-ITR-303.2 Ewis Installation
section | Cabling
checkpoint | Latest consented drawings checked & referenced
text | Drawing & Revision #
bool | Area clear, tidy and accessible
label | Attach Photos/Comments below if any issues & send report to Builder
checkpoint | Have all cable supports been installed in the correct position with no obstructions
checkpoint | Have all cables been cable tied to soffit / catenary wire with no sagging or obstructions
checkpoint | Have all cables been installed for speakers and horns
checkpoint | Have all cables been installed for warden intercom points
checkpoint | Have all cables been installed for emergency call points
checkpoint | Have all cables been installed for strobes
checkpoint | Have all cables been installed for background music inputs
checkpoint | Have all cables been installed for microphone inputs
checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers)
checkpoint | Have all cables been installed in the correct position for devices
checkpoint | Have all cables been joined through for testing purposes or fitted with end of line devices
section | Cable Feeds
checkpoint | Have all cable supports been installed in the correct position with no obstructions
checkpoint | Have all cable feeds been installed in the correct position
checkpoint | Have all cables been tied to cable tray with steel ties with no sagging or obstructions
checkpoint | Have all cable trays been installed correctly and secured including joiners and bends
checkpoint | Have the modified cable trays been re-galvanized
section | Visual Check
checkpoint | Check that no other services are run with or attached to occupant/emergency warning cables
checkpoint | Check that no cables have been damaged
checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
checkpoint | Have all cable runs, cable trays and penetrations been mark on “As Constructed Drawings” for handover
checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
checkpoint | Has photographic evidence been taken and recorded for all penetrations
section | Completion
checkpoint | Works completed to specification/drawings - Attach photos of work below
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Area left clean & tidy | Yes, No
bool | Leemark Sign-Off
bool | Builder Sign-Off
holdpoint | Sign-Off - click to Add signature(s)
checklist | LM-FOR-50-ITR-303.3 Ewis Installation Fit Off
section | EWIS Fit-Off
checkpoint | Latest consented drawings checked & referenced
text | Drawing & Revision #
bool | Area clear, tidy and accessible
label | Attach Photos/Comments below if any issues & send report to Builder
checkpoint | Have all devices been installed in the correct position with no obstructions
checkpoint | Have all speakers / horns been installed in the correct location
checkpoint | Have all warden intercom points been installed in the correct location
checkpoint | Have all emergency call points been installed in the correct location
checkpoint | Have all strobes been installed in the correct location
checkpoint | Have all background music points been installed in the correct location
checkpoint | Have all microphone points been installed in the correct location
checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers) – Double check to make sure no other trades have been in after warning system works
checkpoint | Have all cables and conduits been installed in the correct position for devices
checkpoint | Have all devices been terminated for testing purposes
section | Cable Feeds
checkpoint | Have all cable supports been connected to the first device
checkpoint | Have all end of lines been fitted and measured
checkpoint | Have cables feeds been connected at the panel
section | Visual Check
checkpoint | Check that no other services are run with or attached to occupant/emergency warning cables or devices
checkpoint | Check that no cables or devices have been damaged
checkpoint | Check that all final device locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
checkpoint | Have devices and readings been noted on “As Constructed Drawings” for handover
checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
checkpoint | Has photographic evidence been taken and recorded for all penetrations
section | Completion
checkpoint | Works completed to specification/drawings - Attach photos of work below
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Area left clean & tidy | Yes, No
bool | Leemark Sign-Off
bool | Builder Sign-Off
holdpoint | Sign-Off - click to Add signature(s)
checklist | LM-FOR-50-ITR-303.4 Fire Detection Installation
section | Cabling
checkpoint | Latest consented drawings checked & referenced
text | Drawing & Revision #
bool | Area clear, tidy and accessible
label | Attach Photos/Comments below if any issues & send report to Builder
checkpoint | Have all cable supports been installed in the correct position with no obstructions
checkpoint | Have all cables been cable tied to soffit / catenary wire with no sagging or obstructions
checkpoint | Have all cables been installed for detectors
checkpoint | Have all cables been installed for sprinkler valve sets
checkpoint | Have all cables been installed for magnetic door holders
checkpoint | Have all cables been installed for security fire trips
checkpoint | Have all cables been installed for mechanical fire trips
checkpoint | Have all cables been installed for AS 1668 Fan Controls
checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers)
checkpoint | Have all cables been installed in the correct position for devices
checkpoint | Have all cables been joined through for testing purposes
section | Cable Feeds
checkpoint | Have all cable supports been installed in the correct position with no obstructions
checkpoint | Have all cable feeds been installed in the correct position
checkpoint | Have all cables been tied to cable tray with steel ties with no sagging or obstructions
checkpoint | Have all cable trays been installed correctly and secured including joiners and bends
checkpoint | Have the modified cable trays been re-galvanized
section | Visual Check
checkpoint | Check that no other services are run with or attached to fire detection cables
checkpoint | Check that no cables have been damaged
checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
checkpoint | Have all cable runs, cable trays and penetrations been mark on “As Constructed Drawings” for handover
checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
checkpoint | Has photographic evidence been taken and recorded for all penetrations?
section | Completion
checkpoint | Works completed to specification/drawings - Attach photos of work below
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Area left clean & tidy | Yes, No
bool | Leemark Sign-Off
bool | Builder Sign-Off
holdpoint | Sign-Off - click to Add signature(s)
checklist | LM-FOR-50-ITR- 303.5 Fire Detection Fit Off (V160421)
section | Fit-Off
checkpoint | Latest consented drawings checked & referenced
text | Drawing & Revision #
bool | Area clear, tidy and accessible
label | Attach Photos/Comments below if any issues & send report to Builder
checkpoint | Have all devices been installed in the correct position with no obstructions
checkpoint | Have all detectors been installed in the correct position and addressed
checkpoint | Have all input/output modules been installed in the correct position and addressed, with all enclosures sealed
checkpoint | Have all magnetic door holders been installed correctly
checkpoint | Have all input/output devices been installed and addressed for security fire trips
checkpoint | Have all input/output devices been installed and addressed for mechanical fire trips
checkpoint | Have all input/output devices been installed and addressed for AS 1668 Fan Controls
checkpoint | Have the ELV and LV segregation rules been applied as per AS/CAS 009 (including 90 degrees crossovers) – Double check to make sure no other trades have been in after fire works
checkpoint | Have all cables and conduits been installed in the correct position for devices
checkpoint | Have all devices been terminated for testing purposes
section | Cable Feeds
checkpoint | Have all cable feeds been connected to the first device
checkpoint | Have all cable feeds been connected to the last device
checkpoint | Have cable feeds been connected at the panel
section | Visual Check
checkpoint | Check that no other services are run with or attached to fire detection cables
checkpoint | Check that no cables have been damaged
checkpoint | Check that all final cable locations are correct and match up with the “For Construction Drawings” and “Reflected Ceiling Plans”
checkpoint | Check that all address tags and labels are clear and readable
checkpoint | Have devices and address been noted on “As Constructed Drawings” for handover
checkpoint | Have all stickers been installed to fire rated walls and smoke walls for penetrations
checkpoint | Has photographic evidence been taken and recorded for all penetrations?
section | Completion
checkpoint | Works completed to specification/drawings - Attach photos of work below
label | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
button | Area left clean & tidy | Yes, No
bool | Leemark Sign-Off
bool | Builder Sign-Off
holdpoint | Sign-Off - click to Add signature(s)
checklist | Document Attachment ITP (V.220421)
checkpoint | Documents/Drawings attached for reference - Pass once attached