## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned | f2188e4f-c07a-4047-828a-ba12510caad3 |  | checklist | AES-NZ1005-STE-ITP-PMT-0025 - Combined Services Fire Hydrostatic Pressure Test |  |  |  |  | Yes | AES-NZ1005-STE-ITP-PMT-0025 - Combined Services Fire Hydrostatic Pressure Test | 04cb4854-68c5-41cc-b95a-c903ee335c35
checkpoint-group | da8f9c39-e6da-4348-bc63-aa4dc685d31e |  | section | MATERIAL COMPLIANCE
checkpoint-status | f55809d8-15f5-4295-932c-5b1cdb18d127 |  | checkpoint | RDM & Consent Approval
label | bab2db0e-7948-589e-9b92-8a802c084e72 |  | note | CRITERIA - RDM approval tracker Consent approval tracker
holdpoint | c63f4f35-93b8-4024-a1a3-2bd2e75ac7ea |  | signoff | CPB Hold Point Signature
checkpoint-status | 37d40bf3-e752-4082-aa0f-32ca2dcd8dcb |  | checkpoint | General
label | e27ffffb-b691-5b73-ad5c-d794df089099 |  | note | CRITERIA - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
label | f9fbaa03-01c9-53f3-a4b1-59ab7d558a0a |  | note | • Specifications & QA Documents Approved
label | 65eba237-7609-57c8-a065-9b823317c0b1 |  | note | • Drawings are confirmed
label | 96b594b7-9fea-5ed7-b6e6-05806dcc0c51 |  | note | • Equipment fit for purpose
holdpoint | 360751a5-270c-44e7-8207-fcb57fbb95f3 |  | signoff | CPB Hold Point Signature
checkpoint-group | 8b3ee7ee-4eaf-49fb-8637-aaba3d3068cd |  | section | CONNECT PRESSURE PUMP TO DCW RING MAINS
checkpoint-status | 0af44a30-b648-4ffe-b401-fce8e07ce46f |  | checkpoint | Accept delivery of pump to site
label | a0764a28-5db5-5877-944f-89bd1ac9453e |  | note | CRITERIA - 1. Check pump is rated for pressure test
label | 09303136-d91e-5acd-808c-787f6a6fbeb8 |  | note | 2. Check all supplied attachments are correct and in good order
label | e9a00b57-87dd-5603-b9a7-08a12cfb1745 |  | note | 3. Check fluid levels & fill as necessary
checkpoint-status | 4d4db551-a0ca-4b4b-ae0b-7b1b592cf08c |  | checkpoint | Connect pump to Fire ring mains
label | 965fc0fe-1856-523c-ab9c-e9ccc273196b |  | note | CRITERIA - Confirm connections are safe and correct
checkpoint-status | d70003eb-77b5-4ee0-a7c6-be9d9b709353 |  | checkpoint | Connect calibrated gauges for pressure test
label | f40babb5-fe8a-5288-b1a7-811481130b99 |  | note | CRITERIA - Confirm position is correct, gauge is in good order for test & calibrated
checkpoint-group | f8de9ba2-0c34-4983-a689-275963f018fe |  | section | HYDROSTATIC TEST
checkpoint-status | ba2e1b19-a2ca-4f6b-9b09-7ec0c471630e |  | checkpoint | Fill Fire ring mains with domestic water
label | c780e7e8-627b-58b3-8fb4-f15e01e3aef8 |  | note | CRITERIA - Completely fill closed loop system with water releasing all air from the Valves at each Building
checkpoint-status | 4c418fcd-e23f-495a-a055-34d9d1c98f7b |  | checkpoint | Gradually increase system pressure to 15.5 Bar
label | 90eacdea-6b58-5bba-a99d-be91352a377f |  | note | CRITERIA - Slowly raise system pressure to 15.5 Bar
label | 1abd5484-6f42-59c8-a890-aa69e24ea847 |  | note | • Checking for any signs of leaks or pressure drops
checkpoint-status | 8fd10a0d-7b25-4a11-8b12-8af46908769a |  | checkpoint | Stabilize 15.5 Bar pressure (START WITNESSED)
label | 4de5437a-f431-587a-a4f7-3947fefca462 |  | note | CRITERIA - Record START time & photograph gauge
label | a92cfe97-8ea0-5078-adb7-6a268738680d |  | note | • All relevant parties to witness starting pressure of 15.5 Bar
holdpoint | 978321e4-be43-468a-a5dd-90ce3d2f8748 |  | signoff | CPB Hold Point Signature
checkpoint-no-status | 15ac3046-dc50-4ab3-9d60-f733a173734d |  | checkpoint | Stabilize 15.5 Bar pressure (START WITNESSED) - IR Hold Point Signature
holdpoint | ffaa05cc-1d31-44a7-9e6a-522cff2b1bfe |  | signoff | IR Hold Point Signature
checkpoint-status | a2929c1a-a053-4106-9a3c-038724649a54 |  | checkpoint | Hold 15.5 Bar pressure for 4Hours (END WITNESSED)
label | 950b7423-d9a6-5a48-a67e-a7658c2939a1 |  | note | CRITERIA - Record FINISH time & photograph gauge
label | 1d289ede-8398-5d10-a720-3dc7ef6c803c |  | note | • All relevant parties to witness pressure of 15.5 Bar
holdpoint | 98e31712-b203-4bd4-aec0-59aae9b4652a |  | signoff | CPB Hold Point Signature
checkpoint-no-status | 2db8b97b-fb7d-49ba-9529-9f8ee25a815a |  | checkpoint | Hold 15.5 Bar pressure for 4Hours (END WITNESSED) - IR Hold Point Signature
holdpoint | 75e6b050-70b4-4f45-8ea5-33663e1270b1 |  | signoff | IR Hold Point Signature
checkpoint-status | ab2ad6ee-b325-44d9-860e-aa80d648fcb6 |  | checkpoint | Pressure released or reduced for next test
label | 17b2b1e0-12b9-51ce-9413-dcd5b97f74bd |  | note | CRITERIA - Supervisor to ensure energy (pressure) is only stored while under test
checkpoint-status | 29c5e31e-d1a5-4321-8cba-32fa13184c2c |  | checkpoint | Discharge pressure leave system in a safe state
label | 3e61985c-34ba-5529-bc23-d1fd2211bc94 |  | note | CRITERIA - Discharge system pressure, ensure area is left in a safe state meeting site requirement
checkpoint-group | 1d85ce58-f3fa-4d58-8b6e-eade7bcab891 |  | section | COMPLETION RECORDS
checkpoint-status | 41870a7a-6ccf-4754-baab-9eb02673706b |  | checkpoint | Testing Results
label | f9970583-a837-5b5d-aa74-ea7fe7bdedee |  | note | CRITERIA - All pipework pressure test reports shall be provided
holdpoint | bc286a9a-c192-4bb2-ae88-c23803b26297 |  | signoff | CPB Hold Point Signature
checkpoint-no-status | d7714737-4ca7-414d-947f-a4743f248c9b |  | checkpoint | Testing Results - IR Hold Point Signature
holdpoint | 8d0862e7-276b-4ae4-af99-9469721e255c |  | signoff | IR Hold Point Signature
checklist-flat | fc4c08b1-af97-4fae-926a-57bb2455500d |  | checklist | RBG Combined Services HDPE Potable Water Pipework Installation V2 |  |  |  |  | Yes | RBG Combined Services HDPE Potable Water Pipework Installation V2 | 0568c749-af0f-4547-9684-73ab891bf437
checkpoint-status | 10d55dd1-243f-4f24-9d26-effabcac4faa |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | baedbd5b-1415-4016-bb93-9dcb5cb7f21b |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | 9b6966b3-ce32-45b2-b43a-01bc0da9371e |  | checkpoint | Inspect trench depth, width and pipe alignment
label | 72d345b4-c6e6-598b-a90a-98710f130f7c |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | da128105-03fd-5ceb-ba4b-abc3a36571f7 |  | note | QA documents to be provided prior to installing pipework in trenches . CPB to provide to AE Smith.
checkpoint-status | 51ee531c-7656-41b6-8e28-63f3247f0b9c |  | checkpoint | Number of pipes and dimensions of pipes shall be shown on the drawing
checkpoint-status | e3dcc19a-50d1-470d-8191-2185ad92fbc1 |  | checkpoint | Location of pipe
label | edd8a7b6-1931-5594-b340-a720bf7ab179 |  | note | Shall be as shown on the drawings
label | 46150486-e848-5f26-958a-eb85e5b277b4 |  | note | Ensure correct clearances between water service and other underground services.
checkpoint-status | 0b94a859-2989-4a83-afaa-0a26813012a8 |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
holdpoint | 205ba956-b95e-494a-a279-2ae0aa302ebe |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 84701b10-3cfc-4f42-9f8c-b8aa14cc00f5 |  | checkpoint | Jointing of pipes only via. Rotatable steel flanges, EF Coupling and Butt Welding.
checkpoint-status | 811b93a0-4752-4dd6-8121-b2fedf593963 |  | checkpoint | Electrofusion Welding Checklist completed for each joint?
checkpoint-status | 6d78e9de-0f58-4987-be78-98f62a8ce947 |  | checkpoint | Butt welding checklist completed for each joint ?
checkpoint-status | eaad8f09-17f7-4681-ae77-3ddd3a636f72 |  | checkpoint | Install valves, tees and bends
label | 5ff09d41-48a3-50e6-bc92-43c9450cf876 |  | note | Install all connections as per construction drawings
label | 17853516-b1c9-5fe4-8b6c-777b7cdd3676 |  | note | All valve 100mm and above will require a 1050mm manhole.
checkpoint-status | bbdb1a7a-a5d3-4b8e-8fde-84d494efdd53 |  | checkpoint | Installation of ductile iron bends
label | 367d1efb-e21c-5d7b-9a09-5a0836da7cad |  | note | Inspect pressure class on fittings and ensure correct pressure rating prior to installation.
label | caeab218-c37e-5ed4-8858-9af405c68cb0 |  | note | Ensure correct gaskets are installed.
label | 290bcb62-208b-51d3-b175-cbfb92e5c1ec |  | note | Washers installed on both sides of the flange.
label | 47f627c9-5fd7-5d16-935c-636f875d3cc5 |  | note | Bolts to be tightened in correct tightening sequence.
checkpoint-status | 2c745297-939e-4543-be67-fd12494a1b79 |  | checkpoint | Install Thrust and Anchor Blocks
label | bc99addc-af6e-52c4-9c72-c67970241d6a |  | note | Minimum dimensions as per IFC drawings.
label | 4a49130b-6af9-5945-931e-e34db297e473 |  | note | A protective Denso or black coating membrane is to be installed around the pipe and the concrete anchor/thrust blocks to prevent abrasive damage.
holdpoint | 7c07ef8a-b437-4ce3-96d3-261ec29618cf |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | b7fa29bb-fde0-41cc-a331-f3c351040d44 |  | checkpoint | Completed Construction Pressure Testing with Air
checkpoint-status | c386e340-f90b-45ce-aa9a-509f7e5e2e36 |  | checkpoint | Pre-Pipework Pressure Testing Inspection
label | 8d4cd252-08dc-513b-a8dd-e497bc2cc6cf |  | note | Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | 05b76734-436a-5c52-a541-b99a206fa01f |  | note | Ensure each test length is capped and ball valve installed.
label | 58ec742c-626d-51c4-9622-15ae74f5b9a9 |  | note | Ensure all valves in the system are in the correct position and tagged �DO NOT OPEN� or �DO NOT CLOSE�
label | 7ad70c76-4c7f-5481-8e46-a85c104b4eb9 |  | note | All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing.
checkpoint-status | ffd447f0-5263-4a02-9eee-3be9d9061ecd |  | checkpoint | Introduction of Air to 300 kPa
label | d10d34f4-e78d-5dd6-ae09-c507d3d284dc |  | note | Gradually introduce air into the system to a pressure of 300 kPa and hold for 1 hour.
label | 6f6e953e-8b6c-500b-ade2-0ba077e56ea2 |  | note | Monitor for any drop-in pressure.
label | a1799260-2f92-528c-8993-51666703ad82 |  | note | If a leak is identified discharge the air prior to rectifying any leaks.
checkpoint-status | aeada704-d0ad-4aa7-a49d-d734ffd54959 |  | checkpoint | Increasing Test Pressure
label | 4752b001-8afc-59a2-bb57-4b784b63e52a |  | note | If no leaks are identified Increase pressure by 10% increments until test pressure is achieved.
checkpoint-status | 7d7517a8-15c8-48b4-af1f-5aac0a4a7190 |  | checkpoint | Pipework Pressure Test Report Completed
checkpoint-status | e1a6513d-df0c-4a82-a991-976fea325067 |  | checkpoint | Installation of Trace Wire
label | 2b159c13-4377-5d31-80d6-deb67556cb34 |  | note | Install Trace Wire and ensure tracer wire is continuous between valves and any excess coiled in valve box.
label | 95113112-30d8-5941-acf6-fecde999b91e |  | note | Test Trace Wire following installation.
holdpoint | 8d664468-28ef-4e66-babb-fa7c5872ff9d |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | c3db849d-9204-42d8-8e63-336ed369aa84 |  | checkpoint | As-Builts Completed.
holdpoint | 006d0d48-4c68-4bf5-ba79-d5ba556fda1c |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 84f1edd6-92d1-4095-b761-3c20f7184d5e |  | checklist | Combined Services HDPE Natural Gas Installation |  |  |  |  | Yes | Combined Services HDPE Natural Gas Installation | 0945f706-e66f-4b50-8d17-9a9730a1c2a3
checkpoint-status | 0a3175aa-fe41-4b3d-90b1-f8f0094544c9 |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | a8cc2176-8380-4925-bd8a-218cd6b96d04 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | c2633378-7b57-4d29-842e-850f3303719b |  | checkpoint | Confirm trench depth, width and pipe alignment.
label | 1362d58b-790a-5bf7-ae6c-46c24049fcec |  | note | QA documents to be received from sub-contractor prior to installation of conduit in trench.
checkpoint-status | e6094e81-94ca-4d9d-950c-39e28deaa4bc |  | checkpoint | Number of pipe dimensions shown on the drawings.
checkpoint-status | 8494e1a3-1f51-4714-ba4f-d8880c45c0f3 |  | checkpoint | Location of pipes shall be shown on the drawings.
checkpoint-status | d060a17a-9506-475f-9663-83bcb0f89d02 |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | b842a126-9259-4258-b424-da306dfbbf3d |  | checkpoint | Installation of Valves
label | e6b327b2-1ab3-50da-8e5a-1f74e07840a1 |  | note | Valves Installed as per approved drawings
label | ac7906b2-b8cc-5c24-b10d-c7629c2465ea |  | note | All works have been completed by a registered gas fitter ?
checkpoint-status | 7a8d2d0b-1a5b-40ae-be98-4c3fbfa7742d |  | checkpoint | Pipework Pressure Test Report Completed ?
checkpoint-status | 3b47c0f9-7509-41f8-aad2-7c04494e4d10 |  | checkpoint | As-Builts Completed.
holdpoint | 770763b2-60b2-4a52-bd9c-629cb339c4fb |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 2071fdce-71e6-48f5-a16e-3e869c90e011 |  | checklist | Electrical and Communications Conduit Installation |  |  |  |  | Yes | Electrical and Communications Conduit Installation | 0ac1c466-5cab-4995-b8c8-2e310a39fd64
checkpoint-status | 89ca0071-978f-46b2-a4e2-2e7e94dc2d8c |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 2bd8548e-95dd-488d-93b9-ad086383f072 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | b40091b8-fcd4-44c9-a134-579c66a61246 |  | checkpoint | Confirm trench depth, width and pipe alignment, QA documents to be received from sub-contractor prior to installation of conduit in trench.
checkpoint-status | b7700a38-cba9-450c-9482-923f55821e7a |  | checkpoint | Number of conduit dimensions shall be shown on drawings.
checkpoint-status | bd2227c6-325f-427c-a471-1bfb352116d2 |  | checkpoint | Location of conduits shall be shown on the drawings.
checkpoint-status | a9e6b61f-846b-4aa4-a4fe-f8efb63ed756 |  | checkpoint | After Installation all conduits shall be free from foreign matter and from rough edges which could damage the cable during Installation.
checkpoint-status | 7a0ee8dc-b02f-4d17-aa02-3eb795f97afb |  | checkpoint | Where practicable conduits shall enter and exit the pit at the same height and orientation.
checkpoint-status | 301b1e76-1927-4a3c-a012-7277bee08cec |  | checkpoint | A draw rope shall be installed in each conduit run and shall extend a minimum of 500mm above the top of pit collar.
checkpoint-status | 80bb38ef-e6fc-440e-830d-ffa071494bb6 |  | checkpoint | Rope ends shall be firmly secured to prevent the ends being lost in a conduit.
checkpoint-status | 3e601c5a-5007-4205-8db0-449f1d223a2b |  | checkpoint | As-built drawings completed.
holdpoint | 1d6b6049-ac4b-4177-bc81-571764e33f00 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat |  |  | checklist | B7A - Functional Tests of Terminal Units |  |  |  |  | Yes | B7A - Functional Tests of Terminal Units | 124bc065-0357-4219-bd9c-0dc38bb28b3b
checkpoint-status |  |  | checkpoint | B7A - Functional Tests of Terminal Units complete
text | 08c4630b-6ee9-5ca7-a800-f20660515166 |  | textbox | Plant ref
text | 67e2ca71-8b68-5043-80c7-08016619a816 |  | textbox | Test by
text | cccdd03f-afb6-5be2-afb4-5ce0cef677e0 |  | textbox | Test date
text | dd044b6c-ce6d-59dd-b260-18b5a0220a99 |  | textbox | Revision
text | e0dc2e7f-4c84-5fd7-9c64-340eae93c9d6 |  | textbox | System
text | 45110706-1468-538b-8c0b-f879e998d9fe |  | textbox | Specified flow (L/min)
text | a03ce393-b20a-569a-a4f4-01491873a9d2 |  | textbox | Specified pressure drop (kPa)
checkpoint-status |  |  | checkpoint | In accordance with the contract specification and paragraphs 15.77–15.78
text | f7373a57-c60e-576e-9fa4-23d65eb4a2c2 |  | textbox | Terminal unit number
text | 0fb25664-ff6b-57a4-86c5-38eb1ba6f43a |  | textbox | Room number
checkpoint-status |  |  | checkpoint | Specified flow achieved
boolean | f77cc819-e7b3-5049-a1e5-c36c4cf4e5a4 |  | tickbox | Yes
boolean | 4463c6e7-e395-5db3-9da9-40becfd7850d |  | tickbox | No
checkpoint-status |  |  | checkpoint | Specified pressure drop achieved
boolean | ff1b2465-4669-5735-ae72-617d4655036f |  | tickbox | Yes
boolean | 3b57671d-641e-52e8-a828-9f0219e1374e |  | tickbox | No
text | 5315a658-4207-55d0-b659-cc33cd6b4e38 |  | textbox | Mechanical function
text | bd1ee49a-d3f7-5e42-b518-2cf84e913649 |  | textbox | Gas specificity
checklist-flat | 910b4d2f-20e6-4202-b30f-e5a98f1673b7 |  | checklist | Butt Welding |  |  |  |  | Yes | Butt Welding | 1af85a7b-4718-4fbb-9bfd-d718da1b261e
checkpoint-status | c8dee859-39ca-4784-9e6e-7d9941180258 |  | checkpoint | Weld Details Completed
text | ed0b2069-38ae-51a6-b0c2-c74383a77503 |  | textbox | Weld Number
select | 654e0c4e-ae75-5efb-9283-fce9597f1eee |  | dropdown | Weld Completed By: | Benjamin Habon, EB Lindayao, Jefferson Calla, Redennis Teves, Steve Reeves, William Sabino, Calvin Cheyne, Mark Bateman, John Chingkaw
select | d7bd3611-6574-5e7b-985b-31213b80e0b3 |  | dropdown | Welding Machine # | Machine 1, Machine 2, Machine 3
text | 1ef3ca77-bad6-5887-9679-d203af4d134f |  | textbox | Certificate #
checkpoint-status | 9348f672-5bb8-48af-8f81-f1ebc2d0197e |  | checkpoint | Pre-weld checks - Visual Inspection of Pipe
label | c297085c-730f-5bd0-a703-add028ac308b |  | note | Ensure branding markings correct
text | 72f28d58-c2ea-537b-88a4-d9afc569fad0 |  | textbox | Record pipe batch number as labelled on the pipe.
text | 72602a86-7457-55e5-9585-0023a698231b |  | textbox | Record pipe wall thickness and inspect.
label | aa5c60b5-1bda-547e-b1ba-b0ddb3e8d4df |  | note | External surfaces are free from scratches deeper than 10% of wall thickness.
label | 307a431e-3d7e-5560-bb54-19623f62c94f |  | note | Inspect internal surface of pipe for scratches.
label | 741c3ce7-5ff4-5c6d-a4a4-44176bfa9235 |  | note | Inspect pipe for cracks.
label | 31efab25-044f-586a-afc0-b20d72a11a63 |  | note | Inspect internal ridges or ripples exceeding 0.5mm in height.
label | 69994fdc-2df3-5a06-889c-37bd5e3df477 |  | note | Clean and wipe pipe with Isopropanol.
label | 78fbbf96-1404-5ecd-bb1b-106fd6853b90 |  | note | Inspect pipe ends are dry from any water content.
checkpoint-status | 73772ba4-d361-4e96-8692-3d8c064313f8 |  | checkpoint | Pre-Weld Checks - Weld Machine Checks
checkpoint-status | 305a8ae4-dd9b-47d5-a05a-c98a7c967f08 |  | checkpoint | Heater plate temperature checks taken and recorded
label | 1392f678-f011-5811-8d91-60940c6de348 |  | note | Ensure pipe ends are capped, welding area isolated to regulate cooling and prevent airborne contaminants.
checkpoint-status | 1ea12469-42df-4f80-8fdc-0a2f3f53ec8c |  | checkpoint | Post Weld - Visual Checks
label | 76f5e0b6-ffdb-5394-8452-e2113022e127 |  | note | Alignment of pipes is less than 10% of pipe wall thickness?
label | d23a7c58-7cf9-5b49-93d3-f2f4774a6d5d |  | note | Fusion beads symmetrical on both sides of weld
label | 8a940c97-118c-5404-a362-346945f8027d |  | note | Ensure Beads are fully rolled over
label | e44185ee-cac1-5d5e-881e-703a3e83133c |  | note | Inspect for cracks in beads and welds are free of pitting and bubbling.
label | f6237a4a-5669-50c3-8fc2-c13123f6f9ee |  | note | Inspect for inclusions or other obvious faults present.
label | ab1817be-06cf-55e1-9e24-276ba3926f96 |  | note | Internal weld beads removed from pipe?
checkpoint-status | 0c3354d5-b811-4786-a402-b6cc6a3c35f5 |  | checkpoint | Weld Records and Inspections
label | bd6b904f-1749-5199-a285-561c0b2364f8 |  | note | Data logger records printed, checked and attached?
label | a35d4317-dd9a-5182-809b-b0cc5628a06c |  | note | Weld completed, inspected by AE Smith Supervisor and CPB ?
holdpoint | adfc0216-485c-4223-9d0d-7e70004f848a |  | signoff | Post weld checks by CPB and AE Smith - Request Signoff/ Raise Remedial
checklist-flat | b88a90a9-8ec6-4bd0-83c3-fd66b1c09e1e |  | checklist | LV Installation |  |  |  |  | Yes | LV Installation | 1f616609-c97b-4805-9d58-b0c438af1678
checkpoint-status | f6f8947b-16e3-42f5-b382-14f40af2a14c |  | checkpoint | ROM & consent approval received by the client and approved?
checkpoint-status | 01ba2610-6a11-4cc6-a387-b38b547c4293 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
label | 20b157e9-b034-5ac5-9178-f48ec267f675 |  | note | Attach: material inspection checklist
checkpoint-status | 05176e80-99a4-4af5-b990-7a10b1a87b26 |  | checkpoint | Inspect trench depth, width & cable rout
label | 6541afb4-6977-516a-84fe-01d3731ad744 |  | note | Shall be as shown on the drawings,
label | ea6a8db4-e541-5866-aa8b-4e4c739964a1 |  | note | Attach: Excavation Checklist & Photos
holdpoint | eccd7719-6e0f-4d47-ab5b-a0d3d744b3f8 |  | signoff | CPB HP - Documents
checkpoint-status | 39dc7763-49fc-49ab-82ab-ce0aad17d71e |  | checkpoint | Drum Delivery Test Certificate
label | 90dbdc7d-0a0d-562c-927a-6379f7cae1f6 |  | note | Attach documentation
checkpoint-status | c7ec6c07-df6a-4f84-90cd-e58ef52d5978 |  | checkpoint | Pre-haul Checks
label | 2b1feea8-6aa7-500f-8145-14c400401fb4 |  | note | Verify Cable is in good order and condition prior to haulage
checkpoint-status | 1278206a-c6d8-4a27-a1f2-37a1cbcec1d5 |  | checkpoint | Confirm correct lubricant available for use, where applicable
label | ab1952ea-66e5-5f57-a12a-3a9797764f36 |  | note | Verify correct type, and that sufficient quantities are available
checkpoint-status | b8c26706-a470-49bb-ac5b-923e9084a10f |  | checkpoint | Observe the Haul
label | 4a9e158f-1159-5f38-b3d5-42508a837221 |  | note | Stop the haul if a potential risk of damage is identified
checkpoint-status | 74fd391a-362b-47d6-8692-f3991b4e738b |  | checkpoint | Inspect cable sheath during the haul
label | be7810fc-da3e-501a-b9c6-1b4f14ab99a7 |  | note | Stop the haul if any damage is identified
checkpoint-status | 5ae5906a-12da-441a-b865-fdd0fa1a4280 |  | checkpoint | Inspect cable sheath at the completion of the haul
label | 6bdb4bce-12f2-5a04-9b45-4a02d9897f89 |  | note | identity an signs of damage
checkpoint-status | 38149d36-9dad-4880-b775-dd5bd7f9f7f7 |  | checkpoint | Install Seismic Loop
label | 3ce3d06c-192b-5896-8be2-5f8c08470a27 |  | note | Visual Inspections
checkpoint-status | 2661cab7-a202-4a9f-9833-3cf886c4fb9b |  | checkpoint | Install cables into building and contain to prevent damage
label | c37cbda9-6226-5395-9079-b0f7a5cba406 |  | note | Visual Inspections
checkpoint-status | d1cae302-f0f6-4760-a3e5-083dd37ccdf7 |  | checkpoint | Install lime & compact
label | 894a01bf-fb1f-5ffb-8aaa-1794b623e518 |  | note | Visual Inspections
label | 2b8489db-ac3e-5b1a-babe-b4c979046391 |  | note | Check bedding depth
checkpoint-status | 84502995-5f0d-48e8-beaf-4a90bfa69b07 |  | checkpoint | Install Mag slab
label | 83721026-e99f-5e82-980f-7d62bc3e06d7 |  | note | Visual Inspections
label | ff91f54b-3071-56f3-b020-08f322a9b16c |  | note | Make sure Mag slab is covering the buried cabes
checkpoint-status | 3c52f741-f68b-47e2-86b4-f8d49adcd6b3 |  | checkpoint | Test cables installed
label | f6ac7679-c0a4-5ea4-89c4-eea3d434c355 |  | note | Insulation Resistance Test
label | a6d45549-037e-5b13-b029-d13d92311665 |  | note | Continuity Test
checkpoint-status | a4b0a609-1299-46cc-88bd-bc7b029b64f4 |  | checkpoint | ITP Sign off Witness Points
label | 29cdc45a-af28-5375-a178-cfa3dec4505c |  | note | 2.1 Inspect trench, depth, width & cable route
label | 3bbb9dd7-9eec-50f8-8a36-6645dc30f998 |  | note | 2.2 Testing of cable prior to cable pulling/laying
label | 728f1e3b-95b7-5c1a-9717-a1544b49ad83 |  | note | 3.1 Pre-haul checks
label | 15c4337c-a488-52aa-b5bf-a73a060037ca |  | note | 3.2 Confirm correct lubricant is available for use where applicable
label | 5ca599cc-816f-52a4-a302-2d1229e4b777 |  | note | 3.3 Observe haul
label | 712cb674-76b5-50a1-a57b-2b0aaed7b7fc |  | note | 3.4 Inspect cable sheath during the haul
label | 9327cbd3-c1a0-5e99-a762-01134c1d0d75 |  | note | 3.5 Inspect cable sheath at the completion haul
label | 2287ee07-3f86-5d92-a79e-dc381784dd82 |  | note | 3.6Install Seismic Loop
label | b7a11b53-a188-542d-892c-f9577407548f |  | note | 3.7 Install cables into Building and contain to prevent damage
label | 7f94abb9-094e-55f4-bb04-9fb4926bda29 |  | note | 3.8 Install lime & compact
label | 76f7ac0a-ad0a-54d4-b510-a8d53469f91d |  | note | 3.9 Install Mag slab
label | d7b94529-0a8b-5f0e-adb9-61317507fd36 |  | note | 3.10 Test cables installed
holdpoint | 3e9cf2b7-7bf0-4bbd-b4bb-9ab9b75a6587 |  | signoff | CPB & AES signoff / raise remedial
checkpoint-status | 90606b12-d76c-4017-892b-3f7ae964268f |  | checkpoint | Inspection by Supervisor
label | ef27fa2d-b4ea-5367-aed9-dfd66dfe8bf2 |  | note | QA check sheets, visual inspection and test requirements to AS/NZS 3000:2007 measurements verified
holdpoint | 74029f19-7cb6-4128-9f52-358edd020d90 |  | signoff | CPB & AES signoff / raise remedial
checkpoint-status | d7365079-3b6f-4c32-8f4b-6777dbe34376 |  | checkpoint | Notice of completion
label | ebfec110-9fff-5a00-80e2-b681ced02f7c |  | note | Had back trench to CPB at Mag slab demarcation point.
holdpoint | 17f076d0-9135-4c57-a4cf-ce3cee3e35b1 |  | signoff | CPB & AES signoff / raise remedial
checklist-flat | ec1354de-7626-474b-a8b4-fc7cbed034c0 |  | checklist | Combined Services HDPE Natural Gas Installation Part 2 of V3 |  |  |  |  | Yes | Combined Services HDPE Natural Gas Installation Part 2 of V3 | 2d1dc380-47a6-4f94-9b4a-f3be38081c7f
checkpoint-status | 2eabd90c-616f-4fa4-a244-03681f75bba5 |  | checkpoint | Confirm trench depth, width and pipe alignment.
label | 731c5841-9b8d-5389-ac3f-4fdb57c311d1 |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | f34c87b3-0d5a-507b-9f85-ff3614ed1abc |  | note | Excavation Checklist to be completed prior to installing services.
checkpoint-status | 5d6048c1-3f68-4a1b-b7cb-c22c5ff395cd |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
holdpoint | bbdafedc-5f86-4625-9ada-b5f44c70a9c6 |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 6c7b726e-11b3-4735-836a-7b59b777bb87 |  | checkpoint | As-constructed survey
label | e5a27f82-a093-56bb-af59-74e85a6a61d7 |  | note | As-constructed survey must capture the horizontal and vertical locations of all newly constructed or relocated underground trenches and pipework.
checklist-flat |  |  | checklist | Back-Flush |  |  |  |  | Yes | Flushing - Back-Flush | 334b15c6-7b49-453c-a5df-1af2377ee9a4
checkpoint-status |  |  | checkpoint | Chemical cleaning is completed and clear water is visible at the main drain valve.
checkpoint-status |  |  | checkpoint | Terminals backward and forward flushed and water drained at the terminals until clear water is visible.
text | f7c77e5a-9d25-5472-bd8b-5567f6e7bed5 |  | textbox | List the terminals backward & forward flushed.
checkpoint-status |  |  | checkpoint | Water sample is taken from the furthest terminal, and labeled as "Back-flushed terminal" and dates.
text | cf18e5fc-59b4-562d-bacb-a59df9ad39aa |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Sulphate
text | a7801e30-a7c7-563d-8edb-c18e23fa5c3a |  | textbox | Site measurement
text | b9f6bbd2-a112-5545-b5ad-a1410f182880 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Chloride
text | 97d85d45-decf-5d92-9477-37321bd0931d |  | textbox | Site measurement
text | 09c3df4b-115a-5fd3-92c2-c2530285f6ff |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | pH
text | 8e19a47e-3135-55d7-9861-67decc201e53 |  | textbox | Site measurement
text | 22a8937b-5118-5583-b690-3c62d66505bc |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Conductivity
text | 6768b150-a787-5503-a7a0-28ff7b4ee142 |  | textbox | Site measurement
text | d886c0d4-f102-59f4-ac59-93f9facc07aa |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | 04249184-1ace-51ec-9707-34a396b5a6dc |  | textbox | Site measurement
text | ca1db508-3bb3-57ed-b19f-4c92a23e4d1c |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TVC (Total viable count: the total numbers of microorganisms, such as bacteria, yeast or mould species)
text | 43364d67-e71b-55cf-bc7c-06337d965c80 |  | textbox | Site measurement
text | dcd89c77-1616-5eaf-a50c-fd3404dbc959 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Pseudomonads (microorganism that can create biofilm)
text | f842f9c9-f160-54fe-9aca-88845c75d64a |  | textbox | Site measurement
text | fcab0ba0-ddab-51a9-adcf-c5b8ddba7e16 |  | textbox | Lab test results
checklist-flat | 6652d6e4-22a6-44dd-89b7-d9fad6a9cbf7 |  | checklist | Electrical and Communications Conduit Trench Riser Installation checklist |  |  |  |  | Yes | Electrical and Communications Conduit Trench Riser Installation checklist | 361f1b9f-66ee-4838-867f-e932b5a66fb7
checkpoint-status | bb6a80f2-e56b-42fe-91b4-c3c48af7640f |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | d344d940-9c45-4416-8d0d-709cd2e09d24 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | b1c2655c-59f2-4b9d-aa70-f02d8956f8df |  | checkpoint | Confirm trench depth, width and pipe alignment, QA documents to be received from sub-contractor prior to installation of conduit in trench.
checkpoint-status | af235ead-2c4f-498a-9467-7806fd4c8469 |  | checkpoint | Number of conduit dimensions shall be shown on drawings.
checkpoint-status | 3b54bd5e-1b9d-40cc-8133-7a9cdae089d9 |  | checkpoint | Location of conduits shall be shown on the drawings.
checkpoint-status | bf2ffa7e-f109-47b4-bf39-a9e6a4102ccf |  | checkpoint | After Installation all conduits shall be free from foreign matter and from rough edges which could damage the cable during Installation.
checkpoint-status | dbdcf3a6-e1a8-48b3-80f7-022be8bc2258 |  | checkpoint | Where practicable conduits shall enter and exit the pit at the same height and orientation.
checkpoint-status | e2b8b3af-7c7d-439c-81cc-ffa9d765f60c |  | checkpoint | A draw rope shall be installed in each conduit run and shall extend a minimum of 500mm above the top of pit collar.
checkpoint-status | 18acff54-f214-40d7-8f3f-6605891d1785 |  | checkpoint | Rope ends shall be firmly secured to prevent the ends being lost in a conduit.
checkpoint-status | 8c57b926-1fe7-4512-9631-1b5495a5183a |  | checkpoint | As-built drawings completed.
holdpoint | 3522a344-b88d-4993-9a37-38f6669926a3 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 89983eeb-40b8-4d9a-846b-86db75106d69 |  | checklist | Document: |  |  |  |  | Yes | Project Documentation | 39a14167-4ddb-4a2f-9155-27e491efa078
checkpoint-no-status | 78d25478-5723-4f8e-b4d8-3b7b8d9a0cd0 |  | checkpoint | Document Attached
checklist-flat |  |  | checklist | Dynamic Flushing Checklist |  |  |  |  | Yes | Flushing - Dynamic Flushing Checklist | 40344506-d308-40da-81d2-b9aa8db91eb3
checkpoint-status |  |  | checkpoint | Uploaded highlighted drawing.
text | d92e4ec0-9a51-597c-84a4-c5ad2ddd1b34 |  | textbox | List the zones / terminals / branches flushed during this step.
checkpoint-status |  |  | checkpoint | Confirm all other terminals isolated
checkpoint-status |  |  | checkpoint | Turn the pump on and run it at 20 Hz (or at minimum speed)
checkpoint-status |  |  | checkpoint | Increase the pump speed to 50 Hz and measure the total waterflow
text | 48ca6c6d-fe2f-5d0e-84fa-fcd5817050e6 |  | textbox | Record total and terminal waterflows on the "Flushing Water Flows" test sheet and upload here.
checkpoint-status |  |  | checkpoint | Circulate water for 2-4 hours by sampling the drain water quality. Record the duration.
label | 881aee60-091d-5133-9532-c909b3cb5bf0 |  | note | The duration of this process depends on the size of the system and may required to be extended.
text | 6748fe0c-d52b-5d25-a558-556a4d8621a3 |  | textbox | Duration
checkpoint-status |  |  | checkpoint | Clean strainers as required. Upload dirt and clean strainer photos here.
checkpoint-status |  |  | checkpoint | Photo of water sample at the end of the dynamic flushing
checklist-flat | 2baeceb8-38d8-4273-93a3-5e95292911a0 |  | checklist | Pressure Test Report QCC-01.01 |  |  |  |  | Yes | Pressure Test Report QCC-01.01 | 47e74aba-1a0a-48ca-bcd5-30013cba44bf
checkpoint-status | ea703a41-ec2f-42c2-b741-d07e7c401b23 |  | checkpoint | Details of pressure test
text | 125a1f58-fb93-4fca-b207-81062af299ba |  | textbox | System Name/No.
text | 42b4109d-b3ba-450d-a96a-9217ffe123f7 |  | textbox | Location / Drawing No.
text | ddddbb20-aebf-4150-af44-058724908df6 |  | textbox | Test Instrument & Serial Number.
text | 1ffb4b68-825a-4ff9-a9c6-87fa9700d497 |  | textbox | Normal Working Pressure
text | 22d523d8-c31a-4752-ba5d-2a1ebce470fe |  | textbox | Start test ambient temperature
text | c20847d5-6182-4dec-9899-d1888d45e3d4 |  | textbox | Start test date
text | 31e3a80b-edab-4454-bb5f-ac357745cc76 |  | textbox | Start test time
text | 917ef879-4510-4dcc-a2c1-691a80ea5c5f |  | textbox | Start test pressure
text | dd5b4735-e182-4d04-841c-f425c1267348 |  | textbox | Finish test ambient temperature
text | 2c810d16-e75f-4644-99cc-359aa4d8a695 |  | textbox | Finish test date
text | b675deb2-9fad-453e-be71-589c96095ef0 |  | textbox | Finish test time
text | 4e71ffa8-f76f-4832-8216-a4f15f2ff734 |  | textbox | Finish test pressure
text | cbeee8b8-03d5-46b6-a5ea-8522baa6875f |  | textbox | Corrected pressure at test completion
label | 7990a0c7-14a7-4f43-b773-fb56a6ae93c1 |  | note | Attach photos of the gauges as required
label | 6059a464-043f-4bd0-8b04-c2f8cbad5042 |  | note | FORMULA :
label | 71330246-4fe0-4294-921b-beb085d495cb |  | note | Pc = P x (Ts + 273) / (T + 273) kpa
label | 1a04a208-c0e5-4d52-ad08-4300aed9e545 |  | note | Pc = P x ( +273 ) / ( + 273) kPa
label | 9f8ea800-f4bb-49af-a8b5-389758071961 |  | note | Pc = kPa
label | 57105522-72b0-4769-8f26-25359e8f238e |  | note | WHERE:-
label | 26a80af3-2173-40a6-9868-00ed118f3db0 |  | note | P = PRESSURE REQUIRING CORRECTION i.e. PRESSURE ACTUALLY READ AT TEST END
label | ed49c168-0d5b-4b0f-a64e-e31771f502a8 |  | note | Pc = CORRECTED PRESSURE
label | 241239a4-61f2-4368-98de-7a04516ebd82 |  | note | Ts = AMBIENT TEMPERATURE oC AT START OF TEST
label | 8e6e5ef8-edf4-47ec-9cd1-094d5e762d8d |  | note | T = AMBIENT TEMPERATURE oC AT SAME TIME OF READING P.
checklist-flat | dc5debdb-78dd-41df-9d0d-7175d51df667 |  | checklist | Trench Pipe Riser Installation Checklist |  |  |  |  | Yes | Trench Pipe Riser Installation Checklist | 49ab133b-deac-4693-89d0-576f5af3330c
checkpoint-status | 202c1457-00e8-45cc-a9b0-96400a8f8c13 |  | checkpoint | RDM & Consent Approval received by the client and approved?
checkpoint-status | 7daeeea3-35bf-4161-8815-2566626375ba |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | a5e9b983-bfa3-4fc2-adb2-24dbab8c0672 |  | checkpoint | Confirm trench depth, width and pipe alignment.
checkpoint-status | 2e7a780f-196b-4d1b-a6e0-a1c448c36e7c |  | checkpoint | All pipe flanges are capped, and ball valve installed on pipe ends exiting the trench.
checkpoint-status | 775b3bbe-579b-4041-aa6e-77949cffe878 |  | checkpoint | Each pipe shall be pressure tested prior to installation , Refer to separate pressure test report QCC-01.01
checkpoint-status | 3af545b2-1344-450d-a87c-ce6dd3dfc5f3 |  | checkpoint | 100Kpa of air to remain in pipework to verify no leakage, Refer to separate pressure test report QCC-01.01
checkpoint-status | 8d53cfa0-a2bd-41e4-98cb-e5090f5126fe |  | checkpoint | Number of pipework dimensions shall be shown on drawings.
checkpoint-status | 0f01edef-aad1-4f6a-ba4b-c885a1a8fb93 |  | checkpoint | Location of pipework shall be shown on the drawings.
checkpoint-status | 151b52dd-ba2d-4afb-a04a-cc4aac9b792d |  | checkpoint | Pipework exiting the trench shall conform to the location and dimensions shown on construction drawings and specification.
checkpoint-status | 79d455d7-8c87-49f3-a4b6-389e05da6bf9 |  | checkpoint | Before backfilling inspect all installed pipework and insulation for damage
checkpoint-status | 22c2ead9-6a8c-4fe6-98ef-c247518d52cd |  | checkpoint | Pipework pressure to be verified of no pressure drop prior to connecting to mains pipework
checkpoint-status | d2b04c28-bef1-4754-a1e2-e973211527db |  | checkpoint | As-Builts Completed.
holdpoint | 73c83ccf-d94e-4b6a-aa1e-0e83384c3ca8 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 68c8296b-1494-4c30-991b-785b37ce0b40 |  | checklist | Project Details |  |  |  |  | Yes | Project Details | 51f170ee-0a3a-41ea-bf26-683743dc17d2
checkpoint-status | 08b8e56a-f13a-4198-99cc-0515de89b333 |  | checkpoint | Project Information
text | b6deda1f-d359-47ad-8507-719dc8afe130 |  | textbox | Project Name:
text | 2c5f2213-0e59-43bb-8f75-04b868c594a1 |  | textbox | Project Address:
text | bb311aed-d63c-427b-9031-081bb148d86b |  | textbox | AE Smith Site Manager:
text | 3ed7586f-75c1-49e4-82a2-88dd04bbeecb |  | textbox | Consultant:
text | 10ea1d41-1768-4262-a1aa-060af1a01618 |  | textbox | Client
checkpoint-no-status | 0d418e81-f3d0-47a5-9552-fb4b3cca3e14 |  | checkpoint | Quality Plan for the Project
checklist-flat | ef2c9b78-1c6d-4fa6-8494-8a3d34acbad1 |  | checklist | RBG Combined Services HDPE Potable Water Pipework Installation |  |  |  |  | Yes | RBG Combined Services HDPE Potable Water Pipework Installation | 587a1ea2-2d98-4741-ba46-97a1e1066ff2
checkpoint-status | b1a4af62-9333-4280-a529-7825350fe64a |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | f5ba4de4-fc2b-425f-848e-50c68f6eafa6 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | 3c37ebf1-7478-4272-ac50-916c999f0b14 |  | checkpoint | Inspect trench depth, width and pipe alignment
label | 1f5f14d0-0a46-5076-942c-70387bd78029 |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | 6a4a5612-500c-5daa-bd17-158ae30120b8 |  | note | QA documents to be provided prior to installing pipework in trenches . CPB to provide to AE Smith.
checkpoint-status | 66dda95b-a0c2-480b-b08d-f6b2b72b9e26 |  | checkpoint | Number of pipes and dimensions of pipes shall be shown on the drawing
checkpoint-status | a8c24b3e-58e0-422a-96b1-35c9232254ea |  | checkpoint | Location of pipe
label | 45226daf-6ddc-5f22-b9bb-9acd558e6145 |  | note | Shall be as shown on the drawings
label | a5246ab5-35fc-533a-b91d-6751d7cac815 |  | note | Ensure correct clearances between water service and other underground services.
checkpoint-status | 407771b4-c998-4e44-8c81-6fa5d0efcd52 |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
checkpoint-status | d1cdc9b0-6e1e-4915-af80-0e2a8f247346 |  | checkpoint | Jointing of pipes only via. Rotatable steel flanges, EF Coupling and Butt Welding.
checkpoint-status | f3722075-ca1e-4c00-9c18-2ab560e3d02e |  | checkpoint | Electrofusion Welding Checklist completed for each joint?
checkpoint-status | 199c706a-f340-46b6-9060-509c9f712a10 |  | checkpoint | Butt welding checklist completed for each joint ?
checkpoint-status | c85e8094-f833-4797-a369-0165404fe739 |  | checkpoint | Install valves, tees and bends
label | be38ee2f-c50f-5cd6-a263-61d2ff548f69 |  | note | Install all connections as per construction drawings
label | 854b0cf7-bceb-5a8c-bf65-f3f39f7a1bac |  | note | All valve 100mm and above will require a 1050mm manhole.
checkpoint-status | 7000a464-b8f7-44e7-ab56-bfe1c5e247a4 |  | checkpoint | Installation of ductile iron bends
label | 239721b3-cd49-5229-ad74-33b6b8f3e1fe |  | note | Inspect pressure class on fittings and ensure correct pressure rating prior to installation.
label | 870c7f91-0842-5318-ae66-2460a7e070f9 |  | note | Ensure correct gaskets are installed.
label | c89b836f-47cb-5356-9c6b-993f45c05393 |  | note | Washers installed on both sides of the flange.
label | 31696213-b74a-56ab-b33d-6caed3a04cbb |  | note | Bolts to be tightened in correct tightening sequence.
checkpoint-status | 50ba9efa-0143-40a0-b7fb-23772d49d35f |  | checkpoint | Install Thrust and Anchor Blocks
label | 8d55a9f7-0068-5557-9082-1fefd9343b29 |  | note | Minimum dimensions as per IFC drawings.
label | 03ef9c7c-b704-55b1-94a2-6735ab38d270 |  | note | A protective Denso or black coating membrane is to be installed around the pipe and the concrete anchor/thrust blocks to prevent abrasive damage.
checkpoint-status | 98962c2f-97c6-4dd8-9289-d82f083be9a5 |  | checkpoint | Completed Construction Pressure Testing with Air
checkpoint-status | d197186e-5f6a-4ac5-98e6-9da1a5d8fef6 |  | checkpoint | Pre-Pipework Pressure Testing Inspection
label | 61d9d852-7ecd-5861-a244-c91d0f6396dd |  | note | Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | f7077cef-3021-58ed-b88e-8fec14790ab5 |  | note | Ensure each test length is capped and ball valve installed.
label | e444efc0-92d9-5d01-bda1-d6877f023ef8 |  | note | Ensure all valves in the system are in the correct position and tagged “DO NOT OPEN” or “DO NOT CLOSE”
label | adc2a524-0490-549e-bf2d-5fc9217af438 |  | note | All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing.
checkpoint-status | 7b5cfb5a-3e20-44fa-8397-e16bc0dff973 |  | checkpoint | Introduction of Air to 300 kPa
label | 7f2d9410-77f4-5211-b135-0ceb2a497fd4 |  | note | Gradually introduce air into the system to a pressure of 300 kPa and hold for 1 hour.
label | f54a9352-5577-55ab-9ff9-43c105880bad |  | note | Monitor for any drop-in pressure.
label | 4126733c-45e2-5e4c-8b7b-8576d8fe8f17 |  | note | If a leak is identified discharge the air prior to rectifying any leaks.
checkpoint-status | 9a127470-f19d-4d84-854a-544d47b83642 |  | checkpoint | Increasing Test Pressure
label | 012fd3ad-5953-580b-b117-92a9225d48f5 |  | note | If no leaks are identified Increase pressure by 10% increments until test pressure is achieved.
checkpoint-status | 9bce60e2-322f-4ae7-bf33-1d43167fcfbf |  | checkpoint | Pipework Pressure Test Report Completed
checkpoint-status | 1f012bda-dc7f-49f3-bead-30c191a85678 |  | checkpoint | Installation of Trace Wire
label | 5f304721-e92b-5fbd-af5a-41c3fc4507fb |  | note | Install Trace Wire and ensure tracer wire is continuous between valves and any excess coiled in valve box.
label | 0e802672-3652-5d6e-8f9d-3987542f091c |  | note | Test Trace Wire following installation.
checkpoint-status | e1706b07-87c1-463b-8e8a-ec10239d8048 |  | checkpoint | As-Builts Completed.
holdpoint | 54c918c7-8c76-4c87-9a13-f313df2a3332 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat |  |  | checklist | B5A - Area valve service units – closure and zoning test |  |  |  |  | Yes | B5A - Area valve service units – closure and zoning test | 62221e2e-562a-4bac-95e0-43884d80a0b0
checkpoint-status |  |  | checkpoint | B5A - Area valve service units – closure and zoning test complete
text | 4724c0fb-b223-5bbd-8b5e-b6dabcef804a |  | textbox | Plant ref
text | ed57b170-5faf-5075-a862-c15c38bddf5a |  | textbox | Test by
text | fd66c3b4-910e-58dd-8b36-ae2774f3add5 |  | textbox | Test date
text | 94b4f34e-4f93-5e88-b75d-ef8f88fe85ec |  | textbox | Revision
checkpoint-status |  |  | checkpoint | This is to certify that CLOSURE and ZONING of the AVSUs was tested in accordance with paragraphs 15.63–15.68 on the pipeline system as follows:
text | 41048983-90ef-5923-94c6-0017798f3999 |  | textbox | AVSU number
text | aa684395-8586-596e-9930-8096665abfa3 |  | textbox | Test pressure (kPa)
text | 16c41161-e274-5db9-87dd-bcf91f5b8a58 |  | textbox | Downstream/upstream pressure change after 15 min (kPa)
text | c77b7edc-447c-5f6a-b2ab-aff7d89d22ab |  | textbox | Terminal units controlled (total no)
text | e0cb3f72-36aa-5881-9102-72a1e322cf90 |  | textbox | Terminal unit labelling
text | 47fd0373-b061-50a1-be4d-d78c365106e4 |  | textbox | Contractors representative:
checkpoint-status |  |  | checkpoint | Sign Off Complete
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
checkpoint-status |  |  | checkpoint | Signed off By Witness
text | ce95209f-f790-5d18-9cd4-f1c820e1dac7 |  | textbox | Witness Name
checkpoint-status |  |  | checkpoint | Signed off by Consultant
text | 3df14d22-f7fc-5eb9-ad2d-913d1ea77942 |  | textbox | Consultant Name
checklist-sectioned |  |  | checklist | Combined Services HHW & CHW Hydrostatic Pressure Test |  |  |  |  | Yes | Combined Services HHW & CHW Hydrostatic Pressure Test | 671b7bcb-df87-464e-9ecc-d989ebd88852
checkpoint-group |  |  | section | 1.0 MATERIAL COMPLIANCE
checkpoint-status |  |  | checkpoint | 1.1 - RDM & Consent Approval
label | 7dbf5a1d-3e62-5ff7-a807-10202d7feaef |  | note | Resp. - CPB
label | 7068cb13-8a4e-5117-a02b-886d68a72062 |  | note | Referenced Documentation - RDM Tracker Consent Tracker
label | 10ac9966-51b9-5e5f-b75c-612427073944 |  | note | Conformance Criteria - RDM approval tracker Consent approval tracker
label | 1e938b70-bf83-5788-8df2-ba2802153eec |  | note | Method - Document Review
label | 70421ff2-d41e-5945-ade2-a3f9a5e2ee0c |  | note | Frequency - By Building/Site Wide
label | 4868e02e-b10c-509f-ac33-3d24962a2277 |  | note | HP - CPB
label | 400fc825-4443-59aa-a7f5-3776822350da |  | note | Records - Receipt of Approval by Client
holdpoint |  |  | signoff | CPB HP
checkpoint-status |  |  | checkpoint | 1.2 - General
label | b4b1bfa7-67b6-5492-b9b1-dbc7bee28926 |  | note | Resp. - SE
label | 1100b3f8-2643-54fa-b922-ab802557fbce |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | 6c83f425-27f5-5ce5-825a-a886c3e8ba36 |  | note | Conformance Criteria - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
label | 13d75c94-d94a-54a0-aa06-5065be361919 |  | note | Specifications & QA Documents Approved
label | 6f7d24f6-c43d-5104-970a-a51871de567d |  | note | Drawings are confirmed
label | 635e2f35-7bcf-50ec-b776-c346b66740d1 |  | note | Equipment fit for purpose
label | 3d23aee5-7c2a-5301-8c3b-c0eea4f2a12a |  | note | Method - DR
label | aff1dc65-583c-5776-84f5-2a6cd94c92fd |  | note | Frequency - Each material
label | 85d7d66a-96a9-5464-b4ba-c1c65aec068a |  | note | HP - CPB
label | 1381b675-e8cd-5145-8931-d1ef426aee8c |  | note | Records - Aconex approval
label | 423785e1-26aa-58a1-8aed-76a8f25f8a93 |  | note | Incoming Inspection Checklists
label | 940cd259-ff1d-5d90-b724-31739c929023 |  | note | Drawing Register
holdpoint |  |  | signoff | CPB HP
checkpoint-group |  |  | section | 2.0 CONNECT PUMP TO HHW & CHW RING MAINS
checkpoint-status |  |  | checkpoint | 2.1 - Accept delivery of pump to site
label | 8a3c6ca6-3e46-5cb1-b04c-95be0253baa2 |  | note | Resp. - SUP
label | 5273458c-fb42-5630-a4a5-ea1f6322dd66 |  | note | Referenced Documentation -
label | 899f68dd-c714-50d4-b0f0-ad25046816ac |  | note | Conformance Criteria - 1. Check pump is rated for pressure test
label | 9fec7b3a-4656-5ca6-b3ba-e1cd23988c1f |  | note | 2. Check all supplied attachments are correct and in good order
label | 3670af12-6d1a-50c7-8834-dd6c01cc3ed5 |  | note | 3. Check fluid levels & fill as necessary
label | f6b5903a-f6ef-5996-89c1-d230d11cce5f |  | note | Method - V
label | d0e85f6d-2bbf-55d2-89e3-b9fae7a19590 |  | note | Frequency - Once
label | c46851d0-1b6e-5563-84c1-c8e448cba74f |  | note | WP - AE Smith
label | b2551c16-66f3-5290-92b9-509e4344ef33 |  | note | Records - Check sheet
checkpoint-status |  |  | checkpoint | 2.2 - Connect pump to CHW & CHW ring mains
label | be681df3-d4c2-5a49-8e13-3afa4bae9cfd |  | note | Resp. - SUP
label | daaa3565-e268-590d-ac5c-c406bb132a38 |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | 14f177b4-79b5-53fd-89d3-b2203831ad16 |  | note | Conformance Criteria - Confirm connections are safe and correct
label | 6c9e5c51-225b-5045-95ca-5419bcc700b4 |  | note | Method - V
label | 1a3a9102-55a2-55fc-8f89-16dfd595802e |  | note | Frequency - Once
label | 99fe6aad-b494-5af8-893a-7c086ef87cd5 |  | note | WP - AE Smith
label | 611687d5-9a18-57db-995a-c22f07a03ee1 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | 2.3 - Connect calibrated gauges for pressure test
label | 2ae8e0ee-1bd0-5ca6-b0b9-270a23554167 |  | note | Resp. - SUP
label | 08fc09dd-d090-5c24-bb58-8dfb379c342c |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | d4efb201-1aa1-5e97-8645-ede28ab3726b |  | note | AS 4041:2006
label | c83faef9-9f6c-570a-89f3-d72406fe6ca9 |  | note | Conformance Criteria - Confirm position is correct, gauge is in good order for test & calibrated
label | e7c5abbb-ccf6-5957-a8c2-5008179b80cc |  | note | Method - V + DR
label | 3797bf8b-9ac3-5e4e-a8f3-e66ca0276072 |  | note | Frequency - Each test
label | 686687f7-d200-528c-ad7f-efdc954c03bb |  | note | WP - AE Smith
label | b99b86f2-8f65-5603-8b28-514a0a9dc50c |  | note | Records - Check Sheet + Document
checkpoint-group |  |  | section | 3.0 HYDROSTATIC TEST (STAGE ONE)
checkpoint-status |  |  | checkpoint | 3.1 - Fill CHW & HHW ring mains with domestic water
label | 9b92cadb-c80f-56a6-9353-44402e1cf846 |  | note | Resp. - SUP
label | 046d0a6c-e59d-5c6d-9a64-e0601068fed1 |  | note | Referenced Documentation -
label | 45d26c64-2f78-5b0b-9e90-4afac3e46407 |  | note | Conformance Criteria - Completely fill closed loop system with water releasing all air
label | c82756b6-11e9-5828-bbde-9a6100154b5f |  | note | Method - V
label | dda75679-105b-5504-824b-7d29fbf48b6a |  | note | Frequency - Every time system is opened
label | 28e4626a-0b4a-51c5-b3ff-a948582d5a3f |  | note | WP - AE Smith
label | 5d8878f2-7c65-535e-8429-d4f6b2855f78 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | 3.2 - Gradually increase system pressure to 10 bar
label | 18910c8d-2c5b-53c3-910d-f106233f308c |  | note | Resp. - SUP
label | a58e799b-db12-5d2f-9e21-b365b9c7af98 |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | dd81a14a-6e4d-579c-9a36-d4db2149bb80 |  | note | AS 4041:2006
label | 1bbe82eb-0bd7-5c3c-a88e-9aae0ef783b7 |  | note | Conformance Criteria - Slowly raise system pressure to 10 bar
label | fd23c0c5-48b6-52ad-afdf-6539c10fce90 |  | note | Checking for any signs of leaks or pressure drops
label | 474f6137-6ed5-5de0-938e-435a4f3ad4c5 |  | note | Method - V+M
label | adc12b43-6b60-5929-871c-89708ca816fe |  | note | Frequency - Constantly Monitored
label | d23e8aa7-c3c0-597f-8d10-2e637c18f44e |  | note | WP - AE Smith
label | 887b80ed-fafd-50c1-876a-2cbbf98828e9 |  | note | Records - Check sheet
checkpoint-status |  |  | checkpoint | 3.3 - Hold 10 bar pressure for 2 hours (START WITNESSED)
label | 2bb489a1-50e7-5edd-8681-3cf62d6799c3 |  | note | Resp. - SUP
label | 28786a04-2364-586a-bc82-f1f48436da2a |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | 90a4af89-4f24-50e2-85dd-d8b5b1e9912d |  | note | AS 4041:2006
label | ebd38305-13e0-5571-a800-fb9b188ee56c |  | note | Conformance Criteria - Record START time & photograph gauge
label | 81012cc2-daa9-551a-a420-4ed2636b68fb |  | note | All relevant parties to witness starting pressure of 10 bar
label | ea5e12a7-0d59-58fe-ab0a-5e648e2d1cc1 |  | note | Method - V+M
label | c79dc6c0-0ac5-51db-ab6e-55375e82a145 |  | note | Frequency - Once
label | e17d3be8-52b3-5aeb-88ca-1042def825f9 |  | note | WP - AE Smith
label | 3ae15633-cceb-58e5-a992-c2a3c2d411a4 |  | note | HP - AE Smith / CPB / IR
label | e9954e1a-00bf-58e8-8e83-8ad8f07dacfb |  | note | Records - Check Sheet + Photos
holdpoint |  |  | signoff | AE Smith / CPB / IR HP
checkpoint-status |  |  | checkpoint | 3.4 - Hold 10 bar pressure for 2 hours (END WITNESSED)
label | 5adca4bb-7c79-5fd1-ad9b-0ac1d5c35aa5 |  | note | Resp. - SUP
label | 2adb0c69-470a-5218-b41d-e0dc97ac1352 |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | aed28a3d-5528-5e1b-9ab9-53193b0991c8 |  | note | AS 4041:2006
label | 6aa4f695-5187-5eff-8175-64a96519fc7a |  | note | Conformance Criteria - Record FINISH time & photograph gauge
label | 02ef5a7e-b6c4-5187-acce-fdfc48b1a6b8 |  | note | All relevant parties to witness starting pressure of 10 bar
label | 03b4a320-b280-5045-bd4e-b316424cbae9 |  | note | Method - V+M
label | 68b89544-6730-5ac4-9b8b-978be80ff9ad |  | note | Frequency - Once
label | 02bb7b70-97e2-534a-91b4-ff1ec24cfe25 |  | note | WP - AE Smith
label | ea7e6ae4-d8ce-5edf-b4a8-de7c6272de21 |  | note | HP - AE Smith / CPB / IR
label | a32cea25-ac72-5200-a83b-d4d35095ba57 |  | note | Records - Check Sheet + Photos
holdpoint |  |  | signoff | AE Smith / CPB / IR HP
checkpoint-status |  |  | checkpoint | 3.5 - Pressure released or reduced for next test
label | bf1f51e7-adc6-52ea-8f49-58dc533c1c0f |  | note | Resp. - SUP
label | d57dbb05-0293-5170-84b4-97ebc85e733b |  | note | Referenced Documentation -
label | a65f7e36-5021-5c9d-bff4-0db99b13befa |  | note | Conformance Criteria - Supervisor to ensure energy (pressure) is only stored while under test
label | 8bf25700-e15d-597f-a950-61298c87e67e |  | note | Method - V+M
label | 6d2280b6-f38c-5302-8096-4fc4f50591fc |  | note | Frequency - Once
label | b0f32a39-6163-5ae2-b63d-1d67aa723943 |  | note | WP - AE Smith
label | b7c9bde4-ee73-5dbd-b976-55ae99b77ac3 |  | note | Records - Check Sheet
checkpoint-group |  |  | section | 4.0 HYDROSTATIC TEST (STAGE TWO)
checkpoint-status |  |  | checkpoint | 4.1 - Ensure pressure is 7 bar for second stage of test
label | 5d708d81-da7b-5ade-8e75-28ce05c250ad |  | note | Resp. - SUP
label | 26843b87-3d08-5a38-8ef0-8d47d00a41d9 |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | 3f9992f8-3fbd-5575-9150-061c3bf295f8 |  | note | AS 4041:2006
label | 9cbba29e-509e-5da8-916b-1ea746f8adab |  | note | Conformance Criteria - Ensure system pressure has been reduced from previous test to 7 bar or Gradually raise to 7 bar
label | cd85c35d-dcdb-5d53-9b41-fc25ee4948c7 |  | note | Method - V+M
label | f9141b88-0b1b-599d-a1d2-2041d822468a |  | note | Frequency - Constantly Monitor
label | 7ee6823a-f710-5271-9941-7370117b820d |  | note | WP - AE Smith
label | ac722452-010a-51ef-8761-8b40790184f7 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | 4.2 - Hold 7 bar pressure for 24 hours (START WITNESSED)
label | 4594d04e-a6cd-586b-ac1a-41e3689d00db |  | note | Resp. - SUP
label | 85fe9aa3-147e-54e2-8821-1d711baaff7f |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | 478ea59e-81a5-552f-81e5-cac7da79c4ef |  | note | AS 4041:2006
label | a28e89b0-1452-5097-a237-456578551d32 |  | note | Conformance Criteria - Record START time & photograph gauge
label | 06b779f2-3cef-51b8-b0d6-ae10117a0f92 |  | note | All relevant parties to witness starting pressure of 7 bar
label | 962b97ee-4b9f-52e0-a0f6-953b51dd3042 |  | note | Method - V+M
label | 21477c11-1ab3-5706-8371-2e775da809c9 |  | note | Frequency - Once
label | 7edbbfe0-3815-50df-87f0-30f7949e3741 |  | note | WP - AE Smith
label | 0225d7b1-bc69-5476-9e96-0e0eed51a5f9 |  | note | HP - AE Smith / CPB / IR
label | 210213be-20e4-5344-9b00-b68a35110df3 |  | note | Records - Check Sheet + Photos
holdpoint |  |  | signoff | AE Smith / CPB / IR HP
checkpoint-status |  |  | checkpoint | 4.3 - Hold 7 bar pressure for 24 hours (FINISH WITNESSED)
label | 097ea108-7745-5a88-9a78-2c104924e12e |  | note | Resp. - SUP
label | 6d5f8547-ce40-54a4-b043-3bac197cc2f1 |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | 1e27c264-de09-5470-8a75-6d03cd4854b8 |  | note | AS 4041:2006
label | a1e95013-a1d2-568a-b6fb-231d2d92d8b3 |  | note | Conformance Criteria - Record FINISH time & photograph gauge
label | 80e7be97-909f-50e2-8424-f8a7ff92e806 |  | note | All relevant parties to witness starting pressure of 7 bar
label | 46bfe84c-0169-52cb-9037-a64390bdb6a0 |  | note | Method - V+M
label | d7caeaf0-a0ce-5597-8a82-5a078fbb41b1 |  | note | Frequency - Once
label | 49d4390d-e91a-5bfc-b6e1-b380299cf257 |  | note | WP - AE Smith
label | fdc958d7-ad2e-55ff-9c27-483af0d4eca8 |  | note | HP - AE Smith / CPB / IR
label | 253e59b3-6a9a-5f52-97c5-33bb5e440532 |  | note | Records - Check Sheet + Photos
holdpoint |  |  | signoff | AE Smith / CPB / IR HP
checkpoint-status |  |  | checkpoint | 4.4 - Discharge pressure leave system in a safe state
label | 2205f140-adef-591e-8f28-1c57c4a17dff |  | note | Resp. - SUP
label | 3effbc24-41ec-573f-893c-c9925a36f98e |  | note | Conformance Criteria - Discharge system pressure, ensure area is left in a safe state meeting site requirement
label | 52f4eb68-889a-505c-8cde-e71d2e684491 |  | note | Method - V+M
label | bcb53b27-eb39-5f0a-85af-7dc25328be1a |  | note | Frequency - Once
label | 97b93e35-c645-58a4-bbc0-0533bba95e43 |  | note | WP - AE Smith
label | e2873380-00ca-5dcc-a670-60802ffba1ac |  | note | Records - Check Sheet
checkpoint-group |  |  | section | 5.0 COMPLETION RECORDS
checkpoint-status |  |  | checkpoint | 12.1 - Testing Results
label | a004c4f2-70e8-533c-a8e7-c308002f263f |  | note | Resp. - SE SUP
label | a83dd325-b2f7-524d-9a69-8fb7ccb229b1 |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | 586c4cf5-3ab9-514b-8232-5c2012fd07e1 |  | note | AS 4041:2006
label | 803a3439-7540-5589-bf6c-83320d24b176 |  | note | Conformance Criteria - All pipework pressure test reports shall be provided
label | f8062733-1d7f-50a5-b0ac-b3251fa9b2b6 |  | note | Method - DR
label | 30e6220b-4575-5fe7-9db7-16d700cd68d2 |  | note | Frequency - Each lot
label | 9ab8994d-93a6-54ee-b033-79a812b844fc |  | note | WP - AE Smith
label | b480c72d-4a8b-561a-9a08-1f6c3518ec5e |  | note | HP - AE Smith / CPB / IR
label | f993d506-50dd-594c-8be5-45c630baf3e3 |  | note | Records - Check Sheet
holdpoint |  |  | signoff | AE Smith / CPB / IR HP
checklist-flat | 93007974-954d-45f7-a8ce-a5d51ebae12a |  | checklist | Combined Services HDPE Natural Gas Installation V3 |  |  |  |  | Yes | Combined Services HDPE Natural Gas Installation V3 | 6f88628a-3aa3-4b51-ba7d-adb8c5679307
checkpoint-status | 81d9d1c3-2ca4-4755-aed4-9dd51ccdcaa9 |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 0fb1a183-6dbd-482b-be42-c8e0a34072b3 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | 09f69685-fc69-4bc7-88c7-9198fe341b83 |  | checkpoint | Confirm trench depth, width and pipe alignment.
label | 825b3a50-18bf-57e0-97c4-987d3c605216 |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | b5aa1df9-51c8-5b16-aa17-a51bdc5279b9 |  | note | Excavation Checklist to be completed prior to installing services.
checkpoint-status | 909a3597-29fd-4927-8a6d-2ff7e662fdeb |  | checkpoint | Number of pipe dimensions shown on the drawings.
checkpoint-status | 99b2c206-aacd-45e1-9a8c-4efd37ea0974 |  | checkpoint | Location of pipes shall be shown on the drawings.
checkpoint-status | f8d40eab-e855-4581-a10a-3da602616382 |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
holdpoint | 847199ee-28f0-489d-b68f-a6b1ea2692f0 |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 9428b30e-e48b-4682-8abc-0cd2f6173d12 |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | 8a669313-2aef-4a04-9df8-66e7cc9d1a74 |  | checkpoint | Installation of Valves
label | 3003871f-c66e-5f8a-83f1-7d2b5155bc25 |  | note | Valves Installed as per approved drawings
label | cad845f9-dc68-557b-8a8a-22fee268b063 |  | note | All works have been completed by a registered gas fitter ?
holdpoint | 6e6e5452-7ee5-4ad6-829e-1e8ba0a7ff6f |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | f3317e12-269d-456a-80a4-13b64429f8bb |  | checkpoint | Pipework Pressure Test Report Completed ?
checkpoint-status | 81c263a5-653a-4ab6-b365-f864ce6ae265 |  | checkpoint | As-constructed survey
label | bd6d1095-6d27-5fc3-bb68-e67c7e640bbe |  | note | As-constructed survey must capture the horizontal and vertical locations of all newly constructed or relocated underground trenches and pipework.
checkpoint-status | b4dc20ec-aa59-47ce-a4f7-fc4261ad54b9 |  | checkpoint | As-Builts Completed.
holdpoint | 59d1e029-4656-4fa9-99ab-2651d60b62e9 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | b250d3f5-ae66-4014-bb4e-a32362b20d19 |  | checklist | AECOM Combined Services HDPE Domestic Cold Water Pipework Installation V2 |  |  |  |  | Yes | AECOM Combined Services HDPE Domestic Cold Water Pipework Installation V2 | 70628704-73d6-4a11-91aa-a5b015b276f8
checkpoint-status | d7bf4be1-99a0-4ff0-9b5e-48ad38c0634d |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | dd7e9a09-6b97-4f78-93f6-cee30133549d |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | e510e773-1b51-4181-ab73-cfd8b268cadd |  | checkpoint | Inspect trench depth, width and pipe alignment
label | b674d392-5e7c-5ca3-9202-ceaf3137ff8c |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | 0a151677-2db2-5b35-8db2-09ccf9bd2cab |  | note | QA documents to be provided prior to installing pipework in trenches . CPB to provide to AE Smith.
checkpoint-status | 763d1c15-ba11-4dd2-b87a-f438dd45e987 |  | checkpoint | Number of pipes and dimensions of pipes shall be shown on the drawing
checkpoint-status | 1de6bb3e-dad8-45e2-95ef-1ee9e254b51f |  | checkpoint | Location of pipes shall be shown on the drawing
checkpoint-status | fa064245-31c9-462c-86ea-ad4ec534b709 |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
holdpoint | 205b7165-e006-4b86-8db7-221d4e98981a |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 0b9799ea-f95d-400a-9d87-f3fac0f37a9a |  | checkpoint | Joining of pipework only to be done by Rotable steel flanges and EF Coupling.
checkpoint-status | 2ce115ee-1544-4a18-ac41-ee2fe9b236cc |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | cf3d1a8d-33cb-4033-a900-150f6a1c0482 |  | checkpoint | Install , valves , tees and bends
label | 0b3a6b15-268b-578a-9ff2-65381cf2bbbf |  | note | Connections are installed as per construction drawings ?
label | 3f4274cc-c568-5a08-a7b9-2514acc27342 |  | note | All valves 100mm and above have a 1050 manhole ?
checkpoint-status | c2b63369-e0e5-452f-a3b9-5826d7793c5f |  | checkpoint | Install Thrust and Anchor Blocks
label | 74530e5d-7e8b-5183-bfd2-9f93486db4f4 |  | note | Minimum dimensions as per IFC Drawing
label | 4865529d-49b1-539c-84b9-b4ba36f28be0 |  | note | A protective Denso or black coating membrane has been installed around the pipe and the concrete anchor / thrust block to prevent abrasive damage ?
holdpoint | 748c9329-41d6-4df7-9205-f19d1b70369d |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | fc0af7fb-dc33-461c-a7fd-6c7a4e2bd4e3 |  | checkpoint | Installation of Trace Wire
label | b1b06abf-d879-5ef3-8db7-66fbde7d5a60 |  | note | Install Tracer wire as per Specification 5.21 of the Hydraulic Services Specification and ensure tracer wire is continuous between valves and any excess coiled.
label | d6f51b12-5ac2-50d6-a801-9e4fee2251a2 |  | note | Test Trace Wire as per Specification 5.20.4
holdpoint | dcd029ed-a94a-464a-a536-00813d9e7bea |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 7dfb14f2-d548-46b2-962d-1bef45ae0ff1 |  | checkpoint | Completed Construction Pressure Testing with Air
checkpoint-status | beb04b19-a970-43bb-8faf-3c7bdccc5145 |  | checkpoint | Pre-Pipework Pressure Testing Inspection
label | fcabd6bc-61c9-500d-8683-708a7ea510fc |  | note | Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | b5897680-bcca-503c-a270-bf7fb10c0328 |  | note | Ensure all valves in the system are in the correct position and tagged �DO NOT OPEN� or �DO NOT CLOSE�
label | de2c1291-a448-5e48-9cf1-0492fe39d05e |  | note | All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing.
checkpoint-status | 14b85604-6deb-487b-a6bd-18bf2d78f64c |  | checkpoint | Introduction of Air to 300 kPa
label | 5d28d9e9-e916-59eb-98ef-7b672194a7b7 |  | note | Gradually introduce air into the system to a pressure of 300 kPa and hold for 1 hour.
label | 79c6ceba-e456-5097-abd3-9fd8698866d4 |  | note | Monitor for any drop-in pressure.
label | 9c6da1da-d2ff-5df1-bfcc-e85547f0e631 |  | note | If a leak is identified discharge the air prior to rectifying any leaks.
checkpoint-status | 47f60e36-11ad-48a7-bd62-12423df319a2 |  | checkpoint | Increasing Test Pressure
label | 866f542e-d67e-5f10-9ffb-c2c22ae77676 |  | note | If no leaks are identified Increase pressure by 10% increments until test pressure is achieved.
checkpoint-status | d7d1a254-ac11-41dc-8f2c-b0a2c907c820 |  | checkpoint | Pipework Pressure Test Report Completed
checkpoint-status | bf653005-f8af-4adb-a2dc-a68b083accca |  | checkpoint | As-Builts Completed.
holdpoint | 530f0406-82c3-4cd6-96b9-2928734ca105 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat |  |  | checklist | Cleaning Agent Removal |  |  |  |  | Yes | Flushing - Cleaning Agent Removal | 759932d8-e147-44ea-9415-566d434c7dc7
checkpoint-status |  |  | checkpoint | All sections' valves are opened.
text | daf231f4-7faf-5148-9405-b2582b1c0923 |  | textbox | Make-up valve is opened.
text | 56e67f72-752d-51ea-9ef8-25b90c6a9982 |  | textbox | Date
text | 6e379067-4b55-5305-9eea-fadf1642db65 |  | textbox | Main drain valve at the pump is open.
text | 461a8b11-0034-59ef-8b42-b64fd1324967 |  | textbox | Drain waterflow (l/s)
text | edd774a1-ea8b-54ba-819b-94f893b55fa4 |  | textbox | Drain location
text | 662ddb16-73d4-5444-b82f-20976b1a6b1b |  | textbox | Drain duration (minutes)
text | 73b58ad9-a1e5-5faf-b1c2-de934513145e |  | textbox | Calculated drain water volume (L)
text | 1ee54d61-d023-5122-b7c0-1fbc7afc7491 |  | textbox | Special trade waste water permit obtained.
checkpoint-status |  |  | checkpoint | Adequate make-up water available. System's static pressure is not decreasing.
checkpoint-status |  |  | checkpoint | Clean strainers as required. Upload dirt and clean strainer photos here.
checkpoint-status |  |  | checkpoint | Circulate and replace water until the water runs clear.
checkpoint-status |  |  | checkpoint | Water sample is taken, and labeled as "End of Cleaning" and dates.
text | f732980f-38f7-5f19-a4b0-c0d2783f9553 |  | textbox | Date
checkpoint-status |  |  | checkpoint | Sulphate
text | 736ef1c4-d5c1-523b-b963-eb692c113a78 |  | textbox | Site measurement
text | 64c0c47c-666b-541e-9c17-91e108f78215 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Chloride
text | cacac921-4812-51eb-bfba-b233fa8851a3 |  | textbox | Site measurement
text | 45726c7f-8aeb-53d1-9cc0-7b10c6ef3754 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | pH
text | e8cb8a63-9554-5988-a11b-1df206d551d9 |  | textbox | Site measurement
text | ef28236e-9180-5608-b225-29631ff6cd6b |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Conductivity
text | 557b6f4b-2b3f-5ed2-af54-71577aa3086b |  | textbox | Site measurement
text | c9f5161f-59d5-5afe-84f1-29218f125c91 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | a061317d-f849-5406-8f59-e324a2024dd5 |  | textbox | Site measurement
text | e7272bdf-1ae5-56bf-8452-3cfe66521ceb |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TVC (Total viable count: the total numbers of microorganisms, such as bacteria, yeast or mould species)
text | 36d8f2ee-a9ad-5ee2-bacb-0a7c69c0302c |  | textbox | Site measurement
text | 980cc1ba-1720-5117-a935-b1965e66ba16 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Pseudomonads (microorganism that can create biofilm)
text | 2ecdc3dd-1bbb-5732-84b3-e2e7649b91b1 |  | textbox | Site measurement
text | eb8c7330-99ab-5f84-908b-7229fbeaf9ac |  | textbox | Lab test results
checklist-flat |  |  | checklist | Passivisation |  |  |  |  | Yes | Flushing - Passivisation | 78eb78c6-f986-4151-a1d9-9fd340091ab5
checkpoint-status |  |  | checkpoint | Confirmed all terminals backward & forward flushed
checkpoint-status |  |  | checkpoint | Confirmed the system water quality is as close to the make-up water quality as possible.
checkpoint-status |  |  | checkpoint | Test make-up and system water to compare
checkpoint-status |  |  | checkpoint | pH
text | 9015b3ee-49bb-57cc-bb11-236eae330607 |  | textbox | Make-up Water
text | 2ec935e3-255a-543f-829e-6d9ecf267939 |  | textbox | System Water
checkpoint-status |  |  | checkpoint | Conductivity
text | cf9c6bd3-866a-5823-8271-e12361e046b8 |  | textbox | Make-up Water
text | c6fdbe0a-e2d5-5c84-b43e-d3eb2feb9da7 |  | textbox | System Water
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | 9634d41b-b1e8-5658-970e-91d097eed4d6 |  | textbox | Make-up Water
text | 170f3613-8fe6-5374-87b0-4a082aea92b1 |  | textbox | System Water
checkpoint-status |  |  | checkpoint | Inhibitor chemical(s) added.
text | 7a2c0e76-6a7a-5e83-9a13-4622bf12c682 |  | textbox | Enter Date & Time
text | 8ad3c87b-8306-5780-80e4-003e9efba452 |  | textbox | Name of chemical and SDS
text | 90059b62-2ef6-5b03-a84b-a09168f21bc9 |  | textbox | Name of chemical and SDS
checkpoint-status |  |  | checkpoint | Biocide chemical(s) added.
text | 21bcc1ed-83fa-568d-bbe5-7e2c6ef60e93 |  | textbox | Enter Date & Time
text | 7bf4e880-e518-506c-b490-3d8bd7a0efcc |  | textbox | Name of chemical and SDS
text | 3c22053b-2fb7-534a-98af-93de8b3a1f78 |  | textbox | Name of chemical and SDS
checkpoint-status |  |  | checkpoint | Circulate water 2 - 4 hours
select | eaa21601-450d-5d83-a948-5c1e9a0997df |  | dropdown | Is there any neutralisation chemical added as per chemical specialist advise? | Yes,No
text | b662c954-9960-54dc-bba2-724f46912cf0 |  | textbox | If Yes, enter name and quantiy
checkpoint-status |  |  | checkpoint | Test the water conditions at the completion of the circulation.
checkpoint-status |  |  | checkpoint | Water sample is taken, and labeled as "End of Flushing" and dates.
text | 52973bee-1973-5aa2-a730-4c9e72666a69 |  | textbox | Enter Date & Time
checkpoint-status |  |  | checkpoint | Sulphate
text | 41e5b02b-0578-5daa-8f6d-b0ffff96cc9c |  | textbox | Site measurement
text | 4b0274f2-9cb0-53a2-82e0-e46b84208ae7 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Chloride
text | e38846f7-9236-58ba-ba00-a9625d274a7a |  | textbox | Site measurement
text | e574bfa0-af43-5051-a146-29f32a699f1b |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | pH
text | 399264b2-0a5f-520e-ab97-fbcbbf1440af |  | textbox | Site measurement
text | ddb30371-437e-5156-9124-7be03eff08a6 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Conductivity
text | 0398f88f-0c8b-5344-8660-1f8f0521ed48 |  | textbox | Site measurement
text | bb47ccb2-89c8-5f4a-a71d-7c323b289981 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | 482a9d57-627b-5991-8348-6dba1db0287e |  | textbox | Site measurement
text | 9bcedf1f-fb4e-5eb8-9325-ba46ae185cb4 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TVC (Total viable count: the total numbers of microorganisms, such as bacteria, yeast or mould species)
text | 734e441d-d581-5b86-80e1-1db8add6601a |  | textbox | Site measurement
text | 0358fb07-19f9-523f-a938-7eb45c15d9dc |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Pseudomonads (microorganism that can create biofilm)
text | 0b49e7cf-4d6e-555b-9746-b4b05772eb46 |  | textbox | Site measurement
text | dfcee5d5-b006-5a09-b305-91902cf08fac |  | textbox | Lab test results
checklist-flat | 5e84437d-70fd-4c97-8ded-886705d6182d |  | checklist | Mechanical Services HHW and CHW Water Reticulation |  |  |  |  | Yes | Mechanical Services HHW and CHW Water Reticulation | 7cf706b0-95ed-4830-b2f2-5bfd644f5435
checkpoint-status | 037fb15b-7545-4ed5-b38a-b489084ff84e |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 022f9188-428d-48f8-ad63-73250c555d5b |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | ae72e5c6-ec24-4d46-9ddb-f4faaeb46a85 |  | checkpoint | Confirm trench depth, width and pipe alignment.
label | c25f20c8-ec2e-52b3-aeb6-513d360edc70 |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | b151d6d8-768f-54bd-bee8-2e530404fa3a |  | note | QA documents to be provided prior to installing pipework in trenches. CPB to provide to AE Smith.
checkpoint-status | 9f6cb27c-719b-4b63-a680-9a7ad397c23f |  | checkpoint | Heat Shrink Weld
checkpoint-status | 8fae5aab-4b4c-48f7-b7cc-48131b5f2fef |  | checkpoint | Number of pipe dimensions shown on the drawings.
checkpoint-status | 453a7a67-a625-44c3-8d6f-4a6fe2b938b9 |  | checkpoint | Location of pipes shall be shown on the drawings.
checkpoint-status | 432da7fa-4d1a-4f3d-ab0c-f5bee7747db5 |  | checkpoint | Welding of pipework
label | a663fd0e-27f8-566d-8397-efa1666feac4 |  | note | Joining of steel pipework to be welded as per approved Welding Procedure Specifications (WSP)
checkpoint-status | 2a2e6ed5-6bb1-43bb-b295-8be068cd6f63 |  | checkpoint | Installation of valves
label | 19971166-4a3c-5cc4-8f94-3e87c0f197e2 |  | note | Install valves as per construction drawings
label | 9d1190e9-4de2-5d2d-8caa-6d836bc91e1a |  | note | Lockable toby boxes installed for in-ground valves.
label | d063aec4-bc77-577b-a43a-f892864df3dc |  | note | Correct gaskets installed
label | 37e457a0-6db5-568d-a8d9-daaf607af52e |  | note | Flange bolts tightened in correct tightening sequence.
checkpoint-status | f4f09402-dddf-4f27-bfd2-33d1ad32d0d6 |  | checkpoint | Install Thrust and Anchor Blocks
label | d47e3c17-67a6-5a98-bcc5-d62d3b7913ff |  | note | Minimum dimensions as per IFC drawings.
label | 4ed2b514-fbd7-5e97-a114-e87227bf3050 |  | note | A protective Denso or black coating membrane is to be installed around the pipe and the concrete anchor/thrust blocks to prevent abrasive damage.
checkpoint-status | c4af72b7-c82e-4c22-a9ae-0573ce278049 |  | checkpoint | Installation of Expansion Loops
label | 10f76f8a-fab2-558d-8178-4360f4dbf503 |  | note | Expansion Loops installed as per IFC drawings.
label | aeaed531-b633-5357-b098-f092aec87680 |  | note | Correct dimensions for inner smaller loop as per IFC drawing.
checkpoint-status | 622bcb6f-97d2-44fd-b8f4-bacfca000a6b |  | checkpoint | Inspection of Insulation
label | 976e243b-9583-5cb3-a1eb-f9619036336a |  | note | Inspect insulation for damage
label | e167b5d7-dbe3-5c9e-9411-8687acdd0c2a |  | note | Confirm Insulation is 50mm as per IFC drawings.
checkpoint-status | 9e095f0b-ba89-4d03-9128-a98decdeacbe |  | checkpoint | Installation of Pipework Marking Tape.
label | 6a629d64-6d83-506a-9b1e-37c6d92b7cb7 |  | note | Flow and Return direction arrows installed on all pipework.
label | 75688fa1-c21c-5bc7-ae64-fff0f2a7009e |  | note | Install detector tape 200mm below existing ground level
checkpoint-status | 0b5602c7-4932-4c75-a097-597179637a73 |  | checkpoint | Protection of In-ground bolted flange connections.
label | 559bfa31-b46f-5728-b477-9d307ee6e3b3 |  | note | All in-ground bolted flange connections are to be cladded and foam filled.
checkpoint-status | 947255da-a542-4703-bb14-6fd7ce9a93f5 |  | checkpoint | Completed Construction Pressure Testing with Air at 750 kPa for 4 hours.
checkpoint-status | 9dfb0389-ca3f-41d3-9e23-531ed48f72fe |  | checkpoint | Pre-Pipework Pressure Testing Inspection
label | f2cd7b67-de1d-5396-8d83-bd20ff6b1991 |  | note | Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | 90bb3284-9e41-551a-8b2a-88825dad8c14 |  | note | Ensure each test length is capped and ball valve installed.
label | a46c0cbb-e3fa-56c9-9519-f826233ed6a3 |  | note | Ensure all valves in the system are in the correct position and tagged “DO NOT OPEN” or “DO NOT CLOSE”
label | 67719617-bf11-5890-a9c4-648c6e93d63b |  | note | All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing.
checkpoint-status | 97aa2d84-8517-4d52-b830-30b59bdfd448 |  | checkpoint | Introduction of Air to 300 kPa
label | 297b1b2f-8585-56ba-adf2-8114f20a21ce |  | note | Gradually introduce air into the system to a pressure of 300 kPa and hold for 1 hour.
label | cc4c8556-c9ba-5376-8af2-a7b28b6b7742 |  | note | Monitor for any drop-in pressure.
label | 092f719a-35e7-5b5c-a92a-6e2c721ed40f |  | note | If a leak is identified discharge the air prior to rectifying any leaks.
checkpoint-status | 9ccfaec6-99ef-4394-8171-f8f077009f11 |  | checkpoint | Increasing Test Pressure
label | 2aa63c59-44e2-596c-9f98-725044d652a7 |  | note | If no leaks are identified Increase pressure by 10% increments until test pressure is achieved. Test will begin when pressure reaches 750kPa
checkpoint-status | db77eabc-c134-4bc1-878d-f809bc6dd9ab |  | checkpoint | Pipework Pressure Test Report Completed
checkpoint-status | b7ae5824-0dee-424a-88a3-1c7dd9379ca2 |  | checkpoint | HDPE Jacketing
label | 74142863-9e3b-58ca-854d-93ff91c9f181 |  | note | In situ HDPE jacketing at pipe joints to be completed only after pressure testing is completed and the welds have been checked.
checkpoint-status | c04eac8d-029f-448e-89ec-e289470a8974 |  | checkpoint | As-Builts Completed.
holdpoint | da24fd63-2a6e-4a3a-8596-2024d0f305d5 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 280402e9-0cf3-421d-83a9-a5c1ef65eb7a |  | checklist | Combined Services HDPE Natural Gas Installation V2 |  |  |  |  | Yes | Combined Services HDPE Natural Gas Installation V2 | 8e1d7484-6efb-45c6-bced-9ea574003ae5
checkpoint-status | 5ccc71ca-afef-42c4-84fc-e5652c0c0f08 |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | e3801910-4468-435d-8875-51a676904d81 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | 5938c1be-7848-4b6a-bbef-2d50141ab746 |  | checkpoint | Confirm trench depth, width and pipe alignment.
label | 7ce130fe-dcc6-5d8c-946a-66734c5efcd9 |  | note | QA documents to be received from sub-contractor prior to installation of conduit in trench.
checkpoint-status | 8b897e5b-55ba-450c-8744-bd65348bf275 |  | checkpoint | Number of pipe dimensions shown on the drawings.
checkpoint-status | 25612ac6-ed5e-4a80-87c0-ae3aa0c69a06 |  | checkpoint | Location of pipes shall be shown on the drawings.
checkpoint-status | 42f8b78e-bba8-406b-bcb5-6f243a987534 |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
holdpoint | 542e0144-2661-4753-b07e-136fc26c9df6 |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 613c3028-b1d1-4067-b736-bb6a5201effc |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | a6b5cd37-0e79-424c-870a-5ca17db8d528 |  | checkpoint | Installation of Valves
label | 137e25a4-5153-5f0e-8eb6-41ff1d402454 |  | note | Valves Installed as per approved drawings
label | 9eb75998-efe2-5776-93b1-8dd127338e46 |  | note | All works have been completed by a registered gas fitter ?
holdpoint | 50aa917e-a657-4f19-b102-6866ecd21833 |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 1b7782c1-77b8-4894-94a6-36d9f31e0824 |  | checkpoint | Pipework Pressure Test Report Completed ?
checkpoint-status | 4d752403-1d7c-4b54-9e41-a0dccab6ce11 |  | checkpoint | As-Builts Completed.
holdpoint | 95bf28d5-0c49-4e4b-a95b-da1086faf027 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 7a5d6761-6022-48ab-bc58-643bd116f718 |  | checklist | Seismic Joint Building Connection |  |  |  |  | Yes | Seismic Joint Building Connection | 99f90d07-659f-4092-ae8a-73f7205fe565
checkpoint-status | 051b447e-9569-4ed7-85dc-5cb07aa62dc3 |  | checkpoint | Waterproofing
checkpoint-status | 8094a051-a210-4548-a9c0-0404aac2be84 |  | checkpoint | Insulation
checkpoint-status | b2eed668-0df7-4902-b2a3-56f89abd8a76 |  | checkpoint | Victaulic Coupler
checkpoint-status | c76eecf7-a159-4973-a332-d63ccca65c3a |  | checkpoint | Installed Correctly
holdpoint | 34241939-5483-43b5-bc23-11034c43aa30 |  | signoff | CPB signoff
checklist-sectioned |  |  | checklist | Communications Underground Fiber Micro Duct |  |  |  |  | Yes | Communications Underground Fiber Micro Duct | 9b4b7f65-d129-4870-8259-ac81eded35c9
checkpoint-group |  |  | section | Approval
checkpoint-status |  |  | checkpoint | RDM & Consent Approval received by the client and approved?
checkpoint-status |  |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-group |  |  | section | Location
checkpoint-status |  |  | checkpoint | As shown on the drawings
checkpoint-status |  |  | checkpoint | Instructed by CPB Rep. as to best suit the conditions on the Site at the time of construction
checkpoint-status |  |  | checkpoint | Confirm trench depth, width and micro duct alignment, QA documents to be received from sub-contractor prior to installation of conduit in trench
checkpoint-status |  |  | checkpoint | Bottom of the trench shall be compacted to form a firm uniform surface free from loose material.
checkpoint-status |  |  | checkpoint | Number of micro duct dimensions shall be shown on drawings.
checkpoint-status |  |  | checkpoint | Location of micro shall be shown on the drawings.
checkpoint-group |  |  | section | Bedding of Microduct
checkpoint-status |  |  | checkpoint | Duct shall be bedded on approved bedding material
checkpoint-status |  |  | checkpoint | Bedding material shall be 150mm above top of duct
checkpoint-status |  |  | checkpoint | White marker tape installed with the words
checkpoint-status |  |  | checkpoint | WARNING - Communications cable buried below laid in the trench 150mm below ground level.
checkpoint-status |  |  | checkpoint | As-built drawings completed
checklist-flat | b9105d1f-37c2-4236-8a70-70e4feb899b7 |  | checklist | AECOM Combined Services HDPE Domestic Cold Water Pipework Installation |  |  |  |  | Yes | AECOM Combined Services HDPE Domestic Cold Water Pipework Installation | a8dd93c2-9fa5-4ff0-929a-0f9801d67e39
checkpoint-status | e4e64b97-52cf-45bc-869e-c57ec8ed8771 |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 8b8d8a6b-74a4-4c28-b0b8-c4642fe3e978 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | 0fca93a8-84dc-4ec1-9fb1-2b50a1344bd7 |  | checkpoint | Inspect trench depth, width and pipe alignment
label | edb6e2ab-ad29-5a75-8148-30348da1c006 |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | 9f237b1b-16b0-5c9c-a9bf-2c67dee60fa3 |  | note | QA documents to be provided prior to installing pipework in trenches . CPB to provide to AE Smith.
checkpoint-status | 55c4b252-44cc-4bca-b1c7-1cea09dc6797 |  | checkpoint | Number of pipes and dimensions of pipes shall be shown on the drawing
checkpoint-status | 53478528-8355-4e59-81ac-5d32b6eebd62 |  | checkpoint | Location of pipes shall be shown on the drawing
checkpoint-status | cbf97e7f-17e1-4ca7-a775-d9b4a3c04d87 |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
checkpoint-status | fcf6181a-61c0-451b-9776-790567cbc483 |  | checkpoint | Joining of pipework only to be done by Rotable steel flanges and EF Coupling.
checkpoint-status | 7d421d9b-af0f-4380-8491-580abe44550e |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | b73c79e4-a1af-49fc-97e7-ebfed4925ad0 |  | checkpoint | Install , valves , tees and bends
label | 953a6533-c63d-5d81-ad26-5349ee70a3e3 |  | note | Connections are installed as per construction drawings ?
label | d277ee34-1275-5944-a96d-abbf6eb0609f |  | note | All valves 100mm and above have a 1050 manhole ?
checkpoint-status | 355775f1-5c02-4bc8-aa0b-519d14cbe3af |  | checkpoint | Install Thrust and Anchor Blocks
label | 52aef6fe-31a9-5cd7-9a6f-de54041e88d3 |  | note | Minimum dimensions as per IFC Drawing
label | 4e070d35-b635-5e8c-9ae8-7cfd4801b39f |  | note | A protective Denso or black coating membrane has been installed around the pipe and the concrete anchor / thrust block to prevent abrasive damage ?
checkpoint-status | 6360c5f7-541d-44d2-a082-e912bb31dbcb |  | checkpoint | Installation of Trace Wire
label | 135a1e63-0e25-58c0-8c2a-62fbba11412d |  | note | Install Tracer wire as per Specification 5.21 of the Hydraulic Services Specification and ensure tracer wire is continuous between valves and any excess coiled.
label | e768983c-da82-5038-82a5-75334ae81ff2 |  | note | Test Trace Wire as per Specification 5.20.4
checkpoint-status | fa9d7ce6-a539-4472-9b7f-8ebba00dafb7 |  | checkpoint | Completed Construction Pressure Testing with Air
checkpoint-status | 9bb315da-14cd-4d8d-a4e3-1149b37f515a |  | checkpoint | Pre-Pipework Pressure Testing Inspection
label | 5ccfc376-0079-5abb-9050-2063c1abe3af |  | note | Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | a82dfe3b-b17b-512f-a3c5-5bf67ef0ac53 |  | note | Ensure all valves in the system are in the correct position and tagged “DO NOT OPEN” or “DO NOT CLOSE”
label | 05ded2ac-d02d-563a-98a4-91fdc520b3b5 |  | note | All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing.
checkpoint-status | d51cde8d-f9a2-419b-b0ea-38fff916f20a |  | checkpoint | Introduction of Air to 300 kPa
label | 11da5df0-9bd1-5bbf-a09f-05d9f29e8b18 |  | note | Gradually introduce air into the system to a pressure of 300 kPa and hold for 1 hour.
label | 3b7a3c9f-7244-5232-8367-faf552e02b29 |  | note | Monitor for any drop-in pressure.
label | 4bb5bfa3-6b6b-56c3-928b-0ec794005189 |  | note | If a leak is identified discharge the air prior to rectifying any leaks.
checkpoint-status | b45e64dd-0a51-4fdf-b3e0-fbf7014271f0 |  | checkpoint | Increasing Test Pressure
label | d8157463-5d4c-553e-9c33-0622b9e56fff |  | note | If no leaks are identified Increase pressure by 10% increments until test pressure is achieved.
checkpoint-status | 56eaa2ce-7f14-42d1-a2c4-cc5b980d0fd2 |  | checkpoint | Pipework Pressure Test Report Completed
checkpoint-status | c195a4d7-c1cd-4f46-aae3-317f0aea54ed |  | checkpoint | As-Builts Completed.
holdpoint | 20dc41e7-669f-4440-84a0-74de6e6d4be2 |  | signoff | Request Signoff/ Raise Remedial
checklist-sectioned |  |  | checklist | Ductwork Leakage Test Certificate |  |  |  |  | Yes | Ductwork Leakage Test Certificate | b736f61b-1b40-42c2-8c76-903a9a5321f9
checkpoint-group |  |  | section | Part 1- Physical details
checkpoint-status |  |  | checkpoint | Physical details captured correctly
label | c95af755-cc38-5396-8aaa-12ca63dfc783 |  | note | The issue of this certificate is notification that this sytem has passed and ready for witnessing. Its is to be witnessed within 7 days following the test.
text | 5d020693-ab62-5478-868d-15de08c441a8 |  | textbox | Section of Ductwork Tested
text | 701dec88-9ec7-5724-9712-556fc6258e27 |  | textbox | Test Standard, Class & Pressurisation
text | 698f5e22-b1bd-5322-ad2b-7610fa7a4c21 |  | textbox | Test Static Pressure (Pa)
text | d545571d-0274-56c3-9cf7-3859199d3248 |  | textbox | Leakage Factor (l/s/m²)
text | 4d596cd4-5373-53db-b3d9-ec4efaae4fb2 |  | textbox | Surface area of duct under test (m²)
text | 6d36a571-b43d-53ac-932c-a837f6f62e6d |  | textbox | Maximum permitted leage (l/s)
checkpoint-group |  |  | section | Part 2 - Results
checkpoint-status |  |  | checkpoint | Part 2 Completed
text | fdb87a2f-633e-5f72-9636-70a466965f93 |  | textbox | Test Rig Details
text | 38f3d419-3b62-5210-a8c6-7fb60579a32f |  | textbox | Test Instrument Manufacturer / Model
text | d5977c1d-01df-5508-9446-f82370680a92 |  | textbox | Serial number / Calibration date
text | 75b2f916-c1a3-5774-8b8f-7000774b1f8a |  | textbox | Actual Duct Static Pressure (Pa)
text | c4b55c7c-88d6-583a-ac70-654f970edb65 |  | textbox | Actual Airflow Leakage Rate (l/s)
text | 04e42a95-145d-5201-a5c7-f0b0f445468e |  | textbox | Calculated Leakage rate per m2 (l/s/m²)
text | 29aa2958-d3de-567b-b87e-30b5d314522f |  | textbox | Duration of test ( Airflow reading taken at end of test duration )
text | 97745ebd-8cd2-5d2c-87f3-7b07a0f13688 |  | textbox | Test Outcome
checkpoint-group |  |  | section | Sign Off
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
checkpoint-status |  |  | checkpoint | Signed off By Witness
text | 2828bbc7-e437-504a-9810-320f616133a0 |  | textbox | Witness Name
checkpoint-status |  |  | checkpoint | Signed off by Consultant
text | 523942f7-068d-5f72-bc72-14c484d70b23 |  | textbox | Consultant Name
checkpoint-group |  |  | section | Photos
checkpoint-status |  |  | checkpoint | Start of Pressure test
checkpoint-status |  |  | checkpoint | Pressure test after recorded Duration
checkpoint-status |  |  | checkpoint | Photos Attached
checklist-flat |  |  | checklist | Flushing Preparation Checklist |  |  |  |  | Yes | Flushing - Flushing Preparation Checklist | d209a62f-4c72-431d-94a9-dbfe367d2598
checkpoint-status |  |  | checkpoint | Differential pressure manometer
text | 9c8f765a-8c56-5430-814f-e7829c40f7ec |  | textbox | Model Number
text | 37abac2c-3bad-5887-b1ad-72348facb843 |  | textbox | Serial Number
checkpoint-status |  |  | checkpoint | HydROtwist Portable Digital PH Test Meter
checkpoint-status |  |  | checkpoint | HM Digital Hand Held TDS Temperature Water Test Meter TDS-3
checkpoint-status |  |  | checkpoint | Hm Digital Hand Held Conductivity & Temperature Meter EC-3
checkpoint-status |  |  | checkpoint | 0-14 pH test strips
checkpoint-status |  |  | checkpoint | High level 200 ppm chlorine test strips
checkpoint-status |  |  | checkpoint | Low level 4 ppm chlorine test strips
select | 768cfa8a-a7ff-5f4f-a986-3301f5d356fd |  | dropdown | Flushing pump | Temporary pump,system pump
checkpoint-status |  |  | checkpoint | Pump is available to run under VSD control.
checkpoint-status |  |  | checkpoint | Pump is wired and ready to be turned on.
checkpoint-status |  |  | checkpoint | Strainer basket(s) is installed with commissioning mesh. / skimmers socks installed.
checkpoint-status |  |  | checkpoint | Skimmers sock is installed on the strainers.
checkpoint-status |  |  | checkpoint | Schematic and layout drawings are available and studied.
checkpoint-status |  |  | checkpoint | Isolation valves are installed at each terminal.
checkpoint-status |  |  | checkpoint | Balancing valve is installed at each terminal.
checkpoint-status |  |  | checkpoint | Balancing valves are used to measure waterflows
select | ff27bd34-3774-55a2-b4c2-cd7427cee4e6 |  | dropdown | Any additional method to measure /confirm flushing waterflows. (flushing velocities) | Pump curve,Ultrasonic flow meter,Main Branch valve
checkpoint-status |  |  | checkpoint | Chemicals available on site as detailed in the
checkpoint-status |  |  | checkpoint | Piping system has been pressure tested and passed.
checkpoint-status |  |  | checkpoint | System has been installed as per drawing and schematic. If not mark-up the drawing and upload here.
checkpoint-status |  |  | checkpoint | All high points have air vents installed
checkpoint-status |  |  | checkpoint | All low points have drain cocks installed.
checkpoint-status |  |  | checkpoint | Mains water / make-up water supply pipe is connected at the suction side of the pump downstream of the drain port.
checkpoint-status |  |  | checkpoint | Mains water pipe connection size is 40 mm or bigger.
checkpoint-status |  |  | checkpoint | Mains water pressure is minimum 1.3 Bar at flow.
checkpoint-status |  |  | checkpoint | A backflow prevention valve (check valve) is installed at the mains water supply valve and it is certified.
checkpoint-status |  |  | checkpoint | A local drain is available in the vicinity of the flushing pump.
checkpoint-status |  |  | checkpoint | The drain pipe minimum 40 mm size is connected upstream of the strainer.
checkpoint-status |  |  | checkpoint | A high volume of contaminated water is to be discharged to the sewer drain. A discharge consent is not required and the discharge limits are recorded below in the note sections.
checkpoint-status |  |  | checkpoint | A special council discharge (trade waste water) consent is required and obtained. A copy of permit is attached. The discharge limits are recorded below in the note section.
checkpoint-status |  |  | checkpoint | Sensitive equipment as listed below are isolated (by-passes), and not included in the dynamic and chemical flushing processes.
checkpoint-status |  |  | checkpoint | Coils
checkpoint-status |  |  | checkpoint | Control valves
checkpoint-status |  |  | checkpoint | Heat exchangers
checkpoint-status |  |  | checkpoint | Condensers
checkpoint-status |  |  | checkpoint | Evaporators
checkpoint-status |  |  | checkpoint | Cartridges from any auto-flow control valves
checkpoint-status |  |  | checkpoint | 15 L dosing pot is installed and connected
label | 4e8f86a4-55c4-55ff-b5c6-2afa818aa6e0 |  | note | BSRIA BG 29/2012 recommends make up water quality as below. Label the sample bottle as "Make-up water sample" and date it.
checkpoint-status |  |  | checkpoint | Sulphate
label | f9856671-45e5-5462-b582-5caee790f42e |  | note | Recommended: <250 mg/L
text | 69b4174c-befd-5940-8019-308d83847828 |  | textbox | Site measurement
text | cb99fd52-3e5d-5288-ba61-d8ff19f2b1b1 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Chloride
label | df90db93-8f87-5841-8587-d1cb3e21905a |  | note | Recommended: <250 mg/L
text | f8a12740-9eff-5169-9d7a-44db691dd9c0 |  | textbox | Site measurement
text | b3a772b5-a38c-52c0-a358-6485c4e33f93 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | pH
label | 528d9963-812a-5b77-a118-7ce0948c70b0 |  | note | Recommended: 6.0 < x < 8.5
text | 3a479036-efb3-5459-b98e-4af7e2f6cc18 |  | textbox | Site measurement
text | bd3d4034-25a3-503a-9956-88cca4278c10 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Conductivity
text | 73e23c30-1960-541e-bc52-b17c8747bb54 |  | textbox | Site measurement
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | d56a3d80-f1e0-57af-b32c-96b23e1659b9 |  | textbox | Site measurement
checkpoint-status |  |  | checkpoint | TVC (Total viable count: the total numbers of microorganisms, such as bacteria, yeast or mould species)
label | b04808f0-882c-59d3-8509-01d5075d0a8f |  | note | Recommended: <10000 per ml
text | f5c0f427-028b-5c15-b279-7c04babe5654 |  | textbox | Site measurement
text | 30d7e6f3-32f1-5abf-b84d-674c565d51cb |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Pseudomonads (microorganism that can create biofilm)
label | e180c9f5-9f5a-565f-9df5-2686d149e6b7 |  | note | Recommended: <10 per ml
text | 4b8444ad-923f-570f-a58b-0321532a6322 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | System filled with make-up water
checkpoint-status |  |  | checkpoint | Date
checkpoint-status |  |  | checkpoint | Make-up water connection location
checkpoint-status |  |  | checkpoint | Mains water pressure (kPa)
checkpoint-status |  |  | checkpoint | Water drained from furthest terminal until clear water is visible.
text | 69a66e97-1352-5bd1-bc72-dbd5a6e80ef5 |  | textbox | Drain waterflow (l/s)
text | 7d2bddd2-2b77-5196-be0e-e279a30b019c |  | textbox | Drain location
text | 8dbef6a8-2f8a-54c3-a848-c8c1a3d44d0c |  | textbox | Drain duration (minutes)
text | d30131dc-095f-5061-a74f-e281c3374d55 |  | textbox | Calculated drain water volume (L)
checkpoint-status |  |  | checkpoint | Special trade waste water permit obtained.
checkpoint-status |  |  | checkpoint | Water drained from all other location same as above
checkpoint-status |  |  | checkpoint | Air vent from all high points.
checklist-flat |  |  | checklist | Chemical Flushing Checklist |  |  |  |  | Yes | Flushing - Chemical Flushing Checklist | db610477-7cd1-4b8f-aac4-c233de373004
checkpoint-status |  |  | checkpoint | Uploaded highlighted drawing.
text | d8057836-2670-505f-8dbc-0e210d3da21c |  | textbox | List the zones / terminals / branches flushed during this step.
checkpoint-status |  |  | checkpoint | Confirm all other terminals isolated
checkpoint-status |  |  | checkpoint | Test the water conditions prior adding chemical
checkpoint-status |  |  | checkpoint | pH
text | 1291fd88-4b0c-5216-9cfb-da2bcd3e1d5b |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Conductivity
text | 553c851b-9f54-5c5a-b7ec-5f4b1e14f43f |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | 73397227-eb48-5f6a-b09a-f0ce4e04e37c |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Chloride
text | b3230d25-d131-57fe-b696-0d7298a2b9b9 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Pump is operating at 50 Hz.
checkpoint-status |  |  | checkpoint | Required cleaning chemical (L)
text | 10cee463-0fe7-5558-b3a1-f5ad68c1d257 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Cleaning chemical(s) added.
checkpoint-status |  |  | checkpoint | Name of chemical and SDS
text | deb5eafd-14d4-540e-8466-f9575f18e7fc |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Name of chemical and SDS
text | d4a93df9-11e5-5ee9-a48d-9a1af64cc92c |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Name of chemical and SDS
text | 75fe36a3-2301-5b1d-a519-61e760904595 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Circulate water 2 - 4 hours
checkpoint-status |  |  | checkpoint | Test the water conditions at the completion of the circulation.
checkpoint-status |  |  | checkpoint | pH
text | e56fe2e1-1097-500f-9f3c-8f829d8f6ff7 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Conductivity
text | b50191df-08ff-58cd-a929-e60f36574b2d |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | c14ba298-9b3f-5b92-ac21-ca7c8d8cfc6b |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Chloride
checkpoint-status |  |  | checkpoint | Photo of water sample at the end of the circulation before draining water.
checkpoint-status |  |  | checkpoint | Is there any neutralisation chemical added as per chemical specialist advise? If yes enter name and quantity
checkpoint-status |  |  | checkpoint | Record total and terminal waterflows on the "Flushing Water Flows" test sheet and upload here.
checkpoint-status |  |  | checkpoint | Clean strainers as required. Upload dirt and clean strainer photos here.
checkpoint-status |  |  | checkpoint | If this is last section to be flushed, then continue draining process.
checklist-flat |  |  | checklist | B5B - Line Valve Assemblies – Closure and Zoning Tests |  |  |  |  | Yes | B5B - Line Valve Assemblies – Closure and Zoning Tests | de6797db-b8b9-4930-af6e-8fdf943f800f
checkpoint-status |  |  | checkpoint | B5B - Line Valve Assemblies – Closure and Zoning Tests complete
text | 0b865fd8-807a-56fd-9c7d-9df1383f1a6d |  | textbox | Plant ref
text | 50591040-1290-5110-bc76-31a6cbb5f171 |  | textbox | Test by
text | bdd49dc8-7b4e-5665-905f-488027441404 |  | textbox | Test date
text | 72edb006-aad7-5b69-b6f4-4fed24ba72a6 |  | textbox | Revision
checkpoint-status |  |  | checkpoint | This is to certify that CLOSURE and ZONING of the LVAs was tested in accordance with paragraphs 15.63–15.65 on the pipeline system as follows:
text | 13613164-7825-573b-9290-2a2e1e24bf55 |  | textbox | LVA number
text | 42e6b72a-79db-5b0f-8c75-c44b259f68c3 |  | textbox | Test pressure (kPa)
text | 2bbf2656-8ffc-5975-b49a-dedf6a36d5e0 |  | textbox | Downstream/upstream pressure change after 15 min (kPa)
text | 74c5fe4f-4ad7-5626-999a-a29ee802107b |  | textbox | Terminal units controlled (total no)
text | ae79a404-c3c0-5e33-8051-77c18dcff3b6 |  | textbox | Terminal unit labelling
text | f261024d-2894-5679-a44f-ac73fba94266 |  | textbox | Contractors representative:
checkpoint-status |  |  | checkpoint | Sign Off Complete
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
checkpoint-status |  |  | checkpoint | Signed off By Witness
text | 480b0d8a-bfc8-511c-b940-e63fc17b41f4 |  | textbox | Witness Name
checkpoint-status |  |  | checkpoint | Signed off by Consultant
text | 4646063c-f8c9-5817-9f04-76aeb98e8073 |  | textbox | Consultant Name
checklist-sectioned |  |  | checklist | Combined Services - Heating Hot Water and Chilled Water Pipework Hydrostatic Pressure Test |  |  |  |  | Yes | Combined Services - Heating Hot Water and Chilled Water Pipework Hydrostatic Pressure Test | dedbefcb-af6f-4179-b62f-093e5a81a285
checkpoint-group |  |  | section | Details
checkpoint-no-status |  |  | checkpoint | Reference Documentation:
label | 22a27c7d-17cc-527f-9eaf-0fa66f268745 |  | note | Medium duty black steel to AS 1074
label | 35f9c70a-06c7-59a7-b138-29c8409e515b |  | note | Welded: To ANSI/API Spec 5L grade B.
label | e2ebbb2e-7220-5f46-820c-34879c6316c8 |  | note | Seamless: To ANSI/API Spec 5L grade B or ASTM A106 grade B.
label | 0e5e2b85-1d1f-5f74-8dbe-c72df6c4c605 |  | note | Standard: To AS 4041.
checkpoint-no-status |  |  | checkpoint | Project Specifications:
label | 063bed06-b857-5556-81ff-32213bfb4ef3 |  | note | NZT5007-STE-MSSP-0001
checkpoint-no-status |  |  | checkpoint | Drawings:
label | 27102b56-a06c-5d91-9c2a-fa63f81dca9e |  | note | AES-NZ1005-STE-SHD-MEC-1101-in sequence up to- AES-NZ1005-STE-SHD-MEC-1142
checkpoint-status |  |  | checkpoint | Prepared by:
text | 1d3fe4cc-4a1c-5da0-bfd9-bb100f262feb |  | textbox | Name:
text | 034c38fb-2e78-5c27-8f88-cf4224f53fc8 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Reviewed by: CPB Engineer
text | 021acdc9-f9f7-5bd4-8afc-2bafde4d25f9 |  | textbox | Name:
text | 0964ba3a-8680-59fb-841e-d00d9032d395 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Reviewed by: CPB QA Rep
text | ade30544-5833-5bcf-820e-b72f01b89e23 |  | textbox | Name:
text | d38332ae-c892-56bf-9dc8-70d50bda1bc8 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Reviewed by: CPB Completions Rep
text | 2c16a104-3c5c-5036-8463-f5b1c01d5ae9 |  | textbox | Name:
text | 36b56dfd-6a9e-5d60-8297-f90ab44c520a |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Reviewed by: Consultant (If applicable. N/A for Architects)
text | af3f5244-fc2d-51cf-bcfe-84221d69588a |  | textbox | Name:
text | fccf2193-5360-5055-962f-397742c10880 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Approved by: CPB SPE or higher
text | e3125728-8285-5af9-bfa1-090134ca12fa |  | textbox | Name:
text | 87c6c70a-e701-5b10-bff5-745f566b2adc |  | textbox | Date:
checkpoint-group |  |  | section | Preliminary Inspections and Tests
checkpoint-status |  |  | checkpoint | 1 - RDM & Consent Approval
label | 7bb975b5-8046-5eda-837e-e35e74c83193 |  | note | Responsibility - CPB
label | 2d8bdab6-17c7-5d42-811b-721b44101c81 |  | note | Specification Reference - RDM Tracker Consent Tracker
label | 9a62a6b2-44d4-554f-90d7-eb16b8a0e6a9 |  | note | Conformance Criteria - RDM approval tracker
label | e49db500-6631-5788-99bb-9f77c8a28ad5 |  | note | Consent approval tracker
label | 3639f811-dde8-5cee-969d-7e806f94ede4 |  | note | Method - Document Review
label | 9732e7c0-e266-5275-aae9-7130ab83189c |  | note | Frequency - By Building/Area
label | 49a3c978-a83d-5579-9250-0009c7523a40 |  | note | CPB - HP
label | 621ff52b-d925-542f-a063-f72d815281f8 |  | note | Records - Receipt of Approval by Client
holdpoint |  |  | signoff | CPB - HP
checkpoint-status |  |  | checkpoint | 2 - Define LOT Area
label | 7da66f88-28fd-5c15-83ba-ea18f441d493 |  | note | Specification Reference - IFC Drawings
label | a920cd7d-8ecc-5c24-befe-ada00dfe8ce3 |  | note | Conformance Criteria - Lot areas clearly defined
label | 407aaf4d-9eaf-58d8-bad8-beef069b43df |  | note | Records - LOT Map / Register
checkpoint-group |  |  | section | Quality Control Checklists
checkpoint-status |  |  | checkpoint | QUALITY CONTROL CHECKLIST – ATTACH ALL CHECKLIST TEMPLATES USED FOR THIS ITP
label | f69f4d90-37c6-57d8-af39-0dc01f8eba0d |  | note | *NAME OF CHECKLIST MUST BE INCLUDED ON ITP PART 1 LAST COLUMN (RECORDS OR CHECKLIST REFERENCE)
checkpoint-group |  |  | section | Lot Verification Checklist
checkpoint-status |  |  | checkpoint | Lot Verification
text | ed032731-6e17-50d2-a234-7742c29f7729 |  | textbox | Lot Number:
text | 4549b2fb-43a6-5cbf-aef3-08f0447a429e |  | textbox | Lot Description:
label | 2c15c791-de33-5b11-a03f-d6f466dc8158 |  | note | Note: Item / # records to be filled out by CPB Engineer - minimum is to match ITP, extra documents can be added
checkpoint-status |  |  | checkpoint | 1.0 - ITP / Quality Control Checklists
text | ca6e65b3-7c6d-5cc7-a967-5fb6e270f413 |  | textbox | Item
text | 9ecb1ad4-878f-5770-b3c1-75cc8693851f |  | textbox | Number of Records Required
text | da0ac52d-3110-5d91-90e9-3530b0ad1285 |  | textbox | LOT Subfolder No:
text | fb0326ce-10b0-5157-a970-bbb4af1794a3 |  | textbox | Remarks (initial / date)
checkpoint-status |  |  | checkpoint | 1.1 - ITP / Quality Control Checklists
text | bac63303-cc11-5bc0-b244-88ce8ce34827 |  | textbox | Item
text | 48b58649-2852-54cb-9f34-1123e37a5aeb |  | textbox | Number of Records Required
text | 54f289fe-8d23-5bf5-9702-5653de29904c |  | textbox | LOT Subfolder No:
text | 57ff40db-784a-549e-80c2-d8e8b4161402 |  | textbox | Remarks (initial / date)
checkpoint-status |  |  | checkpoint | 2.0 - Survey Results
text | 6bd40811-0129-5d93-b3fc-d2762addb505 |  | textbox | Item
text | f7d18893-8e29-5ae7-a064-a83fc418682e |  | textbox | Number of Records Required
text | 02b5bdaf-c7e6-50ed-9d81-cbae78113312 |  | textbox | LOT Subfolder No:
text | 5c165c1f-2bce-5264-b5b1-078caa919241 |  | textbox | Remarks (initial / date)
checkpoint-status |  |  | checkpoint | 2.1 - Survey Results
text | bbf0f8b7-1277-5b9d-8150-74bc2c259c65 |  | textbox | Item
text | 36178a5a-d0e2-55ee-94ed-56b15ea3668c |  | textbox | Number of Records Required
text | bdc733b4-3de5-50f0-bfe7-a51a2e5c22ae |  | textbox | LOT Subfolder No:
text | 36f1caed-45c4-5147-ba59-88b8e6e877ac |  | textbox | Remarks (initial / date)
checkpoint-status |  |  | checkpoint | 3.0 - Test Results
text | 20df3581-7bd1-5fbb-9eac-5ef900717b4a |  | textbox | Item
text | 143eb4ca-edc2-5115-b907-b50b111c810b |  | textbox | Number of Records Required
text | 0c0fe370-e5a3-5232-a5dd-07da3cddf09d |  | textbox | LOT Subfolder No:
text | 6a44f676-e740-51d5-b66a-c0dcd413e749 |  | textbox | Remarks (initial / date)
checkpoint-status |  |  | checkpoint | Conformance of Work Statement (if required ie if some docs not signed):
label | eeb45b55-54c5-5087-b857-81e483a5cbe9 |  | note | The works for this construction lot conforms in respects to the ITP.
text | bfb331a1-5632-5576-8cfc-ff500488f172 |  | textbox | Name:
text | 8935c577-c787-524f-a873-5ca2b5a88213 |  | textbox | Subcontractor:
text | 195ba56a-e4a5-5c27-a972-75bd400df5a4 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Conformance of Work Statement:
label | 9975f30c-630c-5290-ac48-f34dfa172331 |  | note | The works for this construction lot conforms in respects to the ITP.
text | c3658552-2753-5b4c-9e89-548deae9afed |  | textbox | Name:
text | 210c207e-1d7e-5626-a1f6-0b310682b7ae |  | textbox | Subcontractor:
text | 8761f1ed-e489-5353-ab5f-c64f0aa19054 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Conformance / Verification of Construction Lot Statement:
label | 49f71d63-db38-55e9-bcbf-262758e41a1e |  | note | This closed lot conforms in all respects with the standards and requirements specified in the Contract Documents. The lot verification records are complete and attached. Any non-conformances have been dispositioned in accordance with the contract requirements.
text | 146ea390-e7b3-5970-88dc-7ded82319c15 |  | textbox | Name:
text | 79303fa7-0100-5d15-b8b2-9502a8ed73c9 |  | textbox | Subcontractor:
text | 3efff00b-f872-593e-ba95-550026187079 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Quality Review:
text | 418d80dc-0e88-5356-a7b0-78d374c0ed8e |  | textbox | Name:
text | 97e7e928-0d85-5697-b962-cd30af1b4ed2 |  | textbox | Subcontractor:
text | 5061896c-719d-5e75-950a-6db10a284839 |  | textbox | Date:
checklist-flat | 1ff1eda9-e246-49ea-a63d-3f7a003a5cf1 |  | checklist | Electrofusion Welding |  |  |  |  | Yes | Electrofusion Welding | e00c3fcb-b742-46a8-a0d3-4bd7bb54b706
checkpoint-status | d12c9200-3934-4fd5-affd-13103cb9a054 |  | checkpoint | Welding details
select | e77830ce-f45a-55a8-8a52-5f6d69e4ba95 |  | dropdown | EF Coupler completed by and recorded. | Benjamin Habon, EB Lindayao, Jefferson Calla, Redennis Teves, Steve Reeves, William Sabino, Calvin Cheyne, Mark Bateman, John Chingkaw
label | 5fd56b78-e9f7-5af6-a50a-a60b0b6e3bcb |  | note | Fusion Machine Used - SR No 402-1348 Caldertech EF welder
text | 3fa48e41-db68-52ab-81c9-804fc5e2807e |  | textbox | Record EF Coupler Used (Size)
checkpoint-status | 1b9c4532-8cf6-4ea3-8480-c96ebb6cfb55 |  | checkpoint | Pipe surface free from scratches, deeper than 10% of the wall thickness ?
checkpoint-status | 7858b33b-4783-4870-b4ea-aed0845ff578 |  | checkpoint | Pipe scraped and marked ?
checkpoint-status | fa06c62f-e8b1-412f-9c43-6714ed83820c |  | checkpoint | Pipe surface cleaned with Isopropyl alcohol?
checkpoint-status | e4e0cca8-6df2-4a79-b3df-d2fd3da92938 |  | checkpoint | Barcode scanned by machine?
checkpoint-status | 2973a4d7-4cbd-4427-b90d-a928bb1181f2 |  | checkpoint | Record cooling time achieved?
checkpoint-status | 053000d2-41d2-4afd-b182-92257266546c |  | checkpoint | Details of E.F Coupler Operator
select | 25ea69af-78dd-5a8e-bc52-08898dcaa0f7 |  | dropdown | Name | Benjamin Habon, EB Lindayao, Jefferson Calla, Redennis Teves, Steve Reeves, William Sabino, Calvin Cheyne, Mark Bateman, John Chingkaw
holdpoint | c555ef4d-303c-46cb-954b-57b8228b5e25 |  | signoff | Signature
checkpoint-status | c2efb854-1674-40de-9085-fa6ab7efb7f1 |  | checkpoint | Post weld checks completed
holdpoint | c62849b8-1925-4dce-a8a5-ea4583b835af |  | signoff | Post weld checks by Client and AE Smith - Request Signoff
checklist-flat | 10ed7224-c711-4507-9897-7f27ab667212 |  | checklist | Combined Services HDPE Fire Pipework Installation |  |  |  |  | Yes | Combined Services HDPE Fire Pipework Installation | e09c19c4-f149-42ee-a51e-24c713d97a1c
checkpoint-status | 8022e9fd-0aa8-40e4-b447-451b1340c5ab |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 697497df-c6fd-4c50-a7ba-01daccadcc52 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | b7edc8b5-9cd9-4ab6-badb-3ce5419219ce |  | checkpoint | Inspect trench depth, width and pipe alignment
label | ba51a8d2-8504-5e37-b3ba-d1d60c9f3349 |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | b066f345-ca72-5060-aa63-a1d2218c4aad |  | note | QA documents to be provided prior to installing pipework in trenches . CPB to provide to AE Smith.
checkpoint-status | 8821beff-0771-4f4b-b472-80a336648a61 |  | checkpoint | Number of pipes and dimensions of pipes shall be shown on the drawing
checkpoint-status | 83f5d64d-2c67-449d-804e-409f76640c0f |  | checkpoint | Location of pipes shall be shown on the drawing
checkpoint-status | 19a7d8c9-46b4-45f7-8a92-80b7fba56b53 |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
checkpoint-status | 43e9ca16-c620-463b-a4e6-31ff9c21c8e2 |  | checkpoint | Joining of pipework only to be done by Rotable steel flanges and EF Coupling.
checkpoint-status | 675a37db-f46f-4999-844b-a19492446763 |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | 2e7c517a-6630-4d4c-9f35-c39b71dc9d99 |  | checkpoint | Installation of tees and bends
label | 5829e92a-c37e-5b9c-b12c-9750e2b9ec8a |  | note | Install all connection tees as per construction drawings
label | 6b3eea05-4075-56c7-94ff-341987301bca |  | note | Ductile iron bends to be installed on pipework above 300ND
checkpoint-status | bb98b517-ae47-44dd-9126-61d2f259c681 |  | checkpoint | Installation of Hydrants and Hydrant Valves
label | f3b2e1c5-8ef0-5303-9483-9a983e177ad6 |  | note | Mount hydrants on approved types of hydrant tees with risers if necessary so that the top of each hydrant is within 100mm of the finished ground surface level
label | 81829216-8aa1-5604-8fe9-c0a077d8703d |  | note | In-ground hydrants and hydrant valves are installed in secure toby boxes and on isolation spurs.
checkpoint-status | 4fd587cb-7603-4b00-83e1-e114d3ac1749 |  | checkpoint | Install Thrust and Anchor Blocks
label | dd6e72d1-065c-55b8-93e0-97ea38ddba0e |  | note | Minimum dimensions as per IFC drawings.
label | 9645f101-c57a-5f3b-bf48-2e5cbc987eda |  | note | A protective Denso or black coating membrane is to be installed around the pipe and the concrete anchor/thrust blocks to prevent abrasive damage.
checkpoint-status | 33bc3bce-aa56-4bb5-9420-3d899912c43d |  | checkpoint | Installation of Trace Wire
label | 5eeda8b3-da8c-5a3e-9923-82b712c44fd6 |  | note | Install Trace Wire and ensure tracer wire is continuous between valves and any excess coiled in valve box.
label | 2f79e2d4-5294-58e3-8f5e-b7d3b92ad862 |  | note | Test Trace Wire following installation.
checkpoint-status | 3c335720-2666-47ab-8c1e-0937e7627ff3 |  | checkpoint | Completed Construction Pressure Testing with Air
checkpoint-status | 737feebe-f37b-4742-8fbd-ad0653cea5f2 |  | checkpoint | Pre-Pipework Pressure Testing Inspection
label | 439a9998-c367-5685-8e62-fd18afcd4b86 |  | note | Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | 1d153018-38ac-5852-ae19-c7ec6607660b |  | note | Ensure each test length is capped and ball valve installed.
label | beff4f06-94da-5d94-83db-ef98f6d4004d |  | note | Ensure all valves in the system are in the correct position and tagged “DO NOT OPEN” or “DO NOT CLOSE”
label | 057e71b5-c379-52e2-8b62-bf8d89f736b6 |  | note | All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing.
checkpoint-status | 393f7ca7-7580-424b-acad-adf968ac53c5 |  | checkpoint | Introduction of Air to 300 kPa
label | 3815b57e-a832-56b4-9683-0ff70760e3cc |  | note | Gradually introduce air into the system to a pressure of 300 kPa and hold for 1 hour.
label | 269a0052-2d5a-5769-865d-5cdbb745c26c |  | note | Monitor for any drop-in pressure.
label | ffb241e8-2908-5f9f-b29e-e700fdf574b0 |  | note | If a leak is identified discharge the air prior to rectifying any leaks.
checkpoint-status | 30df5c34-da48-446e-be8d-a9f8b5337ebe |  | checkpoint | Increasing Test Pressure
label | 34bba2a1-fc69-5d6a-8b65-f2b4d5467462 |  | note | If no leaks are identified Increase pressure by 10% increments until test pressure is achieved.
checkpoint-status | 2c204f13-a04c-4849-a220-22c6afbe940c |  | checkpoint | Pipework Pressure Test Report Completed
checkpoint-status | cd4c256c-d202-4b65-b743-1cad32ad3393 |  | checkpoint | As-Builts Completed.
holdpoint | b5d480b0-8354-4f62-a3ba-04b22a6d7f1f |  | signoff | Request Signoff/ Raise Remedial
checklist-flat |  |  | checklist | Flushing Site Details |  |  |  |  | Yes | Flushing Site Details | e7978756-5687-4d53-acde-f3a59d7ceb67
checkpoint-status |  |  | checkpoint | Flushing Information collected correctly
text | bced8f71-be22-5b90-ad95-23be884c4a22 |  | textbox | Job number
text | 58d42d1b-3125-52f0-b0d5-95438dd39a11 |  | textbox | Job name
text | 734c6279-9958-533e-8802-4e9ee5c88429 |  | textbox | Builder
select | 20c7f828-b67c-52bb-822a-cf6c69a8f951 |  | dropdown | System Type | Domestic Cold Water, Chilled Water, Heating Hot Water, Low Temperature Heating Hot Water, High Temperature Heating Hot Water, Fire Hydrant
text | 4bfd2d78-679a-5962-9290-ec8077784b32 |  | textbox | System Volume (Litre)
text | e7434e49-60c3-5054-8408-0d50704d955a |  | textbox | Location
text | 504ade3c-3097-59bd-9eea-519b78be4477 |  | textbox | Drawing
boolean | 00a94e86-2473-5471-908c-940ccda162f7 |  | tickbox | CIBSE Commissioning Code W
boolean | c3616dd9-3cd7-51dd-a5df-43cd96225f5e |  | tickbox | BSRIA BG 29/2012
checklist-sectioned |  |  | checklist | AES-NZ1005-STE-ITP-PMT-0024 - DCW Pipework Hydrostatic Pressure Test |  |  |  |  | Yes | AES-NZ1005-STE-ITP-PMT-0024 - DCW Pipework Hydrostatic Pressure Test | f6c728bb-5846-40fb-87c0-a65a5f72c860
checkpoint-group |  |  | section | MATERIAL COMPLIANCE
checkpoint-status |  |  | checkpoint | RDM & Consent Approval
label | 5478e124-cf1e-55ba-bc86-7f5eee17e109 |  | note | CRITERIA - RDM approval tracker Consent approval tracker
holdpoint |  |  | signoff | CPB Hold Point Signature
checkpoint-status |  |  | checkpoint | General
label | 5a491135-34fc-5ea1-8d81-f8cb6a38b89c |  | note | CRITERIA - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
label | 44025ba1-7a0e-59cf-b21a-a8d7b869d9ad |  | note | • Specifications & QA Documents Approved
label | f956f66f-c7d1-5e7a-85b8-334368bb4f07 |  | note | • Drawings are confirmed
label | e0d21305-5a99-58b1-b386-959dd7350b87 |  | note | • Equipment fit for purpose
holdpoint |  |  | signoff | CPB Hold Point Signature
checkpoint-group |  |  | section | CONNECT PRESSURE PUMP TO DCW RING MAINS
checkpoint-status |  |  | checkpoint | Confirm Flushing & Disinfection of Pipework
label | a0249970-5137-58d0-9c36-abbd8c42c69e |  | note | CRITERIA - 1. Air should be removed at each building prior to the DCW water supply water entry assembly to prevent debris from entering building.
label | faadcc86-88f2-5117-8f78-c452ed3820c5 |  | note | 2. Ensure system sterilization completed.
label | ed709b78-d374-5bf6-8cb4-f021735f0b85 |  | note | 3. Ensure TNK filtration is cleaned/ inspected if not isolated from test.
label | e3b58431-a7c9-5e57-9487-728d000e009c |  | note | 4. Ensure all screens/ strainers are cleaned/ inspected if not isolated from test.
holdpoint |  |  | signoff | CPB Hold Point Signature
checkpoint-status |  |  | checkpoint | Accept delivery of pump to site
label | 2b06915f-b1a1-58a8-8197-7fcae002eb89 |  | note | CRITERIA - 5. Check pump is rated for pressure test
label | 3037c693-a888-532b-9c6a-3aedd4ca6343 |  | note | 6. Check all supplied attachments are correct and in good order
label | 8a9000e5-0d1d-53cf-b2cf-5480837ce73e |  | note | 7. Check fluid levels & fill as necessary
checkpoint-status |  |  | checkpoint | Isolate: Mains water Storage Tanks
label | e4983d6a-43b8-5304-9937-ffa7b8886515 |  | note | CRITERIA - 1. Check Mains water is isolated
label | 47370c62-c830-5713-ac69-b070e71f7340 |  | note | 2. Check Storage Tank is isolated
checkpoint-status |  |  | checkpoint | Connect pump to DWC ring mains
label | 5a21b3d9-d5f5-5db1-9692-813435cd5d9a |  | note | CRITERIA - Confirm connections are safe and correct
checkpoint-status |  |  | checkpoint | Connect calibrated gauges for pressure test
label | c62bf30f-7fc2-5373-bffe-6a924f29efa3 |  | note | CRITERIA - Confirm position is correct, gauge is in good order for test & calibrated
checkpoint-group |  |  | section | HYDROSTATIC TEST
checkpoint-status |  |  | checkpoint | Fill DWC ring mains with domestic water
label | 4d152ae4-5ff4-51ba-97d6-785d83046349 |  | note | CRITERIA - Completely fill closed loop system with water releasing all air from the Taps at each Building
checkpoint-status |  |  | checkpoint | Gradually increase system pressure to 1550kPa
label | 5284d731-45bf-591e-9be1-d996ef54480d |  | note | CRITERIA - Slowly raise system pressure to 1550kPa
label | 67fb1be6-d0ad-5bad-be3a-269d47c0991a |  | note | • Checking for any signs of leaks or pressure drops
checkpoint-status |  |  | checkpoint | Stabilize 1550kPa pressure (START WITNESSED)
label | 3c69cdc2-6c0a-56ce-bfa4-20b3150d4ea9 |  | note | CRITERIA - Record START time & photograph gauge
label | f4d887b1-12d4-5ec4-b1e3-ee72e280ffdf |  | note | • All relevant parties to witness starting pressure of 1550kPa
holdpoint |  |  | signoff | CPB Hold Point Signature
checkpoint-no-status |  |  | checkpoint | Stabilize 1550kPa pressure (START WITNESSED) - IR Hold Point Signature
holdpoint |  |  | signoff | IR Hold Point Signature
checkpoint-status |  |  | checkpoint | Hold 1550kPa pressure for 35min (END WITNESSED)
label | 6da4a585-dc90-56a1-bb88-209797d8322f |  | note | CRITERIA - Record FINISH time & photograph gauge
label | 504641c3-3955-5c32-b5e3-f6ed81eb72d8 |  | note | • All relevant parties to witness pressure of 1550kPa
holdpoint |  |  | signoff | CPB Hold Point Signature
checkpoint-no-status |  |  | checkpoint | Hold 1550kPa pressure for 35min (END WITNESSED) - IR Hold Point Signature
holdpoint |  |  | signoff | IR Hold Point Signature
checkpoint-status |  |  | checkpoint | Pressure released or reduced for next test
label | 61a33748-c3a1-5a7d-b0bb-a1dca40ee7ed |  | note | CRITERIA - Supervisor to ensure energy (pressure) is only stored while under test
checkpoint-status |  |  | checkpoint | Discharge pressure leave system in a safe state
label | daf9fc84-0752-5ad0-af70-06a044d64ec4 |  | note | CRITERIA - Discharge system pressure, ensure area is left in a safe state meeting site requirement
checkpoint-group |  |  | section | COMPLETION RECORDS
checkpoint-status |  |  | checkpoint | Testing Results
label | 3f506ff8-3e45-5862-a9fb-1527e459017f |  | note | CRITERIA - All pipework pressure test reports shall be provided
holdpoint |  |  | signoff | CPB Hold Point Signature
checkpoint-no-status |  |  | checkpoint | Testing Results - IR Hold Point Signature
holdpoint |  |  | signoff | IR Hold Point Signature