## res4
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | AES-NZ1005-STE-ITP-PMT-0024 - DCW Pipework Hydrostatic Pressure Test | [5 empty] | AES-NZ1005-STE-ITP-PMT-0024 - DCW Pipework Hydrostatic Pressure Test | 2805964d-0a41-4fd3-b4c8-60fcf2eedf6a
section | MATERIAL COMPLIANCE
checkpoint | RDM & Consent Approval
note | CRITERIA - RDM approval tracker Consent approval tracker
signoff | CPB Hold Point Signature
checkpoint | General
note | CRITERIA - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
note | • Specifications & QA Documents Approved
note | • Drawings are confirmed
note | • Equipment fit for purpose
signoff | CPB Hold Point Signature
section | CONNECT PRESSURE PUMP TO DCW RING MAINS
checkpoint | Confirm Flushing & Disinfection of Pipework
note | CRITERIA - 1. Air should be removed at each building prior to the DCW water supply water entry assembly to prevent debris from entering building.
note | 2. Ensure system sterilization completed.
note | 3. Ensure TNK filtration is cleaned/ inspected if not isolated from test.
note | 4. Ensure all screens/ strainers are cleaned/ inspected if not isolated from test.
signoff | CPB Hold Point Signature
checkpoint | Accept delivery of pump to site
note | CRITERIA - 5. Check pump is rated for pressure test
note | 6. Check all supplied attachments are correct and in good order
note | 7. Check fluid levels & fill as necessary
checkpoint | Isolate: Mains water Storage Tanks
note | CRITERIA - 1. Check Mains water is isolated
note | 2. Check Storage Tank is isolated
checkpoint | Connect pump to DWC ring mains
note | CRITERIA - Confirm connections are safe and correct
checkpoint | Connect calibrated gauges for pressure test
note | CRITERIA - Confirm position is correct, gauge is in good order for test & calibrated
section | HYDROSTATIC TEST
checkpoint | Fill DWC ring mains with domestic water
note | CRITERIA - Completely fill closed loop system with water releasing all air from the Taps at each Building
checkpoint | Gradually increase system pressure to 1550kPa
note | CRITERIA - Slowly raise system pressure to 1550kPa
note | • Checking for any signs of leaks or pressure drops
checkpoint | Stabilize 1550kPa pressure (START WITNESSED)
note | CRITERIA - Record START time & photograph gauge
note | • All relevant parties to witness starting pressure of 1550kPa
signoff | CPB Hold Point Signature
checkpoint-no-status | Stabilize 1550kPa pressure (START WITNESSED) - CPB Hold Point Signature & IR Hold Point Signature
signoff | IR Hold Point Signature
checkpoint | Hold 1550kPa pressure for 35min (END WITNESSED)
note | CRITERIA - Record FINISH time & photograph gauge
note | • All relevant parties to witness pressure of 1550kPa
signoff | CPB Hold Point Signature
checkpoint-no-status | Hold 1550kPa pressure for 35min (END WITNESSED) - CPB Hold Point Signature & IR Hold Point Signature
signoff | IR Hold Point Signature
checkpoint | Pressure released or reduced for next test
note | CRITERIA - Supervisor to ensure energy (pressure) is only stored while under test
checkpoint | Discharge pressure leave system in a safe state
note | CRITERIA - Discharge system pressure, ensure area is left in a safe state meeting site requirement
section | COMPLETION RECORDS
checkpoint | Testing Results
note | CRITERIA - All pipework pressure test reports shall be provided
signoff | CPB Hold Point Signature
checkpoint-no-status | Testing Results - CPB Hold Point Signature & IR Hold Point Signature
signoff | IR Hold Point Signature
checklist | AES-NZ1005-STE-ITP-PMT-0025 - Combined Services Fire Hydrostatic Pressure Test | [5 empty] | AES-NZ1005-STE-ITP-PMT-0025 - Combined Services Fire Hydrostatic Pressure Test | 45a5082c-ffa8-445d-9aa6-b205ae90f872
section | MATERIAL COMPLIANCE
checkpoint | RDM & Consent Approval
note | CRITERIA - RDM approval tracker Consent approval tracker
signoff | CPB Hold Point Signature
checkpoint | General
note | CRITERIA - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
note | • Specifications & QA Documents Approved
note | • Drawings are confirmed
note | • Equipment fit for purpose
signoff | CPB Hold Point Signature
section | CONNECT PRESSURE PUMP TO DCW RING MAINS
checkpoint | Accept delivery of pump to site
note | CRITERIA - 1. Check pump is rated for pressure test
note | 2. Check all supplied attachments are correct and in good order
note | 3. Check fluid levels & fill as necessary
checkpoint | Connect pump to Fire ring mains
note | CRITERIA - Confirm connections are safe and correct
checkpoint | Connect calibrated gauges for pressure test
note | CRITERIA - Confirm position is correct, gauge is in good order for test & calibrated
section | HYDROSTATIC TEST
checkpoint | Fill Fire ring mains with domestic water
note | CRITERIA - Completely fill closed loop system with water releasing all air from the Valves at each Building
checkpoint | Gradually increase system pressure to 15.5 Bar
note | CRITERIA - Slowly raise system pressure to 15.5 Bar
note | • Checking for any signs of leaks or pressure drops
checkpoint | Stabilize 15.5 Bar pressure (START WITNESSED)
note | CRITERIA - Record START time & photograph gauge
note | • All relevant parties to witness starting pressure of 15.5 Bar
signoff | CPB Hold Point Signature
checkpoint-no-status | Stabilize 15.5 Bar pressure (START WITNESSED) - CPB Hold Point Signature & IR Hold Point Signature
signoff | IR Hold Point Signature
checkpoint | Hold 15.5 Bar pressure for 4Hours (END WITNESSED)
note | CRITERIA - Record FINISH time & photograph gauge
note | • All relevant parties to witness pressure of 15.5 Bar
signoff | CPB Hold Point Signature
checkpoint-no-status | Hold 15.5 Bar pressure for 4Hours (END WITNESSED) - CPB Hold Point Signature & IR Hold Point Signature
signoff | IR Hold Point Signature
checkpoint | Pressure released or reduced for next test
note | CRITERIA - Supervisor to ensure energy (pressure) is only stored while under test
checkpoint | Discharge pressure leave system in a safe state
note | CRITERIA - Discharge system pressure, ensure area is left in a safe state meeting site requirement
section | COMPLETION RECORDS
checkpoint | Testing Results
note | CRITERIA - All pipework pressure test reports shall be provided
signoff | CPB Hold Point Signature
checkpoint-no-status | Testing Results - CPB Hold Point Signature & IR Hold Point Signature
signoff | IR Hold Point Signature