## Table 1
|  |  |  | Inspection and Test Plan - Control and Supervision of the Works | [10 empty] | Document # ITP-003
[15 empty] | Revision : 02 | Date : 21/03/2024
Client: |  | Yarra Trams |  |  | Construction Process: |  |  | Prepared by: |  | Reviewed by : |  |  |  |  | Approved by :
Project: |  | Victoria Street - Elizabeth to Swanston |  |  | Electrical and Communication Conduit |  |  | Name: | Cedric Guico | Name: |  |  | Rocky Sam |  | Name: | Shaun Kent
Contract No: |  | 8B5000 |  |  | Specifications: Yarra Trams Infrastructure - Tram Track Construction Standard (CE- 019-ST-0033)
[5 empty] | Structure / Component: Tram Tracks (Electrolysis, Platform Conduits) |  |  | Signed : |  | Signed : |  |  |  |  | Signed :
[5 empty] | Location: |  |  | Date : 17/07/2024 |  | Date : 17/07/2024 |  |  |  |  | Date : 17/07/2024
Lot No: Lot Details: Lot Size/ Quantity:
Item | Task/Activity Description |  |  | Inspection / Controls and Verification Detail | [5 empty] | HP/ WP/ AP/ IP/ TP/ SCP |  | Responsibility |  | Checked by:
No. |  |  |  | Frequency | Acceptance Criteria |  | Reference Documents | Inspection / Test Method | Record of conformity |  |  | Project Engineer Site Engineer Superintendent Surveyor Foreman |  | Client | Fulton Hogan | FH's Sub- contractor | Date
1 | Preliminary Works
1.1 | Check for correct documentation |  |  | Prior to commencing any activity | Employees and sub contractors shall be issued with the most current and complete construction drawings |  | Drawings and drawing registers | Visual inspection | This ITP signed off | HP* |  | Fulton Hogan Engineer |  | N/A |  | N/A
1.2 | Implementation of all measures and controls |  |  | Prior to commencing any activity | All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, JSEA, SWMS & WP |  | PSP, EMP, TMP, JSEA, SWMS, WP | Visual Inspection | This ITP signed off | HP* |  | Fulton Hogan Engineer |  | N/A |  | N/A
1.3 | Materials |  |  | Per Batch | • Electrical supply conduit to be Orange and rigid HD UPVC of sizes as required. • Communications conduit to be White and rigid UPVC of either 32 or 50mm size or larger as required. |  | CE-019-ST-0033 cl 4.4.1 AS 2053 | Verify | This ITP signed | HP* |  | Fulton Hogan Engineer |  | N/A |  | N/A
2 | Construction Works
2.1 | Survey set-out |  |  | As required | • Work is set out in accordance with drawings. |  | Work procedure | Verify | This ITP signed | HP* |  | Fulton Hogan Engineer |  | N/A |  | N/A
2.2 | Excavation and Trenching |  |  | Prior to Installation | • Minimum cover for underground conduits shall be 600mm • Open trenching only permitted in unpaved areas, line of trench to be at right angle to the track • Trench shall maintain a minimum clearance of 300mm from all existing services where possible |  | CE-019-ST-0033 cl 4.2.5 & 4.2.8 | Verify | This ITP signed | WP |  | Fulton Hogan Engineer |  | N/A |  | N/A
2.3 | Installation of Conduits and pits |  |  | Each Lot | • Conduits in the same run shall be spaced 50mm by using clean sand to pack voids Conduit shall be embedded in not less than 50mm sand and covered by >50mm - 75mm< sand • Mechanical protection shall be provided by installation of polymeric cable or cover strip of thickness not less than 3mm, and of a material equivalent of UPVC conduit complying to AS 2053. Protective material shall be placed not less than 100mm above the conduit, and shall not be less than 150mm wide. • Conduits shall be joined male to female ends and sealed with approved adhesive immediately prior to joining. • Conduits shall not be subject to construction loadings • Bottom of lowest conduit shall maintain a minimum 100mm above pit floor • Conduits shall be capped with UPVC electrical caps |  | CE-019-ST-0033 cl 4.4 | Visual inspection | This ITP signed | WP |  | Fulton Hogan Engineer/ YT |  | N/A |  | N/A
2.4 | Inspection of conduit installation |  |  | Each Lot | Laying of conduits and installation of pits shall be inspection by superintendent and conform to design drawings before any backfilling procedure is to commence |  | Work procedure | Visual Inspection | This ITP Signed | *HP |  | Fulton Hogan Engineer/YT |  | N/A |  | N/A
Item | Task/Activity Description |  |  | Inspection / Controls and Verification Detail | [5 empty] | HP/ WP/ AP/ IP/ TP/ SCP |  | Responsibility |  | Checked by:
No. |  |  |  | Frequency | Acceptance Criteria |  | Reference Documents | Inspection / Test Method | Record of conformity |  |  | Project Engineer Site Engineer Superintendent Surveyor Foreman |  | Client | Fulton Hogan | FH's Sub- contractor | Date
2.5 | Back Fill of Trenches |  |  | Each Lot | • Backfilling (for trenching or road crossings) - conduit trench shall be backfilled above marker tape with crushed rock or suitable excavated material and compacted to 90% standard compaction 150mm-200mm below sub base level, the last 150mm-200mm shall be compacted to 100% standard compaction using handheld mechanical plant |  | CE-019-ST-0033 cl 4.2.5 | Verify | This ITP signed | IP |  | Fulton Hogan Engineer |  | N/A |  | N/A
2.6 | Installation of Draw Cords |  |  | Each Lot | Draw wire shall be provided for each conduit, with extra 3m length at each pit, material to be used shall be 6mm 'telstra rope' |  | CE-019-ST-0033 cl 4.4.6.2 | Verify | This ITP signed | IP |  | Fulton Hogan Engineer |  | N/A |  | N/A
2.7 | Compaction |  |  | Each Lot | During compaction optimum moisture content of bedding and select fill is within 85% to 115% as provided by suppliers |  | CE-019-ST-0033 cl 4.2.8 | Verify | This ITP signed | HP* |  | Fulton Hogan Engineer |  | N/A |  | N/A
Final Inspection
The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
Print Name: |  |  | Position: |  |  | Signature: |  |  |  |  | Date: / /
Legend
HP | Hold Point | Work shall not proceed past the HP until released by the Superintendent |  |  |  |  | IP | Inspection point |  | Formal Inspection to be done and recorded
HP* | FH Hold Point | Work shall not proceed past the HP* until released by FHDB |  |  |  |  | TP | Test Point |  | Product compliance test to be undertaken and recorded/reported
WP | Witness Point | An inspection which must be witnessed by the Superintendent |  |  |  |  | SCP | Survey conformance point |  | A qualified surveyor to check product/section/structure and report
AP | Approval Point | Written or verbal approval given by the Superintendent