## ChecklistsITCs
Delete rows that aren't applicable to the project, then create the project breakdown and send to CONQA
type | name | values | prefix | postfix
checklist | Site Establishment and Safety Checklist | Pass, Fail
checkpoint | Delivery and goods lift location
checkpoint | Delivery requirements i.e. booking process
checkpoint | On site storage / office location
checkpoint | Site specific restrictions i.e. noise / starting times
checklist | Ductwork Checklist | Pass, Fail, N/A
checkpoint | Ductwork installed as per latest drawing
checkpoint | Inspect ductwork is not damaged. Record and report for any issues
checkpoint | Confirm correct spacing / supports installed
checkpoint | Duct flanges firmly bolted and sealed correctly
checkpoint | Cleats installed as required
checkpoint | Ductwork insulated where required and free of damage
checkpoint | Ductwork restrained for wind/seismic where required
checkpoint | Confirm ductwork joints and seams are sealed
checkpoint | Pops & flex installed as per latest drawing
checkpoint | Correct hanger spacing / supports installed for flex
checkpoint | Flexible duct connections completed correctly
checkpoint | Blade dampers installed as documented and left in the open position
checkpoint | BD pop access panel coordinated and marked
checkpoint | Cushion boxes installed as per latest drawing
checkpoint | Balancing dampers installed as documented and left in the open position
checkpoint | Volume Control Dampers installed as per latest drawing
checkpoint | Motorised dampers installed as per latest drawing / actuator fit off
checkpoint | Smoke dampers installed as per latest drawing / actuator fit off
checkpoint | Damper access panels coordinated and marked
checkpoint | Check all motorised dampers, fire damper and smoke damper are in open position.
checklist | Pipework Checklist | Pass, Fail, N/A
checkpoint | Pipe and valve sets installed as per latest drawing/ schematics
checkpoint | Inspect the pipework is not damaged. Record and report for any issues
checkpoint | Confirm correct spacing of supports installed
checkpoint | Confirm couplings, unions and flanges securely fixed to the pipework
checkpoint | Confirm valves, strainers and major line fittings correctly installed as documented
checkpoint | Confirm spacers provided
checkpoint | Confirm insulation provided
checkpoint | Confirm air bleeds have been installed at the highest point and drains at the lowest point
checkpoint | Correct flow and return checked
checkpoint | Access to valve sets checked
checkpoint | No other services suspended from pipe work
Checklist | Drains | Pass, Fail, N/A
checkpoint | Drain trapped where required
checkpoint | Drain pump installed on a gradient/ level
checkpoint | Drain terminates at a tundish
checkpoint | Drain pipe insulated where required
checkpoint | Drains, pump and tundish access for maintenance
checkpoint | Drain pipe is labelled clearly
checklist | General Equipment Checklist | Pass, Fail, N/A
checkpoint | Unit installed as per latest drawing
checkpoint | Inspect the unit is not damaged. Record and report for any issues
checkpoint | Unit is labelled clearly
checkpoint | Unit correctly supported as per documented
checkpoint | Confirm pipework connections to the unit are correct and include all fittings and accessories as documented
checkpoint | Confirm drains are terminated correctly
checkpoint | Confirm all thermal insulation and sheating is complete and undamaged
checkpoint | Confirm electrical connection to unit
checkpoint | Adequate maintenance clearance maintained
checklist | VAV/ Heating Coils Checklist | Pass, Fail, N/A
checkpoint | Unit installed as per latest drawing
checkpoint | Inspect the unit casing is not damaged. Record and report for any issues
checkpoint | Unit is labelled clearly
checkpoint | Unit correctly supported as per documented
checkpoint | Confirm correct CHW/HHW pipe work installed as per latest drawing (e.g. Valves, binder points, air vents)
checkpoint | Confirm test points, sensors and pressure points have been provided and installed as documented
checkpoint | Confirm electrical connection to unit
checkpoint | Confirm ductwork connections to the unit are correct
checkpoint | Unit complete with acoustic wrapping as per documented
checkpoint | Adequate maintenance clearance maintained
checkpoint | Installed as per manufacturer's requirements. Refer to specific equipment schedule for detail
checklist | Split DX Unit Checklist | Pass, Fail, N/A
checkpoint | FCU and condensing units installed as per latest drawing
checkpoint | Inspect the FCU and condensing unit. Record and report for any issues
checkpoint | Unit is labelled clearly
checkpoint | Unit correctly supported as per documented
checkpoint | Confirm safety tray and/ or condensate drain provided to the units and is piped to adjacent waste point
checkpoint | Confirm refrigeration pipework are installed
checkpoint | Confirm refrigeration pipework insulation are installed with adequate support
checkpoint | Confirm correct eletrical connections to the refrigeration system as per wiring schematic
checkpoint | Adequate maintenance and ventilation clearance maintained
checkpoint | Installed as per manufacturer's requirements. Refer to specific equipment schedule for detail.
checklist | Fan Coil Unit Checklist | Pass, Fail, N/A
checkpoint | FCU installed as per latest drawing
checkpoint | Inspect the unit casing is not damaged. Record and report for any issues
checkpoint | Unit is labelled clearly
checkpoint | Unit correctly supported as per documented
checkpoint | Confirm safety tray and/ or condensate drain provided to the units and is piped to adjacent waste point
checkpoint | Confirm installation of any dampers on the units
checkpoint | Confirm correct CHW/HHW pipe work installed as per latest drawing (e.g. Valves, binder points, air vents)
checkpoint | Confirm VSD is installed
checkpoint | Confirm electrical connection to unit
checkpoint | Flexible connections installed
checkpoint | Air filters installed
checkpoint | Magnehelic gauges installed across the filters
checkpoint | Check for cleaniness inside the AHU housing
checkpoint | Check for internal lights
checkpoint | Confirm seismic bracing to requirements
checkpoint | Unit complete with acoustic wrapping as per documented
checkpoint | Adequate maintenance clearance maintained
checklist | Pump Checklist | Pass, Fail, N/A
checkpoint | Pump installed as per latest drawing
checkpoint | Unit correctly supported as per documented
checkpoint | Inspect the unit casing is not damaged. Record and report for any issues
checkpoint | Pump is labelled clearly
checkpoint | Inertia base installed
checkpoint | Pump base plate is grouted and bolted
checkpoint | Pump and pipe are indenpendently supported
checkpoint | Confirm safety tray provided with fall to drain point
checkpoint | Confirm drain pipe taken to appriorate drain point
checkpoint | Confirm pipework connections to the pump are correct and include all fittings, valves and accessories as documented
checkpoint | Confirm test points, sensors and gauges have been provided and installed as documented
checkpoint | Confirm electrical connection to pump
checkpoint | Confirm VSD is installed
checkpoint | Adequate maintenance clearance maintained
checkpoint | Access to all valves and fittings is achievable
checkpoint | Installed as per manufacturer's requirements. Refer to specific equipment schedule for detail
checklist | Chiller Checklist | Pass, Fail, N/A
checkpoint | Chiller installed as per latest drawing
checkpoint | Unit correctly supported as per documented
checkpoint | Confirm chiller meets approved equipment details
checkpoint | Inspect unit is not damaged. Record and report for any issues
checkpoint | Chiller is labelled clearly
checkpoint | Confirm pipework connection to chiller are correct and include all fittings and accessories as documented
checkpoint | Confirm refrigerant leak detector installed on chiller
checkpoint | Confirm correct electrical connection to chiller
checkpoint | Adequate maintenance and ventilation clearance maintained
checkpoint | Installed as per manufacturer's requirements. Refer to specific equipment schedule for detail.
checklist | Fan Checklist | Pass, Fail, N/A
checkpoint | Fan installed as per latest drawing
checkpoint | Inspect the fan. Record and report for any issues
checkpoint | Fan is labelled clearly
checkpoint | Confirm ductwork connections to the fans are correct and include flexible connections
checkpoint | Confirm VSD is installed
checkpoint | Confirm test points, sensors and gauges have been provided and installed as documented
checkpoint | Confirm correct eletrical connections to the fan
checkpoint | Adequate maintenance clearance maintained
checkpoint | Unit complete with acoustic wrapping as per documented
checkpoint | Installed as per manufacturer's requirements. Refer to specific equipment schedule for detail.
checklist | Grille Fit-Off Checklist | Pass, Fail, N/A
checkpoint | Confirm grilles type and colour as per schedule
checkpoint | Grilles installed in correct location as per latest duct layout / RCP
checkpoint | Inspect the grille. Record and report for any issues
checkpoint | Grille left clean of fingerprints and caps installed where required
checkpoint | Area left clean/tidy (Any Issues comment below)
checklist | All Subbie Rough-in Progression Checklist | Complete, Incomplete
checkpoint | All work in zone completed and appear compliant
label | Pass once all work complete
checklist | All Subbie Fit off & Testing Progression Checklist | Complete, Incomplete
checkpoint | All work in zone completed and appear compliant
label | Pass once all work complete
checklist | As Builts Checklist | Complete, Incomplete
button | Update As-Built's of any known changes
checklist | Pipework Testing | Pass, Fail, N/A
checkpoint | Pipe tested and recorded (attach results)
checkpoint | Initial pipe pressure test (attach photo)
checkpoint | 24hr pipe pressure test (attach photo)
checkpoint | Piping cleaned and flushed (attach photo of results)
checklist | Ductwork leakage testing | Pass, Fail, N/A
checkpoint | Ductwork leakage testing performed on tested section
checkpoint | Provide markup with highlighted tested section
checkpoint | Tested ductwork have been pressurised and achieve minimal audible leakage
checkpoint | Provide test result sheet (attach photo)

## TO BUILD - DUCTWORK
Project Breakdown |  | Checklists
PROJECT NAME: Level 18, 452 Flinders Street
OHS |  | Site Establishment and Safety Checklist
Site QA | LEVEL 18 | Ductwork Checklist
Grille Fit-Off Checklist

## TO BUILD - PIPEWORK
Project Breakdown |  | Checklists
PROJECT NAME: Level 18, 452 Flinders Street
OHS |  | Site Establishment and Safety Checklist
Site QA | LEVEL 18 | Pipework Checklist
Pipework Testing

## TO BUILD - FCU
Project Breakdown |  | Checklists
PROJECT NAME: Level 18, 452 Flinders Street
OHS |  | Site Establishment and Safety Checklist
Site QA | PAC-18.01 | Fan Coil Unit Checklist
| PAC-18.02 | Drains
PAC-18.03

## TO BUILD - FANS
Project Breakdown |  | Checklists
PROJECT NAME: Level 18, 452 Flinders Street
OHS |  | Site Establishment and Safety Checklist
Site QA | GEF-18.01 | Fan Checklist

## TO BUILD - VAV
Project Breakdown |  | Checklists
PROJECT NAME: Level 18, 452 Flinders Street
OHS |  | Site Establishment and Safety Checklist
Site QA | VAV-N1-S | VAV/ Heating Coils Checklist
VAV-N2-M
VAV-N3-M