## res_1630-P200-SYM-QAC-ITP-0021.
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | CC0394 - ITP-007 - Electrical Trenching and Blinding | itp |  |  |  |  | CC0394 - ITP-007 - Electrical Trenching and Blinding REV0
section | Lot Conformance.
checkpoint | Lot Conformance
select | Lot Status | Awaiting Hold Point Release, Awaiting NCR Closure, Awaiting Test Results, Awaiting Verification, Cancelled, Closed-out, Outstanding, Work In Progress
text | Lot opened date:
text | Lot opened by:
text | Date lot closed:
button | NCR raised? | Yes, No
text | NCR Raised Date:
button | NCR closed? | Yes, No
text | NCR Closed Date:
text | NCR Number:
text | Comments
holdpoint | AUTHORITY HOLDPOINT
section | 1.0 Pre-start activities
checkpoint | 1.1 - Safety
label | Ensure that the following items have been actioned:
label | – SWMS if applicable
label | – Plant Pre-start Inspection
label | – Service locations identified
label | – Worksafe notification in place
label | – Traffic Management Plans (if reqd)
label | – All staff inducted
label | Ref docs - SMP
label | Acceptance criteria - SWMS/WMS submitted reviewed & accepted if required.
label | ○ Plant inspections completed & entered.
label | ○ Pre-work briefings completed.
label | ○ Service Diagrams available and services located
button | Have any/all of the above SWMS been reviewed and are available to all staff and signed onto every month? | Yes,No,N/A
label | Frequency - Once (Pre Start)
label | Key - H
label | Resp - SE
checkpoint | 1.2 - Environmental
label | – Air & noise levels
label | – Sediment & erosion controls
label | – Heritage controls
label | – Dust control
label | – Water quality
label | Ref docs - EMP
label | Acceptance criteria - Site Environnemental Management Plans (SEMP) on site.
label | ○ Controls installed as per CEMP.
label | ○ Water available for dust suppression.
button | Have any/all of the above management plans been acquired and are available for review? | Yes,No,N/A
label | Frequency - Prior to excavation in each location
label | Key - H
label | Resp - SE
checkpoint | 1.3 - Excavation Permit (if required)
label | Ref docs - Worksafe Excavation Permit. Symal Ground Penetration Permit.
label | Acceptance criteria -
bool | Penetration Permit
bool | Excavation Permit
label | Frequency - Prior to start of works
label | Key - H
label | Resp - SE
checkpoint | 1.4 - Survey Setout
label | Ref docs - DWG: 5668-122-1020 Rev 0, DWG: 5668-126-1005 Rev 1
label | Acceptance criteria - Peg location of proposed underground services with levels from end to end.
button | Has the above been completed and approved? | Yes,No,N/A
label | Frequency - Every section of Culvert
label | Key - S
label | Resp - SE
checkpoint | 1.5 - Material Classification and Source
label | Acceptance criteria - Mix design to be approved prior to placement.
label | ○ Material properties meet project specification, AS 3600, AS 1379. 25mPa as per construction drawings.
label | Frequency - Ongoing
label | Key - H
label | Resp - PE
label | RJE Key - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.6 - Determine lot size
label | Acceptance criteria - Lot Size = Each construction stage
label | Frequency - Ongoing
label | Key - S
label | Resp - SE
section | 2.0 Excavation
checkpoint | 2.1 - Excavate to width and depth as per survey pegs
label | Ref docs - Drawing no. 5668-126-1005 Rev 1
label | Acceptance criteria - Trench depth nominated tolerance is 0 to -20mm. In reference to the depth of the culvert.
label | ○ Trench Width is as per drawings provided. Typical trench width will be 1.6m.
label | ○ Road Crossing trench width will be 4.5m.
button | Have the above depths of cover been achieved and approved? | Yes,No,N/A
label | Frequency - Entire length of Culvert
label | Key - S
label | Resp - SE
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Photos of trench width and depth.
checkpoint | 2.2 - Damp Proof Membrane
label | Ref docs - Drawing no. 5668-126-1005 Rev 1
label | Acceptance criteria - Has the 0.2mm damp proof membrane been installed with accordance to the design drawings?
label | ○ The DPM extends up the sides of the blinding on both edges, above the surface of the blinding.
label | ○ Has the DPM been laid and overlapped at 200mm along the length of the culvert trench.
label | Frequency - Entire length of Culvert
label | Key - S
label | Resp - SE
checkpoint | 2.3 - Connoly Joint Installation
label | Ref docs - Drawing no. 5668-126-1005 Rev 1
label | Acceptance criteria - Have Connolly joints been installed at 2500mm spacings. Nominated KJ100.
label | Frequency - Entire length of Culvert
label | Key - W
label | Resp - SE
label | RJE Key - W
checkpoint | 2.4 - Installation of Formwork and boxing/finished levels
label | Ref docs - Drawing no. 5668-126-1005 Rev 1
label | Acceptance criteria - Has formwork or boxing or height pins been installed as per the nominated design tolerance of 0 to -10mm of the design finished level of the blinding. As per the nominal datum of 10m.
label | ○ Note: RJE are to confirm applicable height of Concrete Culvert segments.
label | Frequency - Entire length of Culvert
label | Key - H
label | Resp - SE, SS
label | RJE Key - W
checkpoint | 2.5 - Pre pour Inspection
label | Ref docs - Drawing no. 5668-126-1005 Rev 1, Pre-Pour Checklist
label | Acceptance criteria - Pre-pour inspection undertaken, confirming that all requirements have been met and pour can be completed.
button | Has all requirements been met, RJE supervision involved in inspection and approval given and considered ready to pour? | Yes,No,N/A
label | Frequency - Entire length of Culvert
label | Key - H
label | Resp - SE, SS
label | RJE Key - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Pre pour checklist
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.6 - Finishing
label | Ref docs - Specifications
label | Acceptance criteria - Steel Trowel non-slip finish nominated.
label | Frequency - Entire length of Culvert
label | Key - W
label | Resp - SE
label | RJE Key - W