## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP - Piling | itp |  |  |  |  | ITP - Piling
section | 1.0 Pre-Construction
checkpoint | 1.1 - Accepted Method Statement
label | Standard / Spec Reference - Project specification
label | Acceptance Criteria - Engineer’s acceptance
label | Frequency - Once prior to commencement of piling
label | Responsibility - CLL
label | Hold Point H/W/S - DO: H
label | Hold Point H/W/S - BBO: H
label | Hold Point H/W/S - CLL: H
label | Verifying Record - Email Confirmation
label | Comment - To be submitted at least 10 days in advance.
holdpoint | HOLD POINT (DO/BBO/CLL)
checkpoint | 1.2 - Accepted Inspection and Test Plan
label | Acceptance Criteria - Issue
label | Frequency - Once prior to commencement of piling
label | Responsibility - CLL
label | Hold Point H/W/S - DO: H
label | Hold Point H/W/S - BBO: H
label | Verifying Record - Email Confirmation
holdpoint | HOLD POINT (DO/BBO)
checkpoint | 1.3 - Accepted Safety Plan - SSSP
label | Acceptance Criteria - Issue
label | Frequency - Once prior to commencement of piling
label | Responsibility - CLL
label | Hold Point H/W/S - DO: H
label | Verifying Record - Email Confirmation
holdpoint | HOLD POINT (DO)
checkpoint | 1.4 - Accepted support fluid details
label | Acceptance Criteria - Issue
label | Frequency - Once prior to commencement of piling
label | Responsibility - CLL
label | Hold Point H/W/S - DO: H
label | Hold Point H/W/S - BBO: H
label | Verifying Record - Email Confirmation
holdpoint | HOLD POINT (DO/BBO)
checkpoint | 1.5 - Permits issued
label | Acceptance Criteria - Issue
label | Frequency - Once at commencement of piling
label | Responsibility - DO
label | Hold Point H/W/S - DO: H
label | Hold Point H/W/S - CLL: H
label | Verifying Record - Site Hardcopy
holdpoint | HOLD POINT (DO/CLL)
checkpoint | 1.6 - Concrete Design Mix Verification
label | Acceptance Criteria - Issue
label | Frequency - Once prior to commencement of piling
label | Responsibility - DO/BBO
label | Hold Point H/W/S - DO: H
label | Hold Point H/W/S - BBO: H
label | Verifying Record - Email Confirmation
holdpoint | HOLD POINT (DO/BBO)
checkpoint | 1.7 - Reinforcement Steel – mill cert
label | Acceptance Criteria - Project specification
label | Frequency - Post Construction for every pile
label | Responsibility - CLL
label | Hold Point H/W/S - DO: H
label | Hold Point H/W/S - BBO: H
label | Verifying Record - Issued by supplier - email confirmation
holdpoint | HOLD POINT (DO/BBO)
section | 2.0 Pile Boring
checkpoint | 2.1 - Client Notification
label | Acceptance Criteria - Issue
label | Frequency - Once at commencement of piling
label | Responsibility - DO
label | Hold Point H/W/S - DO: H
label | Hold Point H/W/S - BBO: H
label | Hold Point H/W/S - CLL: H
label | Verifying Record - Email Confirmation
label | Comment - 48 hours’ notice of pile drilling commencement.
holdpoint | HOLD POINT (DO/BBO/CLL)
checkpoint | 2.2 - Check drill tool diameter
label | Standard / Spec Reference - As per HCC 1298/2022
label | Acceptance Criteria - Visual Inspection
label | Frequency - Prior to commencement of piling
label | Responsibility - CLL
label | Hold Point H/W/S - DO: W/S
label | Hold Point H/W/S - CLL: W/S
label | Verifying Record - As per pile QAC
label | Comment - Minimum agreed diameter is 870 mm for 900 DIA piles, due to ID of permanent casing supplied by DO, and 1200 mm for 1200 DIA piles.
checkpoint | 2.3 - Check depth gauge/instrumentation of piling rig
label | Standard / Spec Reference - Operators Manual
label | Acceptance Criteria - Visual Inspection
label | Frequency - Daily
label | Responsibility - Rig Operator
label | Hold Point H/W/S - DO: W/S
label | Hold Point H/W/S - CLL: H
label | Comment - Operator daily checks
holdpoint | HOLD POINT (CLL)
checkpoint | 2.4 - Ground penetration and extraction with due diligence
label | Standard / Spec Reference - Operators Manual
label | Acceptance Criteria - Visual Monitoring
label | Frequency - Every Pile
label | Responsibility - Rig Operator
label | Hold Point H/W/S - DO: W/S
label | Hold Point H/W/S - BBO: S
label | Hold Point H/W/S - CLL: S
label | Comment - Operator to penetrate/extract with due diligence, no adverse effect on bore integrity.
checkpoint | 2.5 - Check pile position/pile numbers
label | Standard / Spec Reference - Drawings
label | Acceptance Criteria - Visual Inspection
label | Frequency - Every Pile
label | Responsibility - CLL
label | Hold Point H/W/S - DO: W/S
label | Hold Point H/W/S - CLL: W/S
checkpoint | 2.6 - Pile Setout/Offsets
label | Standard / Spec Reference - Drawings
label | Acceptance Criteria - Hz +/- 10mm
label | Frequency - Every Pile
label | Responsibility - DO
label | Hold Point H/W/S - DO: W
label | Hold Point H/W/S - CLL: W
label | Verifying Record - Survey record
label | Comment - Due to tight plan tolerances set-out is critical
checkpoint | 2.7 - Casing Inspection
label | Standard / Spec Reference - As per HCC 1298/2022 – note minimum agreed diameters at ITP item 2.2
label | Acceptance Criteria - Visual Inspection
label | Frequency - Length/diameter/Wall thickness at start of piling, RL every pile
label | Responsibility - CLL
label | Hold Point H/W/S - DO: H
label | Hold Point H/W/S - CLL: H
label | Verifying Record - QAC - Pile Card
label | Comment - RL check pre-concrete & pre- drill
holdpoint | HOLD POINT (DO/CLL)
checkpoint | 2.8 - Measure and check position and verticality
label | Standard / Spec Reference - As per ASGPILES - Rev G
label | Acceptance Criteria - Visual Inspection Permitted deviation from vertical shall be not more than 1:75 or 0.8 degree.
label | Frequency - Every Pile
label | Responsibility - CLL
label | Hold Point H/W/S - DO: W
label | Hold Point H/W/S - CLL: H
label | Verifying Record - QAC - Pile Card
label | Comment - Spirit level has a +-0.5 degree accuracy. Verticality of pile to be checked via use of electronic level on the side of the casings & against Kelly bar.
holdpoint | HOLD POINT (CLL)
checkpoint | 2.9 - Bentonite checks
label | Standard / Spec Reference - Fluid Specification
label | Acceptance Criteria - Visual Inspection/Testing
label | Frequency - Per batch, each pile prior to concreting
label | Responsibility - CLL
label | Hold Point H/W/S - DO: W
label | Hold Point H/W/S - CLL: H
label | Verifying Record - QAC - Pile Card
holdpoint | HOLD POINT (CLL)
checkpoint | 2.10 - Bentonite level
label | Standard / Spec Reference - As per construction specification - Methodology
label | Acceptance Criteria - Visual Inspection Bentonite head to be maintained at 0.5m above groundwater level or adjusted as required.
label | Frequency - Each pile
label | Responsibility - CLL
label | Hold Point H/W/S - DO: W
label | Hold Point H/W/S - CLL: H
label | Verifying Record - QAC - Pile Card
label | Comment - Any significant fluid loss/stability will be addressed with Project Engineer.
holdpoint | HOLD POINT (CLL)
checkpoint | 2.11 - Soil logging and bagging
label | Standard / Spec Reference - As per HCC 1298/2022 11.7
label | Acceptance Criteria - Visual Inspection Engineer Inspection
label | Frequency - Every Pile
label | Responsibility - DO/CLL
label | Hold Point H/W/S - DO: S
label | Hold Point H/W/S - BBO: S
label | Hold Point H/W/S - CLL: S
label | Verifying Record - QAC - Pile Card Labelled, bagged core samples
label | Comment - Boreholes are to be continuously logged on QAC - Pile Card. Material from the base will be bagged, labelled and securely stored on site for Engineer’s inspection.
checkpoint | 2.12 - Confirmation design minimum toe depth achieved
label | Standard / Spec Reference - Construction Specification/ Drawings
label | Acceptance Criteria - By means of weighted tape Designer Hold Point: Maximum depth exceedance
label | Frequency - Every Pile
label | Responsibility - BBO & DO Rep/CLL
label | Hold Point H/W/S - DO: H
label | Hold Point H/W/S - BBO: H
label | Hold Point H/W/S - CLL: H
label | Verifying Record - QAC - Pile Card
label | Comment - Visual inspection not possible due to drilling under fluid. Engineer to agree correct drill depth. Designer to be notified if drilling reaches >300mm below design RL for pile toe. Maximum depth exceedance to be 40m from piling platform.
holdpoint | HOLD POINT (DO/BBO/CLL)
checkpoint | 2.13 - Base cleanliness
label | Standard / Spec Reference - Construction Specification
label | Acceptance Criteria - By means of weighted tape
label | Frequency - Every Pile
label | Responsibility - BBO & DO Rep/CLL
label | Hold Point H/W/S - DO: H
label | Hold Point H/W/S - BBO: H
label | Hold Point H/W/S - CLL: H
label | Verifying Record - QAC - Pile Card
label | Comment - Visual inspection not possible due to drilling under fluid.
holdpoint | HOLD POINT (DO/BBO/CLL)
checkpoint | 2.14 - Pile Boring Monitoring
label | Standard / Spec Reference - Construction specification
label | Acceptance Criteria - Visual Monitoring
label | Frequency - Every Pile
label | Responsibility - Rig Operator
label | Hold Point H/W/S - DO: S
label | Hold Point H/W/S - BBO: S
label | Hold Point H/W/S - CLL: S
label | Verifying Record - QAC - Pile Card
label | Comment - Depth check, possible collapse, changing ground conditions, any unexpected occurrences
section | 3.0 Pre-Pour Inspection
checkpoint | 3.1 - QA check on previous pile
label | Standard / Spec Reference - Engineer Specification
label | Acceptance Criteria - Client notification/Engineer’s Approval
label | Frequency - Every Pile Ongoing Engineer’s approval
label | Responsibility - DO Rep/CLL
label | Hold Point H/W/S - DO: H
label | Hold Point H/W/S - BBO: S
label | Hold Point H/W/S - CLL: H
label | Verifying Record - QAC - Pile Card
label | Comment - Engineer’s approval to proceed with subsequent piles
holdpoint | HOLD POINT (DO/CLL)
checkpoint | 3.2 - Reinforcement Cage inspection/ check spacers, pile bore tolerances
label | Standard / Spec Reference - BBO SS 2110 Rev 9
label | Acceptance Criteria - Alignment lesser of +- 4% DIA or +-75mm
label | • Height +- 50mm
label | • Reinforcement Type- As per drawings
label | • Concrete cover: 75mm, 50mm minimum
label | • Bottom of pile position lesser of +-1% pile length, +-12.5% of shaft diameter, or +-400mm
label | Frequency - Every Pile
label | Responsibility - DO Rep/CLL
label | Hold Point H/W/S - DO: H
label | Hold Point H/W/S - BBO: S
label | Hold Point H/W/S - CLL: H
label | Verifying Record - QAC - Pile Card
label | Comment - Pre-installation check required of all pile sections
holdpoint | HOLD POINT (DO/BBO/CLL)
checkpoint | 3.3 - Stabilising Fluid Verification
label | Standard / Spec Reference - Construction Specification
label | Acceptance Criteria - <4% sand content acceptable
label | Frequency - Every Pile
label | Responsibility - DO Rep/CLL
label | Hold Point H/W/S - DO: H
label | Hold Point H/W/S - BBO: S
label | Hold Point H/W/S - CLL: H
label | Verifying Record - QAC - Pile Card
holdpoint | HOLD POINT (DO/CLL)
checkpoint | 3.4 - Pile cage installation
label | Standard / Spec Reference - BBO SS 2110 Rev 9
label | Acceptance Criteria - Engineer Inspection
label | Frequency - Every Pile
label | Responsibility - BBO/CLL
label | Hold Point H/W/S - DO: H
label | Hold Point H/W/S - BBO: H
label | Hold Point H/W/S - CLL: H
label | Verifying Record - QAC - Pile Card
label | Comment - Pile cage to be installed immediately after Engineer inspection and acceptance
holdpoint | HOLD POINT (DO/BBO/CLL)
section | 4.0 Concrete Placement
checkpoint | 4.1 - Verify Concrete Mix – batch times, mix
label | Standard / Spec Reference - BBO SS 2140 Rev 5
label | Acceptance Criteria - 401T4504R
label | Frequency - Each delivery
label | Responsibility - DO Rep/CLL
label | Hold Point H/W/S - DO: W/S
label | Hold Point H/W/S - BBO: S
label | Hold Point H/W/S - CLL: W/S
label | Verifying Record - Concrete Docket
checkpoint | 4.2 - Slump/ Spread test
label | Standard / Spec Reference - BBO SS 2140 Rev 5
label | Acceptance Criteria - Slump 100-130mm +- 25mm
label | • Spread 500mm +-100mm
label | Frequency - Each delivery
label | Responsibility - DO Rep/CLL
label | Hold Point H/W/S - DO: H
label | Hold Point H/W/S - BBO: S
label | Hold Point H/W/S - CLL: H
label | Verifying Record - QAC - Pile Card
holdpoint | HOLD POINT (DO/CLL)
checkpoint | 4.3 - Concrete level
label | Standard / Spec Reference - BBO SS 2140 Rev 5
label | Acceptance Criteria - Design +50mm
label | Frequency - Every Pile
label | Responsibility - DO Rep/CLL
label | Hold Point H/W/S - DO: H
label | Hold Point H/W/S - BBO: S
label | Hold Point H/W/S - CLL: H
label | Verifying Record - QAC - Pile Card
holdpoint | HOLD POINT (DO/CLL)
checkpoint | 4.4 - Concrete placement
label | Standard / Spec Reference - HCC 1298/2022
label | Acceptance Criteria - ITP Item 3.3
label | Frequency - Every Pile
label | Responsibility - BBO/CLL
label | Hold Point H/W/S - DO: W/S
label | Hold Point H/W/S - BBO: S
label | Hold Point H/W/S - CLL: W/S
label | Verifying Record - QAC - Pile Card
label | Comment - Pile to be concreted within the same day as Engineer’s acceptance of reinforcing cage installation, ITP Item 3.3.
checkpoint | 4.5 - Concrete pouring – Check volume
label | Standard / Spec Reference - Construction Specification
label | Acceptance Criteria - As per QAC - Pile card
label | Frequency - Each delivery
label | Responsibility - DO Rep/CLL
label | Hold Point H/W/S - DO: W
label | Hold Point H/W/S - BBO: S
label | Hold Point H/W/S - CLL: W
label | Verifying Record - Concrete docket, QAC - Pile Card
label | Comment - Concrete volumes and Tremie records to be maintained as per QAC - Pile Card
checkpoint | 4.6 - Pile concrete overpour
label | Standard / Spec Reference - HCC 1298/2022
label | Acceptance Criteria - Visual check - Sign off by Engineer
label | Frequency - Every Pile
label | Responsibility - BBL/CLL
label | Hold Point H/W/S - DO: W
label | Hold Point H/W/S - BBO: W
label | Hold Point H/W/S - CLL: W
label | Verifying Record - QAC - Pile Card
label | Comment - Pile to be overpoured and slurry at the top of the head removed until only sound concrete is present.
checkpoint | 4.7 - Formation of construction joint
label | Frequency - Every Pile
label | Responsibility - DO Rep/CLL
label | Comment - Formation of construction joint by others.
checkpoint | 4.8 - Concrete curing (tops of piles)
label | Standard / Spec Reference - BBO SS 2146 Rev 4
label | Acceptance Criteria - 7-day wet curing required
label | Frequency - Every Pile
label | Comment - Concrete curing by others. Curing requirements will depend on the thickness of concrete which to be removed after concreting and weather conditions.
checkpoint | 4.9 - Compressive Strength Sampling
label | Standard / Spec Reference - NZS 3112
label | Acceptance Criteria - 28 day - 40MPa
label | Frequency - Batch plant sampling and testing per piles – 4no cylinders – 1no @7 days, 3no @ 28 days
label | Responsibility - Concrete Supplier – samples cast at plant
label | Hold Point H/W/S - Sub: H
label | Hold Point H/W/S - DO: S
label | Hold Point H/W/S - BBO: S
label | Hold Point H/W/S - CLL: S
label | Verifying Record - Lab. Test Record
label | Comment - On site independent testing to be done by others. Samples to be taken at batch plant.
holdpoint | HOLD POINT (Sub)
checkpoint | 4.10 - Post pour/ Post casing removal - Reinforcement and concrete RL, orientation check.
label | Standard / Spec Reference - As per Auckland Structural Group Piling Specification
label | Acceptance Criteria - Alignment lesser of +- 4% DIA or +-75mm Height +- 50mm Concrete cover: 75mm, 50mm minimum
label | Frequency - Every Pile
label | Responsibility - DO Rep/CLL
label | Hold Point H/W/S - DO: W
label | Hold Point H/W/S - BBO: S
label | Hold Point H/W/S - CLL: W
label | Verifying Record - QAC - Pile Card
label | Comment - As builts by others.
section | 5.0 Close out
checkpoint | 5.1 - Pile Cut off level verification
label | Standard / Spec Reference - Construction Specification
label | Acceptance Criteria - +/- 10mm
label | Frequency - Every Pile
label | Responsibility - DO Rep
label | Hold Point H/W/S - DO: S
label | Hold Point H/W/S - BBO: S
label | Verifying Record - Survey Record
checkpoint | 5.2 - Pile & Reinforcement Cleaning
label | Standard / Spec Reference - Construction Specification
label | Acceptance Criteria - Visual
label | Frequency - Every Pile
label | Responsibility - DO Rep
label | Hold Point H/W/S - DO: S
label | Hold Point H/W/S - BBO: S
label | Verifying Record - QAC - Pile Card
checkpoint | 5.3 - Reinforcement to specification
label | Standard / Spec Reference - Construction Specification
label | Acceptance Criteria - Visual
label | Frequency - Every Pile
label | Responsibility - DO Rep
label | Hold Point H/W/S - DO: S
label | Hold Point H/W/S - BBO: S
label | Verifying Record - QAC - Pile Card
checkpoint | 5.4 - Pile records
label | Standard / Spec Reference - Construction Specification
label | Acceptance Criteria - Collation and Submission of records
label | Frequency - Within 24hrs of completion, Every Pile
label | Responsibility - CLL
label | Hold Point H/W/S - DO: H
label | Hold Point H/W/S - BBO: S
label | Verifying Record - Email Confirmation
holdpoint | HOLD POINT (DO)