## QA Folder Structure
QA Folder Structure |  |  | Checklists
Site QA
| Project Photos |  | Project Photos Checklist
Site Wide
Sewer
QA8.1A – Below Ground Sewer Checklist
Grease Waste
QA8.1 - Below Ground Drainage Checklist
Stormwater
QA8.1B – Stormwater Drainage Checklist
Water and Fire Services
• QA8.1C - Below Ground Fire Service Pipework Checklist
• QA8.1D – Below Ground Water Pipework Checklist
• QA6 - Quality Control Pressure Test Report
Building Works
Sewer
QA8.1A – Below Ground Sewer Checklist
Trade Waste
Grease Waste
QA8.1 - Below Ground Drainage Checklist
Water and Fire Service
QA8.1C - Below Ground Fire Service Pipework Checklist
QA8.1D – Below Ground Water Pipework Checklist
QA6 - Quality Control Pressure Test Report

## Checklists ITPs
type | name | values | prefix | "Add+" Template Name | Q's for CONQA
checklist-flat | QA 8.1 - Below Ground Drainage Checklist |  |  | 8.1 - Below Ground Drainage Checklist
checkpoint | Principal Contractor Permits Issued
checkpoint | Set out pits, trench depths and runs.
text | Drawing & Revision #
text | Survey setout completed by:
text | Starting IL established - enter IL
checkpoint | Pipes and fittings comply with relevant Authority and Specification.
label | Spec#: AS3500 and Hydraulic Specification
text | Materials used:
button | Approved by Principal | Yes,No
checkpoint | Bedding material, placement and compaction meets specification.
label | Spec#: AS3500 and Hydraulic Specification
Text: | Material used:
checkpoint | Laying and jointing of pipes - RL and fall
Text: | Jointing Type:
Text: | Fall:
Text" | AS3500
checkpoint | Service run was inspected prior being covered
button | Geschke Group Signature Sign-Off added below | Yes,No
button | Principal Contractor Representative Sign-Off added below | Yes,No
checkpoint | Hydrostatic tests are carried out as required.
button | Air or Water? | Water,Air
text | Geschke - Initial/Date
text | Principal- Initial/Date
checkpoint | Placement and compaction of backfill and material meets spec
Text | Material used:
checkpoint | Temporary cover provided to open drain.
checkpoint | PVC/ Plastic caps to open ends
checkpoint | As built information updated onto drawings
button | Drain installed as per nominated drawing | Yes,No
Text: | Comments
checkpoint | Invert levels checked by a surveyor
label | As Built drawings and 3D Model to be updated as required
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
label | FINAL SIGN OFF - Pass when work completed and signed off by Geschke Supervisor
label | Company: Geschke Group
label | Phone: 03 9798 1619
label | Address: 45 Pacific Drive, Keysborough
label | Project: Resilience Australia
label | Principal: MULTIPLEX
checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
button | Geschke Group Signature Sign-Off added below | Yes,No
button | Representative Sign-Off added below | Yes,No
checklist-flat | QA 8.1A - Below Ground Sewer Checklist |  |  | 8.1A - Below Ground Sewer Checklist
checkpoint | Principal Contractor Permits Issued
checkpoint | Set out pits, trench depths and runs.
text | Drawing & Revision #
text | Survey setout completed by:
text | Starting IL established - enter IL
checkpoint | Pipes and fittings comply with relevant Authority and Specification.
label | Spec#: AS3500 and Hydraulic Specification
text | Materials used:
button | Approved by Principal | Yes,No
checkpoint | Bedding material, placement and compaction meets specification.
label | Spec#: AS3500 and Hydraulic Specification
Text: | Material used:
checkpoint | Laying and jointing of pipes - RL and fall
Text: | Jointing Type:
Text: | Fall:
Text" | AS3500
checkpoint | Connections to pits and existing services as per Hydraulic Specification and Australian Standards
checkpoint | Hydrostatic tests are carried out as required.
button | Air or Water? | Water,Air
button | Inspected and recorded by Independent Certifier or PIC | Yes,N/A, No
text | Geschke - Initial/Date
text | Principal- Initial/Date
checkpoint | Placement and compaction of backfill and material meets spec
Text | Material used:
checkpoint | Temporary cover provided to open drain.
checkpoint | PVC/ Plastic caps to open ends
checkpoint | As built information updated onto drawings
button | Drain installed as per nominated drawing | Yes,No
Text: | Comments
label | As Built drawings and 3D Model to be updated as required
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
label | FINAL SIGN OFF - Pass when work completed and signed off by Geschke Supervisor
label | Company: Geschke Group
label | Phone: 03 9798 1619
label | Address: 45 Pacific Drive, Keysborough
label | Project: Resilience Australia
label | Principal: MULTIPLEX
checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
button | Geschke Group Signature Sign-Off added below | Yes,No
button | MULTIPLEX Representative Sign-Off added below | Yes,No
checklist | QA 16.1 - Electrofusion Welding - Field Operational Sheet |  |  | QA 16.1 - Electrofusion Welding -
checkpoint | Operator Details
text | Name
text | ID No.
text | Company
text | Address
text: | Training ticket / certificate No.
checkpoint | Welding Machine Details
text | Manufacturer
text | Type/Model
text | Serial Number
text | Year Built
label: | Attach calibration certificate
checkpoint | Actual Pipe Size
text | Type
text | Brand
text | En
text | OD
text | Ovality %
checkpoint | Fitting Data
text | Brand
text | Type (Coupling, Tee, Reducer etc.)
checkpoint | Unit Setting
text | Manual
text | Automatic
checkpoint | Preparation
text | Cleaned and Peeled
text | Pipe/Fitting Clamped
checkpoint | Welding Times
text | Joining Seconds
text | Cooling Minutes
checkpoint | Conditions
text | Ambient Temp
text | Weather
text | Preventive Measures
checkpoint | Power
text | Mains
text | Gen Set
checkpoint | Operator Sign Off
checkpoint | Foreman Sign-Offs
checklist | QA 8.1B - Stormwater Drainage Checklist |  |  | 8.1B - Stormwater Drainage Checklist
checkpoint | Stormwater Drainage Inspection Report Details:
text | Spec No.:
text | Drawing & Revision no.:
text: | Shop Drawings no:
text: | Starting IL established:
checkpoint | Pipes and fittings comply with relevant Authority and Specification
label | Spec#: AS3500 and Hydraulic Specification
text | Materials used, Size and Class:
button | Approved by Principal | Yes,No
checkpoint | Pipe Lines
text | Date started:
text | Drainage Line Number:
button | Pipe Damaged? | Yes,No
text | Jointing Required
button | Bedding and Haunching | Yes,No
checkpoint | Bedding material, placement and compaction meets specification.
label | Spec#: AS3500 and Hydraulic Specification
Text: | Material used:
text | GPL - Initial/Date
text | Builder - Initial/Date
checkpoint | Laying and jointing of pipes - RL and fall
Text: | Jointing Type:
Text: | Fall:
Text" | AS3500
Text: | RL's as installed
text | GPL - Initial/Date
text | Builder - Initial/Date
checkpoint | Backfill
label | Spec#: AS3500 and Hydraulic Specification
Text: | Material used:
checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
button | Geschke Group Signature Sign-Off added below | Yes,No
button | Principal Contractor Representative Sign-Off added below | Yes,No
checkpoint | Drainage Pits
text | Date Installed:
text | Pit Number:
text | Pit Base:
text | Step Irons - GPL Initial/Date
text | Bedding - GPL Initial/Date
label | Benching, Grouting and Patching
button | Placement of cover | Yes,No
button | Concreting of cover | Yes,No
text | Comments
label | Final Sign Off (Initial & Date)
text | GPL
text | Builder - Initial/Date
checkpoint | Pit Sign off: Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
button | Geschke Group Signature Sign-Off added below | Yes,No
button | Principal Contractor Representative Sign-Off added below | Yes,No
checklist | QA 8.1C - Below Ground Fire Service Pipework Checklist |  |  | 8.1C - Below Ground Pipework Checklist - Fire
checkpoint | Principal Contractor Permits Issued
checkpoint | Set out trench depths and runs.
text | Project drawing #
text | Shop drawing #
checkpoint | Pipes and fittings comply with relevant Authority and Specification.
label | Spec#: AS3500
text | Material used
button | Approved by Principal | Yes,No
checkpoint | Bedding placement and compaction and material meets specification.
label | Spec#: AS3500 and Hydraulic Specification
text | Geschke - Initial/Date
text | Principal- Initial/Date
text | Comments
checkpoint | Jointing of pipes
Text | Jointing type
Text | Attach welding checklist if applicable
text | Geschke - Initial/Date
text | Comments
checkpoint | Hydrostatic tests are carried out as required.
button | GPL QA6 form completed | Yes,No
label | Fire system tested to 1700 kpa regularly prior to finished surfaces installed. Independent fire test at completion.
checkpoint | Placement and compaction of backfill and material meets spec.
button | Compacted backfill as per the Specification | Yes, no
label | Detectable marker tape
checkpoint | PVC/ Plastic caps to open ends
checkpoint | As built information updated onto drawings and 3D Model
label | To be provided
checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
button | Geschke Group Signature Sign-Off added below | Yes,No
button | Principal Contractor Representative Sign-Off added below | Yes,No
checklist | QA 8.1D - Below Ground Water Pipework Checklist |  |  | 8.1D - Below Ground Water Pipework Checklist
checkpoint | Principal Contractor Permits Issued
checkpoint | Set out trench depths and runs.
text | Project drawing #
text | Shop drawing #
text | Depth of the installed run
checkpoint | Pipes and fittings comply with relevant Authority and Specification.
label | Spec#: AS3500
text | Material used
button | Approved by Principal | Yes,No
checkpoint | Bedding placement and compaction and material meets specification.
label | Spec#: AS3500 and Hydraulic Specification
text | Geschke - Initial/Date
text | Principal- Initial/Date
text | Comments
checkpoint | Jointing of pipes
Text | Jointing type
Text | Attach welding checklist if applicable
text | Geschke - Initial/Date
text | Comments
checkpoint | Hydrostatic tests are carried out as required.
button | GPL QA6 form completed | Yes,No
text | Water system tested to (kPa)
checkpoint | Placement and compaction of backfill and material meets spec.
button | Compacted backfill as per the Specification | Yes, no
label | Detectable marker tape
checkpoint | PVC/ Plastic caps to open ends
checkpoint | As built information updated onto drawings and 3D Model
label | To be provided
checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
button | Geschke Group Signature Sign-Off added below | Yes,No
button | Principal Contractor Representative Sign-Off added below | Yes,No
checklist | QA 6.1 - Quality Control Pressure Test Report |  |  | QA 6.1 - Quality Control Pressure Test Report
checkpoint | Quality Control Pressure Test Report:
text | Drawing No.:
text | Rev.:
button | Test: | Air,Water
text | Section
text | From
text | To
text | Applicable Standard No.
label | Specified System Working
text | Pressure (KPA)
text | Duration (HRS)
label | Specified System Test
text | Pressure (KPA)
text | Duration (HRS)
checkpoint | 1st Reading
text | Time
text | KPA
text | Ambient Temp
checkpoint | 2nd Reading
text | Time
text | KPA
text | Ambient Temp
checkpoint | Test Result - Passed?
text | Repeat
checkpoint | Foreman/QA Officer Sign-Offs completed - Click to Attach Signature(s) below
button | Geschke Group Signature Sign-Off added below | Yes,No
button | Principal Contractor Representative Sign-Off added below | Yes,No
checklist | Water Services Flushing |  |  | QA 32 - Water Main Flushing
checkpoint | Water Services Flushing Details:
text | Zone/Pod No's:
Bool | Mains
Bool | Cold Water
Bool | Fire Hydrant
Bool | RW
checkpoint | As built information updated onto drawings
label | Ongoing
label | To be provided
checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
label | FINAL SIGN OFF - Pass when work completed and signed off by Geschke Supervisor
label | Company: Geschke Group
label | Phone: 03 9798 1619
label | Address: 45 Pacific Drive, Keysborough
label | Project: Resilience Australia
checkpoint | Sign-Offs completed - Click to Attach Signature(s) below
button | Geschke Group Supervisor Sign-Off added below | Yes, No
button | Principal Contractor Representative Sign-Off added below | Yes, No
checklist | Installation Test Sheet (Waste, Vent, Downpipes etc) |  |  | QA 4 - Installation Test Sheet (Waste, Vent, DP etc)
checkpoint | Installation Test Sheet:
textbox | Drawing No.:
textbox | Rev.:
checkpoint | PIPE CLIP HANGERS
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | MATERIAL AND SIZE
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | ALIGNMENT
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | LABELING AND IDENTIFICATION
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | JOINTING
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | PENETRATION SEALING
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | FIRE STOP COLLARS
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | TESTING
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | AUTHORITY INSPECTION (if applicable)
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | AS BUILT INFORMATION UPDATED ONTO DRAWINGS
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | Sign-Offs completed - Click to Attach Signature(s) below
button | Geschke Group Supervisor Sign-Off added below | Yes, No
button | Principal Contractor Representative Sign-Off added below | Yes, No
checklist | Installation Test Sheet (Water Services) |  |  | QA 5 - Installation Test Sheet (Water Services)
checkpoint | Installation Test Sheet:
textbox | Drawing No.:
textbox | Rev.:
checkpoint | PIPE CLIP HANGERS
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | MATERIAL AND SIZE
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | ALIGNMENT
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | LABELING AND IDENTIFICATION
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | JOINTING
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | PENETRATION SEALING
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | FIRE STOP COLLARS
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | PRESSURE TESTING COMPLTED (QA6)
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | AUTHORITY INSPECTION (if applicable)
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | AS BUILT INFORMATION UPDATED ONTO DRAWINGS
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | Sign-Offs completed - Click to Attach Signature(s) below
button | Geschke Group Supervisor Sign-Off added below | Yes, No
button | Principal Contractor Representative Sign-Off added below | Yes, No
checklist | Quality Control Flow Test and Compliance Report - Safety Showers |  |  | QA 6C - Quality Control Flow Test and Compliance Report - Safety Showers
checkpoint | Quality Control Flow Test and Compliance Report - Safety Showers:
textbox | Drawing nos/rev:
textbox | Appliance Tested:
textbox | Room No.:
checkpoint | Specified System Working
textbox | Pressure:
textbox | Flow Rate:
checkpoint | International Standard ANSI Z358.1 2004
textbox | Pressure:
textbox | Flow Rate:
checkpoint | Pipe Installed
textbox | Pressure set on each floor: KPA
textbox | Cold - Size:
textbox | Capable Flow Rate:
textbox | Hot - Size:
textbox | Capable Flow Rate:
checkpoint | TMV Installed
textbox | Brand:
textbox | Model:
textbox | Flow Rate:
textbox | Temp Set:
checkpoint | Pull Lever Confirm Flow
checkpoint | Riser Valves Open
checkpoint | Safety Shower Valve Open
checkpoint | Drain Outlet not Obstructed
checkpoint | Temperature Test
note | Disconnect shower head, connect hose and extend to drain, turn on shower, test temperature.
textbox | Temperature:
checkpoint | Sign-Offs completed - Click to Attach Signature(s) below
textbox | Others Present
button | Geschke Group Supervisor Sign-Off added below | Yes, No
button | Principal Contractor Representative Sign-Off added below | Yes, No
checklist | Commissioning Test Report |  |  | QA 7 - Commissioning Test Report
checkpoint | Commissioning Test Report:
textbox | Zone/Grid:
textbox | Drawing No.:
textbox | Rev.:
checkpoint | Item: FIXTURE OPERATION - Pans, Basins, Sinks, Other
note | Test:
note | Performance Test CL 2.20
note | Fill fixture with water remove plug
note | Test for:
note | Leaks
note | Loss of water
note | Seal in Trap
note | Induce siphonage in trap of adjacent fixture
note | Complete draining of fixture
textbox | OK:
textbox | Not OK:
checkpoint | Item: Water Supply
note | Test:
note | Performance Test CL 2.20
note | Check for adequate water volume.
note | Flush out pipework
note | Clean aerator
note | Water hammer
textbox | OK:
textbox | Not OK:
checkpoint | Item: Flush Performance
note | Test:
note | Performance Test
note | Check for:
note | Water Volume
note | Duration of flush
note | Flush out pipework
note | Water hammer
textbox | OK:
textbox | Not OK:
checkpoint | Other
checklist | Backflow Prevention Device Test Report |  |  | QA 13 - Backflow Prevention Device Test Report
checkpoint | Backflow Prevention Device Test Report Details:
textbox | Owner/Occupier:
textbox | Address:
note | Licence: 50043
button | Type of Test: | Annual Test, Installation Test
textbox | Location of Device:
textbox | Authorized Tester Name:
textbox | Test Kit Serial No.
textbox | Tester Licence No.:
textbox | Test Kit Calibration Date:
textbox | Date of Test:
checkpoint | Device Details and Test Results
button | Permission to Isolate Water Supply | No,Yes
note | Device:
textbox | Make:
textbox | Size:
textbox | Model No.:
textbox | Serial No.:
button | Is the device installed high enough to prevent ingress of any possible contaminated water? | No,Yes
tickbox | Containment Protection
tickbox | Individual Protection
tickbox | Zone Protection
button | Strainer Installed | No,Yes
button | Strainer Cleaned | No,Yes
button | Device Type | Double Check Valve, RPZD (Reduced Pressure Zone Device)
note | Valve
textbox | Check Valve 1
textbox | Check Valve 2
textbox | Relief Valve
note | Testing Results
textbox | Close tight at:
tickbox | Leaked
textbox | Close tight at:
tickbox | Leaked
textbox | Opened at:
tickbox | Leaked
note | Reason for the device failure
tickbox | Incorrect position
tickbox | Incorrect installation
tickbox | Foreign material in the device
tickbox | Spring wear damage
tickbox | Seal or Rubber Damage
tickbox | Other
textbox | Other:
note | Test after maintenance
textbox | Close tight at:
tickbox | Leaked
textbox | Close tight at:
tickbox | Leaked
textbox | Opened at:
tickbox | Leaked
button | Water turned back on | Yes, No
textbox | Describe the maintenance:
textbox | Parts used in repair:
button | Is the device installed correctly | Yes, No
checkpoint | Test Result
textbox | Tester Name:
textbox | Date:
signoff | Add Signature
checklist | TMV Commissioning Log Sheet |  |  | QA 14 - TMV Commissioning Log Sheet
checkpoint | TMV Commissioning Log Sheet:
text | Building Name:
text | Contact Person:
text | Address:
text | Lic:
text | Registration number:
text | Phone number:
text | Make of valve:
text | Model number:
text | Valve location:
text | Room name:
text | Valve purchased from:
text | Installation date:
text | Valve installed by:
text | Number of outlets served - Baths:
text | Number of outlets served - Basins:
text | Number of outlets served - Showers:
text | Total number of mixing valves on site:
button | Does the installation comply with the manufacturer's/supplier's published installation instructions? | No,Yes
button | Does the installation comply with the current requirements of the local water supply authority? | No,Yes
text | Temperature of hot water supply?
text | Temperature of cold water supply?
text | Temperature of warm water delivery at outlet fitting?
text | Dynamic pressure of hot water:
text | Dynamic pressure of cold water:
checkpoint | Check fail safe operation (hot water at least 20c above warm water)
checkpoint | Commissioned by
text | Commissioned by:
text | Company name:
checklist | Service Cross Connection Check List Report |  |  | QA 19 - Service Cross Connection Check List Report
checkpoint | Service Cross Connection Check List Report Details:
textbox | Zone/Grid:
textbox | Drawing No.:
textbox | Rev:
checkpoint | Service to be tested
note | Isolation of potable supply in general.
checkpoint | Potable Water Supply
note | Confirmation of service isolation at all fixtures.
note | Keep potable water turned off.
checkpoint | Non Potable Supply
note | Confirmation of water flow for non potable water supply at each non potable fixture while potable is still isolated.
checkpoint | Turn potable back on
note | Potable back on
checkpoint | Non potable supply
note | Isolate non potable water flow and prove that each non potable fixture has no water flow.
checkpoint | Potable Supply
note | Check all fixtures that receive potable water are still getting potable water.
checkpoint | Pipe Identification
note | Confirm recycled water piping is identified by colour and noteling.
checkpoint | Other
checkpoint | Conducted by
text | Conducted by:
checklist | Hot Water Unit Service Maintenance Log |  |  | QA 22 - Hot Water Unit Service Maintenance Log
checkpoint | Hot Water Service Unit Details
text | Purchased from:
text | Make:
text | Model No.:
text | Location:
text | Room Designation:
text | Installed by:
text | Installation Date:
text | Number of units in series:
text | Prescribed temperature set on unit or combined package:
checkpoint | Does installation comply with manufacturers instructions
checkpoint | Does installation comply with current requirements of the local water supply authority
checkpoint | Clean Pump Strainers
checkpoint | Clean Hot Water inlet Strainer
checkpoint | Clean Hot Water Return Strainer
checkpoint | Confirm all Valve Isolation reinstatement
checkpoint | Confirm Unit is Operational
checkpoint | Confirm Unit is Back to Operational Temp with no leaks on Strainer seals
checkpoint | Commissioned By:
text | Name:
text | Date:
checklist | Hot Water Unit Service Maintenance Log |  |  | QA 23 - Boiling Water Unit Service Maintenance Log
checkpoint | Boiling Water Unit Service Details
text | Purchased from:
text | Make:
text | Model No.:
text | Location:
text | Room Designation:
text | Installed by:
text | Installation Date:
checkpoint | Does installation comply with manufacturers instructions
checkpoint | Does the installation appear in good working order.
checkpoint | Confirm all warning lights working correctly
checkpoint | Confirm filter is clean
checkpoint | Confirm Unit is Fully Operational
checkpoint | Commissioned By:
text | Name:
text | Date:
checklist | QA 29 Periodic Flushing / Copper Protection Test Sheet |  |  | QA 29 - Periodic Flushing / Copper Protection Test Sheet
checkpoint | ITP QA 29 Periodic Flushing / Copper Protection Test Sheet
label | Copper systems are failing in the construction industry due to stagnate water being left in both hot and cold copper pipelines. Copper needs to form a protective layer of copper oxide on the internal surface which is formed by the contact with fresh aerated and oxygenated water. Periodic flushing of the systems is the only way to ensure this occurs.
label | The purpose of this ITP is to help you create the strategy to get this water out and replaced with fresh water every four weeks.
checkpoint | Flushing Details:
text | Level / building being flushed:
bool | Time and Type of flushing: | Ring main Single point for flushing; the entire loop can be achieved in a maximum 10-minute flush., Non ring mains  Any copper sub-branch from the main feed requires individual flush time of 5 minutes (an example of this would be a corridor feed)., Short branches of copper that feed rehau do not need individual flushing., Multi storey projects will require flushing on each level. Starting from the top and working your way down
text | Which fixtures are being used to flush the system (Point of connection and point of discharge):
text | Start time of flushing:
text | Zone/branch to be flushed:
text | Finish time of flushing:
text | Zone/branch to be flushed:
checkpoint | Has the schematic / layout of the flushed zone been highlighted, attached and flush points nominated.
checkpoint | Is the flushed water clear with no visible debris or dirt. If NO, discuss with project foreman and or head office on why this might be the case.
checkpoint | Have you set a reminder for the next flushing of this pipework?
checkpoint | Have the hot and cold been interconnected for flushing purposes?
checkpoint | Date for next flushing (Flushing to be performed every 4 weeks):
text | Date for next flushing:
text | Test completed by:
text | Builder Representative:
checklist | QA 30 Fixture / Hydraulic Installation |  |  | QA 30 - Fixture / Hydraulic Installation
checkpoint | What is being installed?
Bool | WC
Bool | Shower
Bool | Basin
Bool | Sink
Bool | Tapware
Bool | Boiling Water Unit
Bool | TMV Cover
Bool | RPZD Cover
Bool | Other (Specify Below)
text | Other (Specify Below)
checkpoint | Where is this fixture being installed?
text | Location
checkpoint | Have all parts been connected/completed and tested? - Pass = Yes / Fail = No (Detail why below)
checkpoint | Photos of installation been taken and uploaded below