## Table 1
M Lot No: |  |  |  |  | Lot Details: |  | Lot size/Quantity: |  |  |  |  | Date:
Item No. |  | Task/Activity Description |  | Inspection/Test | [9 empty] | HP/ WP/ AP/ IP/ TP/ SCP | Responsibility
|  |  |  | Frequency |  | Acceptance Criteria |  | Reference Documents |  | Inspection/ Test Method | Record of conformity |  |  |  | Project Engineer Principal’s Rep. Surveyor Foreman
1 |  | Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
1.1 |  | Check for correct documentation |  | Prior to commencing activity |  | Ensure that all employees and subcontractors are: - using the correct and complete set of drawings. - all drawings are the latest revision. |  | Drawings / Aconex Register |  | Verify | Drawings and drawing registers |  |  | HP* | Project Engineer
1.2 |  | Implementation of all measures and controls |  | Prior to commencing activity |  | All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP. |  | PSP, EMP, TMP, JSEA, SWMS, WP |  | Visual inspection | This ITP signed |  |  | HP* | Project Engineer
1.3 |  | Survey Checks |  | Prior to commencing activity |  | Check survey to be completed of all footing positions prior to placing any of the components. |  | Drawings |  | Verify | This ITP signed Survey Report |  |  | HP* | Project Engineer / Surveyor
1.4 |  | Material Submissions and Shop Drawings |  | Prior to commencing activity |  | HOLD POINT Items to include but not limited to: - Fuel lines - Fuel line Connections - Fuel storage materials - 900kV Diesel Generator - Fuel Tanks |  | ZULU-BECA-001-SPC-00005 - C2100 - ELECTRICAL SERVICES - GENERAL Drawings AS 1692, AS 1940:2017 and AS 1692:2006 |  | Verify | Aconex Reference |  |  | HP | Project Engineer / Principals Representative
1.5 |  | Temporary Works |  | Prior to commencing activity |  | Submission and approval of documentation based on the Temporary Design Process Matrix |  | ZULU-BECA- 001-SPC-00005 Drawings |  | Verify | As defined by the Temporary Works Design Process Matrix (where applicable) |  |  | HP* | Project Engineer
1.6 |  | Off-site Inspections |  | Each Lot |  | WITNESS POINT Inspection and attendance on site for Factory Acceptance Testing for:  Cummins Generator  Fuel tanks Following these inspections FAT testing shall be submitted. |  | ZULU-BECA- 001-SPC-00005 Drawings |  | Verify | This ITP Signed Factory Acceptance Tests |  |  | WP TP IP | Project Engineer / Principals Representative
2 |  | Construction
2.1 |  | Delivery of Materials to Site |  | Each Lot |  | Inspection of materials whilst still loaded on the truck prior to accepting the delivery on site. Identify any damage/defects prior to unloading of the material. |  | Drawings |  | Visual Inspection | This ITP Signed Materials Inspection Checklist on Conqa |  |  | IP | Project Engineer / Site Engineer
2.2 |  | Inspection of Pipes, Transition Pits, Pits, Conduits, Slabs, and Structure |  | Each Lot |  | Generator/Fuel Contractor to inspect builder’s trench to confirm suitability and as per design Generator/Fuel Contractor to install pipes, pits and conduits as per approved design. |  | Drawings |  | Visual Inspection | This ITP Signed |  |  | IP | Project Engineer / Site Engineer
2.2 |  | Lifting Preparation (900KVA Generator, 1000L Fuel Tank and 20000L Fuel Tank) |  | Each Lot |  | Complete Pre-Lift/s Commencement Checklist prior to each component being lifted. Ensure relevant drawings, lifting & fixing plans available to the crew. |  | ZULU-BECA- 001-SPC-00005 Drawings Lifting Plan |  | Visual Inspection | Pre-Lift/s Commencement Checklist This ITP Signed |  |  | IP, SCP | Site Engineer / Foreman / Surveyor
2.3 |  | Equipment Placement |  | Each Lot |  | Survey to confirm component placement as per the design. Install all fixings as per the drawings & engineers plan and suppliers’ specification. Ensuring the generator is placed on waffle mats for vibration dampening purposes and aligned properly with the radiator duct & exhaust outlet. |  | ZULU-BECA- 001-SPC-00005 Drawings Lifting Plan |  | Verify | This ITP Signed Subcontractor ITP |  |  | IP / SCP | Site Engineer / Surveyor
2.4 |  | Generator Installation |  | Each Lot |  | WITNESS POINT Installation to include but not limited to:  900KVA Generator  Flashings, trims & weatherproofing  Exhaust Mounting Bracket  Intake Cowl  Radiator Duct  Exhaust System Installation  Duct Installation  Control Panels |  | ZULU-BECA- 001-SPC-00005 Drawings Manufacturers Specification |  | Visual Inspection | This ITP Signed Factory Acceptance Tests Subcontractor ITP |  |  | WP TP | Project Engineer / Principals Representative
2.5 |  | 20000L & 1000L Fuel Tank Installation |  | Each Lot |  | WITNESS POINT Installation to include but not limited to:  20000L Fuel Tank  1000L Fuel Tank  Fuel Pump Delivery System  Fuel Control Panel  Earthing system (AS1020 & AS4897) |  | ZULU-BECA- 001-SPC-00005 Drawings Manufacturers Specification |  | Visual Inspection | This ITP Signed Factory Acceptance Tests Subcontractor ITP |  |  | WP TP | Project Engineer / Principals Representative
2.6 |  | Fuel line Connections |  | Each Lot |  | Fuel lines are to be connected between the generator and fuel cell(s) and terminated in their final positions. Ensure bend radius, connections etc are all as per manufacturers specification. |  | ZULU-BECA- 001-SPC-00005 Drawings |  | Verify | This ITP Signed Subcontractor ITP |  |  | IP | Project Engineer / Site Engineer
2.7 |  | Testing of Fuel lines |  | Each Lot |  | WITNESS POINT Fuel lines are to be pressure tested to ensure there are no leaks or weak points prior to any fuel being introduced into the system. |  | ZULU-BECA- 001-SPC-00005 Drawings |  | Verify | This ITP Signed Test results Subcontractor ITP |  |  | WP TP | Project Engineer / Principals Representative
Final Inspection The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications. Print Name: Position: Signature: Date: / /
Legend:
| HP |  | Hold Point | Work shall not proceed past the HP until released by the Principal’s Representative |  |  |  |  | IP | Inspection point |  |  | Formal Inspection to be done and recorded
| HP* |  | Fulton Hogan Hold Point | Work shall not proceed past the HP* until released by Fulton Hogan |  |  |  |  | TP | Test Point |  |  | Product compliance test to be undertaken and recorded/reported
| WP |  | Witness Point | An inspection which must be witnessed by the Principal’s Representative |  |  |  |  | SCP | Survey conformance point |  |  | A qualified surveyor to check product/section/structure and report
| AP |  | Approval Point | Written or verbal approval given by the Principal’s Representative
Notes