## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP046 - ALER 3 Fuel & Generator install | itp |  |  |  |  | FH-ZU2-QU-ITP046 - ALER 3 Fuel & Generator install - Rev 0
section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
checkpoint | 1.1 - Check for correct documentation
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - Ensure that all employees and subcontractors are:
label | — using the correct and complete set of drawings.
label | — all drawings are the latest revision.
label | Reference Documents - Drawings / Aconex Register
label | Inspection/Test Method - Verify
label | Record of conformity - Drawings and drawing registers
label | HP*
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 1.2 - Implementation of all measures and controls
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
label | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed
label | HP*
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 1.3 - Survey Checks
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - Check survey to be completed of all footing positions prior to placing any of the components.
label | Reference Documents - Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed Survey Report
label | HP*
label | Responsibility - Project Engineer / Surveyor
date | Date Completed:
checkpoint | 1.4 - Material Submissions and Shop Drawings
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - HOLD POINT
label | ○ Items to include but not limited to:
label | — Fuel lines
label | — Fuel line Connections
label | — Fuel storage materials
label | — 900kV Diesel Generator
label | — Fuel Tanks
label | Reference Documents - ZULU-BECA-001-SPC-00005-C2100 - ELECTRICAL SERVICES - GENERAL Drawings AS 1692, AS 1940:2017 and AS 1692:2006
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex Reference
label | HP
label | Responsibility - Project Engineer / Principals Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.5 - Temporary Works
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - Submission and approval of documentation based on the Temporary Design Process Matrix
label | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - As defined by the Temporary Works Design Process Matrix (where applicable)
label | HP*
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 1.6 - Off-site Inspections
label | Frequency - Each Lot
label | Acceptance Criteria - WITNESS POINT
label | ○ Inspection and attendance on site for Factory Acceptance Testing for:
label | — Cummins Generator
label | — Fuel tanks
label | ○ Following these inspections FAT testing shall be submitted.
label | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed Factory Acceptance Tests
label | WP, TP, IP
label | Responsibility - Project Engineer / Principals Representative
date | Date Completed:
section | 2.0 - Construction
checkpoint | 2.1 - Delivery of Materials to Site
label | Frequency - Each Lot
label | Acceptance Criteria - Inspection of materials whilst still loaded on the truck prior to accepting the delivery on site.
label | ○ Identify any damage/defects prior to unloading of the material.
label | Reference Documents - Drawings
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed, Materials Inspection Checklist on Conqa
label | IP
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 2.2 - Inspection of Pipes, Transition Pits, Pits, Conduits, Slabs, and Structure
label | Frequency - Each Lot
label | Acceptance Criteria - Generator/Fuel Contractor to inspect builder’s trench to confirm suitability and as per design
label | ○ Generator/Fuel Contractor to install pipes, pits and conduits as per approved design.
label | Reference Documents - Drawings
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed
label | IP
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 2.2 - Lifting Preparation (900KVA Generator, 1000L Fuel Tank and 20000L Fuel Tank)
label | Frequency - Each Lot
label | Acceptance Criteria - Complete Pre-Lift/s Commencement Checklist prior to each component being lifted.
label | ○ Ensure relevant drawings, lifting & fixing plans available to the crew.
label | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings Lifting Plan
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - Pre-Lift/s Commencement Checklist This ITP Signed
label | IP, SCP
label | Responsibility - Site Engineer / Foreman / Surveyor
date | Date Completed:
checkpoint | 2.3 - Equipment Placement
label | Frequency - Each Lot
label | Acceptance Criteria - Survey to confirm component placement as per the design.
label | ○ Install all fixings as per the drawings & engineers plan and suppliers’ specification.
label | ○ Ensuring the generator is placed on waffle mats for vibration dampening purposes and aligned properly with the radiator duct & exhaust outlet.
label | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings Lifting Plan
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed Subcontractor ITP
label | IP / SCP
label | Responsibility - Site Engineer / Surveyor
date | Date Completed:
checkpoint | 2.4 - Generator Installation
label | Frequency - Each Lot
label | Acceptance Criteria - WITNESS POINT
label | ○ Installation to include but not limited to:
label | — 900KVA Generator
label | — Flashings, trims & weatherproofing
label | — Exhaust Mounting Bracket
label | — Intake Cowl
label | — Radiator Duct
label | — Exhaust System Installation
label | — Duct Installation
label | — Control Panels
label | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings, Manufacturers Specification
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed Factory Acceptance Tests, Subcontractor ITP
label | WP TP
label | Responsibility - Project Engineer / Principals Representative
date | Date Completed:
checkpoint | 2.5 - 20000L & 1000L Fuel Tank Installation
label | Frequency - Each Lot
label | Acceptance Criteria - WITNESS POINT
label | ○ Installation to include but not limited to:
label | — 20000L Fuel Tank
label | — 1000L Fuel Tank
label | — Fuel Pump Delivery System
label | — Fuel Control Panel
label | — Earthing system (AS1020 & AS4897)
label | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings, Manufacturers Specification
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP Signed Factory Acceptance Tests, Subcontractor ITP
label | WP TP
label | Responsibility - Project Engineer / Principals Representative
date | Date Completed:
checkpoint | 2.6 - Fuel line Connections
label | Frequency - Each Lot
label | Acceptance Criteria - Fuel lines are to be connected between the generator and fuel cell(s) and terminated in their final positions.
label | ○ Ensure bend radius, connections etc are all as per manufacturers specification.
label | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed Subcontractor ITP
label | IP
label | Responsibility - Project Engineer / Site Engineer
date | Date Completed:
checkpoint | 2.7 - Testing of Fuel lines
label | Frequency - Each Lot
label | Acceptance Criteria - WITNESS POINT
label | ○ Fuel lines are to be pressure tested to ensure there are no leaks or weak points prior to any fuel being introduced into the system.
label | Reference Documents - ZULU-BECA- 001-SPC-00005 Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP Signed Test results, Subcontractor ITP
label | WP TP
label | Responsibility - Project Engineer / Principals Representative
date | Date Completed:
checkpoint | Final Inspection
label | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
date | Work Completed On:
date | Date: