## ITC Prefixes
ITC prefix | ITC Type | ITC prefix | ITC Type
Electrical |  | Mechanical
E01 | In Ground services Install | M01A | BMS panel rough in
E02 | In Slab Services Install | M01B | sensor fit off - BMS/
E03 | Cable Rough In | M01C | BMS panel fit off
E04 | Cable Tray Installation | M02A | MECHANICAL rough in
E05 | MSB | M02B | Mechanical Fit OFF
E06 | DB | M03 | Electrical rough in
E07 | Luminaires | M04A | DX Split Systems ROUGH IN
E08 | Power Fit-Off | M04B | DX Split Systems FIT OFF
E09 | Data Fit-Off | M05A | Exhaus Systems rough in
E10 | MSPs | M05B | Exhaus Systems fit off
E11 | Generator | M07 | Grilles/Cushion Boxes
E12 | UPS | M08 | Mech Plumbing
E13 | Lightning Protection | M09 | Electrical Fit off
|  | M10 | AHU Insulation
|  | M11 | Pipe work insualtion
External Electrical
E11 | Light Poles
E12 | Security Cameras
E13 | Carpark Duress | Medical Gas
Security |  | MG01 | Pipework
|  | MG02 | Outlets
|  | MG03 | Manifolds
|  | MG05 | Gas Alarm
|  | MG06 | ZVB
Communications
Nurse Call |  | C01 | WAPS Fit-off
|  | C02 | Communications rack install
Fire Detection
|  | F01 | Field Devices
|  | F02 | FIP
Fire Protection
|  | F03 | Hydrant Systems
|  | F04 | Hose Reels
Hydraulic
|  | H01 | Sanitary Fixtures
|  | H02 | Pipework - Pressure Tests
|  | H03 | Pumps
|  | H04 | RO System
|  | H05 | Hot Water System/Unit
|  | H06 | TVM's
|  | H07 | Backflow Prevention Devices

## ITC Worklot Register Mechanical
ITC Worklot Register
Subcontractor | Dewpoint
Services Discipline | ITC Name | ITC Prefix (refer next sheet for prefixes) | ITC Type | Worklot No. | ITC No. | Status | Date | Comments
e.g., Electrical Services | Electrical Distribution Board (DB-RENAL) | E02 | DB | PER-ITC-E02 | PER-ITC-E02-001 | Open | 2022-12-08 | Half complete, remainder to be completed by 5/12
MEDICAL GAS | REHABILITATION-ROOM 0.2.000 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 0.2.000-001 |  |  |  | Comments Requiring Actions/Responses Medical Gas:- ZVIB ITCS to become a Fit-off ITC. Separate ITC for Medical Gas Cabling rough-in to be be produced for each Zone/level. This can be incorporated by using ITC Electrical Rough-in M03 . MGAP ITCS to become a Fit-off ITC. Separate ITC for Medical Gas Electrical rough-in to be be produced for each Zone/level. This Can be incorporated by using ITC Electrical Roug-in M03. Cold Rooms:- No Cold Room ITCs Provided. To be provided for review. BMS:- Rename BMS Panel Fit-off ITC (E.G.M01C) to separate it from BMS Sensor Fit-off. These are different ITCs with different checklists. Check List item to be added to BMS Panel Fit-off for BMS Dead Point to Point testing completed and results provided with ITC. Checklist item to be added to reflect this on the ITC. Mechanical Plumbing:- M08 does not cover off on Pressure testing in the checklist items. Add a check list item to M08 for the pressure test of the installation and remove the pressure test ITC from the ITC register. Mechanical Electrical:- ITC Not Re-submitted with changes requested from last HB review on 2/5/24. Use Electrical Rough-in M03 document to cover off on the Medical Gas Cabling Installation. Additional ITCs have been added to the register and highlighted orange Fan and AHU Install:- AHU/Fan Fit-off ITC's have three prefixes 2B, 5B & 6B, when they are exactly the same checklist items? This is not required. Remove the mention of 5B and 6B as the system being covered by the ITC is in the name and will be referenced on the ITC. Fan Rough-in ITC's have two prefixes 5A & 6A, when they are exactly the same checklist items? This is not required. Remove the mention of 6A as the system being covered by the ITC is in the name and will be referenced on the ITC. ITC Reister:- ITC No. Column needs to be completed. This had the incorrect information in the previous Dewpoint update. This has been moved to the relevant column (ITC Name) in this revision ITC Prefixes to be reviewed, removed and added to cover the above comments.
| REHABILITATION-ROOM 0.2.003 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 0.2.003-002
| REHABILITATION-ROOM 0.2.004 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 0.2.004-003
| REHABILITAITON-ROOM 0.2.007 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 0.2.007-004
| REHABILITATION-ROOM 0.2.008 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 0.2.008-005
| REHABILITATION-ROOM 0.2.011 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 0.2.011-006
| REHABILITATION-ROOM 0.2.014 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 0.2.014-007
| REHABILITATON-ROOM 0.2.017 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 0.2.017-008
| REHABILITATION-ROOM 0.2.018 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 0.2.018-009
| SHARED THERAPY-ROOM 0.3.017 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 0.3.017-010
| SHARED THERAPY-ROOM 0.3.001 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 0.3.001-011
| SHARED THERAPY-ROOM 0.3.003 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 0.3.003-012
| REHABILITATION-ROOM 0.2.066 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 0.2.066-013
| REHABILITATION-ROOM 0.2.067 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 0.2.067-014
| REHABILITATION- ROOM 0.2.062 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02- ROOM 0.2.062-015
| REHABILITATION- ROOM 0.2.063 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02- ROOM 0.2.063-016
| REHABILITATION-ROOM 0.2.059 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 0.2.059-017
| REHABILITATION- ROOM 0.2.049 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02- ROOM 0.2.049-018
| REHABILITATION-ROOM 0.2.054 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 0.2.054-019
| REHABILITATION- ROOM 0.2.051 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02- ROOM 0.2.051-020
| REHABILITATION-ROOM 0.2.055 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 0.2.055-021
| REHABILITATION-L0 OXYGEN RING MAIN | MG01 | MED GAS PIPEWORK | DPA-ITC-MG01 | DPA-ITC-MG01-L0 OXYGEN RING MAIN-001
| REHABILITATION-L0 SUCTION RING MAIN | MG01 | MED GAS PIPEWORK | DPA-ITC-MG01 | DPA-ITC-MG01-L0 SUCTION RING MAIN-002
| REHABILITATION-L0 MEDICAL AIR RING MAIN | MG01 | MED GAS PIPEWORK | DPA-ITC-MG01 | DPA-ITC-MG01-L0 MEDICAL AIR RING MAIN-003
| REHABILITATION-L0 MEDICAL GAS CABLING | M03 | Medical Gas Cabling | DPA-ITC-M03 | DPA-ITC-MG01-L0 MEDICAL GAS CABLING -001 |  |  | Add to cover Medical Gas ELV Cabling Installation
| REHABILITATION MEDICAL GAS VALVE ISOLATION BOX - MGVB-00-1 | MG06 | MGVB | DPA-ITC-MG06 | DPA-ITC-MG06- MEDICAL GAS VALVE ISOLATION BOX - MGVB-00-1-001 |  |  | ZVIB ITCS to become a Fit-off ITC. Separate ITC for Medical Gas Cabling rough-in to be be produced for each Zone/level. This can be incorporated by using ITC Electrical Rough-in M03 .
| FOH-MEDICAL GAS VALVE ISOLATION BOX - MGVB-00-2 | MG06 | MGVB | DPA-ITC-MG06 | DPA-ITC-MG06-MEDICAL GAS VALVE ISOLATION BOX - MGVB-00-2-002 |  |  | ZVIB ITCS to become a Fit-off ITC. Separate ITC for Medical Gas Cabling rough-in to be be produced for each Zone/level. This can be incorporated by using ITC Electrical Rough-in M03 .
| REHABILITATION-MEDICAL GAS ALARM PANEL - MGAP-00-1 | MG05 | MGAP | DPA-ITC-MG05 | DPA-ITC-MG05-MEDICAL GAS ALARM PANEL - MGAP-00-1-001 |  |  | MGAP ITCS to become a Fit-off ITC. Separate ITC for Medical Gas Electrical rough-in to be be produced for each Zone/level. This Can be incorporated by using ITC Electrical Roug-in M03.
| REHABILITATION-MEDICAL GAS ALARM PANEL - MGAP-00-2 | MG05 | MGAP | DPA-ITC-MG05 | DPA-ITC-MG05-MEDICAL GAS ALARM PANEL - MGAP-00-2-002 |  |  | MGAP ITCS to become a Fit-off ITC. Separate ITC for Medical Gas Electrical rough-in to be be produced for each Zone/level. This Can be incorporated by using ITC Electrical Roug-in M03.
| FOH-MEDICAL GAS ALARM PANEL - MGAP-00-3 | MG05 | MGAP | DPA-ITC-MG05 | DPA-ITC-MG05-MEDICAL GAS ALARM PANEL - MGAP-00-3-003 |  |  | MGAP ITCS to become a Fit-off ITC. Separate ITC for Medical Gas Electrical rough-in to be be produced for each Zone/level. This Can be incorporated by using ITC Electrical Roug-in M03.
| GAS STORE ROOM-MEDICAL GAS ALARM PANEL - MGAP-00-4 | MG05 | MGAP | DPA-ITC-MG05 | DPA-ITC-MG05-MEDICAL GAS ALARM PANEL - MGAP-00-4-004 |  |  | MGAP ITCS to become a Fit-off ITC. Separate ITC for Medical Gas Electrical rough-in to be be produced for each Zone/level. This Can be incorporated by using ITC Electrical Roug-in M03.
| GEM THERAPY-ROOM 1.1.002 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 1.1.002- 022
| GEM THERAPY-ROOM 1.1.003 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 1.1.003-023
| GEM THERAPY-ROOM 1.1.006 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 1.1.006-024
| GEM THERAPY-ROOM 1.1.007 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 1.1.007-025
| GEM THERAPY-ROOM 1.1.010 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 1.1.010-026
| GEM THERAPY-ROOM 1.1.013 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 1.1.013-027
| GEM THERAPY-ROOM 1.1.014 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 1.1.014-028
| GEM THERAPY-ROOM 1.1.017 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 1.1.017-029
| GEM THERAPY-ROOM 1.1.018 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 1.1.018-030
| TRANSIT-ROOM 1.1.020 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 1.1.020-031
| GEM THERAPY-ROOM 1.1.069 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 1.1.069-032
| GEM THERAPY-ROOM 1.1.068 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 1.1.068-033
| GEM THERAPY-ROOM 1.1.065 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 1.1.065-034
| GEM THERAPY-ROOM 1.1.062 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 1.1.062-035
| GEM THERAPY-ROOM 1.1.061 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 1.1.061-036
| GEM THERAPY-ROOM 1.1.058 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 1.1.058-037
| GEM THERAPY- ROOM 1.1.057 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02- ROOM 1.1.057-038
| GEM THERAPY-ROOM 1.1.054 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 1.1.054-039
| GEM THERAPY-ROOM 1.1.053 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 1.1.053-040
| GEM THERAPY-ROOM 1.1.050 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 1.1.050-041
| GEM THERAPY -TERRACE 1.E099 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-TERRACE 1.1.E099-042 |  |  | ADDED IN AS SHOWING ON SCHEMATIC
| GEM THERAPY-L1 OXYGEN RING MAIN | MG01 | MED GAS PIPEWORK | DPA-ITC-MG01 | DPA-ITC-MG01-L1 OXYGEN RING MAIN-004
| GEM THERAPY-L1 SUCTION RING MAIN | MG01 | MED GAS PIPEWORK | DPA-ITC-MG01 | DPA-ITC-MG01-L1 SUCTION RING MAIN-005
| GEM THERAPY-L1 MEDICAL AIR RING MAIN | MG01 | MED GAS PIPEWORK | DPA-ITC-MG01 | DPA-ITC-MG01-L1 MEDICAL AIR RING MAIN-006
| GEM THERAPY-L1 MEDICAL GAS CABLING | M03 | Medical Gas Cabling | DPA-ITC-M03 | DPA-ITC-MG01L1 MEDICAL GAS CABLING-002 |  |  | Add to cover Medical Gas ELV Cabling Installation
| GEM THERAPY -MEDICAL GAS VALVE ISOLATION BOX - MGVB-01-1 | MG06 | MGVB | DPA-ITC-MG06 | DPA-ITC-MG06-MEDICAL GAS VALVE ISOLATION BOX - MGVB-01-1-003 |  |  | ZVIB ITCS to become a Fit-off ITC. Separate ITC for Medical Gas Cabling rough-in to be be produced for each Zone/level. This can be incorporated by using ITC Electrical Rough-in M03 .
| GEM THERAPY-MEDICAL GAS ALARM PANEL - MGAP-01-1 | MG05 | MGAP | DPA-ITC-MG05 | DPA-ITC-MG05-MEDICAL GAS ALARM PANEL - MGAP-01-1-005 |  |  | MGAP ITCS to become a Fit-off ITC. Separate ITC for Medical Gas Electrical rough-in to be be produced for each Zone/level. This Can be incorporated by using ITC Electrical Roug-in M03.
| GEM THERAPY-MEDICAL GAS ALARM PANEL - MGAP-01-2 | MG05 | MGAP | DPA-ITC-MG05 | DPA-ITC-MG05-MEDICAL GAS ALARM PANEL - MGAP-01-2-006 |  |  | MGAP ITCS to become a Fit-off ITC. Separate ITC for Medical Gas Electrical rough-in to be be produced for each Zone/level. This Can be incorporated by using ITC Electrical Roug-in M03.
| PALLIATIVE CARE-ROOM 2.1.000 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 2.1.000-043
| PALLIATIVE CARE-ROOM 2.1.003 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 2.1.003-044
| PALLIATIVE CARE-ROOM 2.1.004 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 2.1.004-45 |  |  | ADDED IN AS SHOWING ON SCHEMATIC
| PALLIATIVE CARE-ROOM 2.1.007 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 2.1.007-046
| PALLIATIVE CARE-ROOM 2.1.008 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 2.1.008-047
| PALLIATIVE CARE-ROOM 2.1.011 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 2.1.011-048
| PALLIATIVE CARE-ROOM 2.1.015 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 2.1.015-049
| PALLIATIVE CARE-ROOM 2.1.017 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 2.1.017-050
| PALLIATIVE CARE-ROOM 2.1.075 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 2.1.075-051
| PALLIATIVE CARE-ROOM 2.1.074 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 2.1.074-052
| PALLIATIVE CARE- ROOM 2.1.071 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02- ROOM 2.1.071-053
| PALLIATIVE CARE-ROOM 2.1.070 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 2.1.070-054
| PALLIATIVE CARE-ROOM 2.1.067 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 2.1.067-055
| PALLIATIVE CARE-ROOM 2.1.066 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 2.1.066-056
| PALLIATIVE CARE-ROOM 2.1.063 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 2.1.063-057
| PALLIATIVE CARE-ROOM 2.1.062 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 2.1.062-058
| PALLIATIVE CARE-ROOM 2.1.059 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 2.1.059-059
| PALLIATIVE CARE-ROOM 2.1.058 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 2.1.058-060
| PALLIATIVE CARE-ROOM 2.1.055 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 2.1.055-061
| PALLIATIVE CARE-ROOM 2.1.054 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 2.1.054-062
| PALLIATIVE CARE-ROOM 2.1.051 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 2.1.051-063
| PALLIATIVE CARE-ROOM 2.1.050 | MG02 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-ROOM 2.1.050-064
| PALLIATIVE CARE-TERRACE 2.E.099 | MG03 | Outlets | DPA-ITC-MG02 | DPA-ITC-MG02-TERRACE 2.E.099-65 |  |  | ADDED IN AS SHOWING ON SCHEMATIC, AS UPDATED
| PALLIATIVE CARE-L2 OXYGEN RING MAIN | MG01 | Pipework | DPA-ITC-MG01 | DPA-ITC-MG01-L2 OXYGEN RING MAIN-007
| PALLIATIVE CARE-L2 SUCTION RING MAIN | MG01 | Pipework | DPA-ITC-MG01 | DPA-ITC-MG01-L2 SUCTION RING MAIN-008
| PALLIATIVE CARE-L2 MEDICAL AIR RING MAIN | MG01 | Pipework | DPA-ITC-MG01 | DPA-ITC-MG01-L2 MEDICAL AIR RING MAIN-009
| PALLIATIVE CARE-L2 MEDICAL GAS CABLING | M03 | Medical Gas Cabling | DPA-ITC-M03 | DPA-ITC-M03-L2 MEDICAL GAS CABLING-003 |  |  | Add to cover Medical Gas ELV Cabling Installation
| PALLIATIVE CARE-MGVB-02-1 | MG06 | MGVB | DPA-ITC-MG06 | DPA-ITC-MG06-MGVB-02-1-004 |  |  | ZVIB ITCS to become a Fit-off ITC. Separate ITC for Medical Gas Cabling rough-in to be be produced for each Zone/level. This can be incorporated by using ITC Electrical Rough-in M03 .
| PALLIATIVE CARE MGAP-02-1 | MG05 | MGAP | DPA-ITC-MG05 | DPA-ITC-MG05- MGAP-02-1-007 |  |  | MGAP ITCS to become a Fit-off ITC. Separate ITC for Medical Gas Electrical rough-in to be be produced for each Zone/level. This Can be incorporated by using ITC Electrical Roug-in M03.
| PALLIATIVE CARE-MGAP-02-2 | MG05 | MGAP | DPA-ITC-MG05 | DPA-ITC-MG05-MGAP-02-2-008 |  |  | MGAP ITCS to become a Fit-off ITC. Separate ITC for Medical Gas Electrical rough-in to be be produced for each Zone/level. This Can be incorporated by using ITC Electrical Roug-in M03.
| DPA-ITC-MG03-PLANT FITOFF - ROOM 2.E.007 | MG03 | MG03-MED GAS PLANT FIT OFF | DPA-ITC-MG03 | DPA-ITC-MG03-PLANT FITOFF - ROOM 2.E.007-004
REFRIGERATION - COOLROOMS | FDC-00-1 SYSTEM ROUGH IN | M04A | DX Coolrooms | DPA-ITC-M04A | DPA-ITC-M04A-001 FDC-00-1 SYSTEM ROUGH IN-001
| FDC-00-2 SYSTEM ROUGH IN | M04A | DX Coolrooms | DPA-ITC-M04A | DPA-ITC-M04A-002-FDC-00-2 SYSTEM ROUGH IN -002
| FDC-00-3 SYSTEM ROUGH IN | M04A | DX Coolrooms | DPA-ITC-M04A | DPA-ITC-M04A-003-FDC-00-3 SYSTEM ROUGH IN-003
| COOLROOM 1 ROUGH IN | M04A | DX Coolrooms | DPA-ITC-M04A | DPA-ITC-M04A-004-COOLROOM 1 ROUGH IN-004 |  |  | No cold room ITCs provided. To be provided for review ASAP.
| COOLROOM 2 ROUGH IN | M04A | DX Coolrooms | DPA-ITC-M04A | DPA-ITC-M04A-005-COOLROOM 2 ROUGH IN-005 |  |  | No cold room ITCs provided. To be provided for review ASAP.
| FREEZER ROOM ROUGH IN | M04A | DX Coolrooms | DPA-ITC-M04A | DPA-ITC-M04A-006-FREEZER ROOM ROUGH IN-006 |  |  | No cold room ITCs provided. To be provided for review ASAP.
REFRIGERATION - COOLROOMS | FDC-00-1 SYSTEM FIT OFF | M04B | DX Coolrooms | DPA-ITC-M04B | DPA-ITC-M04B-001-FDC-00-1 SYSTEM FIT OFF-001
| FDC-00-2 SYSTEM FIT OFF | M04B | DX Coolrooms | DPA-ITC-M04B | DPA-ITC-M04B-002-FDC-00-2 SYSTEM FIT OFF-002
| FDC-00-3 SYSTEM FIT OFF | M04B | DX Coolrooms | DPA-ITC-M04B | DPA-ITC-M04B-003- FDC-00-3 SYSTEM FIT OFF-003
| COOLROOM 1 FIT OFF | M04B | DX Coolrooms | DPA-ITC-M04B | DPA-ITC-M04B-004- COOLROOM 1 FIT OFF-004 |  |  | No cold room ITCs provided. To be provided for review ASAP.
| COOLROOM 2 FIT OFF | M04B | DX Coolrooms | DPA-ITC-M04B | DPA-ITC-M04B-005- COOLROOM 2 FIT OFF-005 |  |  | No cold room ITCs provided. To be provided for review ASAP.
| FREEZER ROOM FIT OFF | M04B | DX Coolrooms | DPA-ITC-M04B | DPA-ITC-M04B-006- FREEZER ROOM FIT OFF-006 |  |  | No cold room ITCs provided. To be provided for review ASAP.
REFRIGERATION - DX A/C | CU-00-1 SYSTEM - AC-00-1.1 AND AC-00-1.2 | M04A | DX Split Systems - Rough in | DPA-ITC-M04A | DPA-ITC-M04A-CU-00-1 SYSTEM - AC-00-1.1 AND AC-00-1.2-001
| CU-00-2 SYSTEM - AC-00-2.1 AND AC-00-2.2 | M04A | DX Split Systems - Rough in | DPA-ITC-M04A | DPA-ITC-M04A-CU-00-2 SYSTEM - AC-00-2.1 AND AC-00-2.2-002
| CU-00-3 SYSTEM - AC-00-3.1 AND AC-00-3.2 | M04A | DX Split Systems - Rough in | DPA-ITC-M04A | DPA-ITC-M04A-CU-00-3 SYSTEM - AC-00-3.1 AND AC-00-3.2-003
| CU-00-4 SYSTEM - AC-00-4.1 AND AC-00-4.2 | M04A | DX Split Systems - Rough in | DPA-ITC-M04A | DPA-ITC-M04A-CU-00-4 SYSTEM - AC-00-4.1 AND AC-00-4.2-004
| CU-01-1 SYSTEM - AC-01-1.1 AND AC-01-1.2 | M04A | DX Split Systems - Rough in | DPA-ITC-M04A | DPA-ITC-M04A-CU-01-1 SYSTEM - AC-01-1.1 AND AC-01-1.2-005
| CU-01-2 SYSTEM - AC-01-2.1 AND AC-01-2.2 | M04A | DX Split Systems - Rough in | DPA-ITC-M04A | DPA-ITC-M04A-CU-01-2 SYSTEM - AC-01-2.1 AND AC-01-2.2-006
| CU-02-1 SYSTEM - AC-02-1.1 AND AC-02-1.2 | M04A | DX Split Systems - Rough in | DPA-ITC-M04A | DPA-ITC-M04A-CU-02-1 SYSTEM - AC-02-1.1 AND AC-02-1.2-007
| CU-02-2 SYSTEM - AC-02-2.1 AND AC-02-2.2 | M04A | DX Split Systems - Rough in | DPA-ITC-M04A | DPA-ITC-M04A-CU-02-2 SYSTEM - AC-02-2.1 AND AC-02-2.2-008
| CU-02-3 SYSTEM - AC-02-3 | M04A | DX Split Systems - Rough in | DPA-ITC-M04A | DPA-ITC-M04A-CU-02-3 SYSTEM - AC-02-3-009
| CU-02-4 SYSTEM - AC-02-4 | M04A | DX Split Systems - Rough in | DPA-ITC-M04A | DPA-ITC-M04A-CU-02-4 SYSTEM - AC-02-4-010
| CU-02-5 SYSTEM - AC-02-5 | M04A | DX Split Systems - Rough in | DPA-ITC-M04A | DPA-ITC-M04A-CU-02-5 SYSTEM - AC-02-5-011
| CU-02-6 SYSTEM - AC-02-6 | M04A | DX Split Systems - Rough in | DPA-ITC-M04A | DPA-ITC-M04A-CU-02-6 SYSTEM - AC-02-6-012
| CU-SMSR-1 SYSTEM | M04A | DX Split Systems - Rough in | DPA-ITC-M04A | DPA-ITC-M04A-CU-SMSR-1 SYSTEM -013
| CU-SMSR-2 SYSTEM | M04A | DX Split Systems - Rough in | DPA-ITC-M04A | DPA-ITC-M04A-CU-SMSR-2 SYSTEM -014
| CU-PR-1 SYSTEM - AC-PR-1.1 AND AC-PR-1.2 | M04A | DX Split Systems - Rough in | DPA-ITC-M04A | DPA-ITC-M04A-CU-PR-1 SYSTEM - AC-PR-1.1 AND AC-PR-1.2-015
| CU-00-5 SYSTEM - AC-00-5 | M04A | DX Split Systems - Rough in | DPA-ITC-M04A | DPA-ITC-M04A-CU-00-5 SYSTEM - AC-00-5-016
| CU-00-6 SYSTEM - AC-00-6 | M04A | DX Split Systems - Rough in | DPA-ITC-M04A | DPA-ITC-M04A-CU-00-6 SYSTEM - AC-00-6-017
REFRIGERATION - DX A/C | CU-00-1 SYSTEM - AC-00-1.1 AND AC-00-1.2 | M04B | DX Split Systems - Fit Off | DPA-ITC-M04B | DPA-ITC-M04B-CU-00-1 SYSTEM - AC-00-1.1 AND AC-00-1.2-001
| CU-00-2 SYSTEM - AC-00-2.1 AND AC-00-2.2 | M04B | DX Split Systems - Fit Off | DPA-ITC-M04B | DPA-ITC-M04B-CU-00-2 SYSTEM - AC-00-2.1 AND AC-00-2.2-002
| CU-00-3 SYSTEM - AC-00-3.1 AND AC-00-3.2 | M04B | DX Split Systems - Fit Off | DPA-ITC-M04B | DPA-ITC-M04B-CU-00-3 SYSTEM - AC-00-3.1 AND AC-00-3.2-003
| CU-00-4 SYSTEM - AC-00-4.1 AND AC-00-4.2 | M04B | DX Split Systems - Fit Off | DPA-ITC-M04B | DPA-ITC-M04B-CU-00-4 SYSTEM - AC-00-4.1 AND AC-00-4.2-004
| CU-01-1 SYSTEM - AC-01-1.1 AND AC-01-1.2 | M04B | DX Split Systems - Fit Off | DPA-ITC-M04B | DPA-ITC-M04B-CU-01-1 SYSTEM - AC-01-1.1 AND AC-01-1.2-005
| CU-01-2 SYSTEM - AC-01-2.1 AND AC-01-2.2 | M04B | DX Split Systems - Fit Off | DPA-ITC-M04B | DPA-ITC-M04B-CU-01-2 SYSTEM - AC-01-2.1 AND AC-01-2.2-006
| CU-02-1 SYSTEM - AC-02-1.1 AND AC-02-1.2 | M04B | DX Split Systems - Fit Off | DPA-ITC-M04B | DPA-ITC-M04B-CU-02-1 SYSTEM - AC-02-1.1 AND AC-02-1.2-007
| CU-02-2 SYSTEM - AC-02-2.1 AND AC-02-2.2 | M04B | DX Split Systems - Fit Off | DPA-ITC-M04B | DPA-ITC-M04B-CU-02-2 SYSTEM - AC-02-2.1 AND AC-02-2.2-008
| CU-02-3 SYSTEM - AC-02-3 | M04B | DX Split Systems - Fit Off | DPA-ITC-M04B | DPA-ITC-M04B-CU-02-3 SYSTEM - AC-02-3-009
| CU-02-4 SYSTEM - AC-02-4 | M04B | DX Split Systems - Fit Off | DPA-ITC-M04B | DPA-ITC-M04B-CU-02-4 SYSTEM - AC-02-4-010
| CU-02-5 SYSTEM - AC-02-5 | M04B | DX Split Systems - Fit Off | DPA-ITC-M04B | DPA-ITC-M04B-CU-02-5 SYSTEM - AC-02-5-011
| CU-02-6 SYSTEM - AC-02-6 | M04B | DX Split Systems - Fit Off | DPA-ITC-M04B | DPA-ITC-M04B-CU-02-6 SYSTEM - AC-02-6-012
| CU-SMSR-1 SYSTEM | M04B | DX Split Systems - Fit Off | DPA-ITC-M04B | DPA-ITC-M04B-CU-SMSR-1 SYSTEM -013
| CU-SMSR-2 SYSTEM | M04B | DX Split Systems - Fit Off | DPA-ITC-M04B | DPA-ITC-M04B-CU-SMSR-2 SYSTEM -014
| CU-PR-1 SYSTEM | M04B | DX Split Systems - Fit Off | DPA-ITC-M04B | DPA-ITC-M04B-CU-PR-1 SYSTEM -015
| CU-00-5 SYSTEM - AC-00-5 | M04B | DX Split Systems - Fit Off | DPA-ITC-M04B | DPA-ITC-M04B-CU-00-5 SYSTEM - AC-00-5-016
| CU-00-6 SYSTEM - AC-00-6 | M04B | DX Split Systems - Fit Off | DPA-ITC-M04B | DPA-ITC-M04B-CU-00-6 SYSTEM - AC-00-6-017
BUILDING MANAGEMENT SYSTEM | BMS-MSSB-01-1 | M01A | BMS Panel Rough In | DPA-ITC-M01A | DPA-ITC-M01A-BMS-MSSB-01-1-001
| BMS-MSSB-02-4 | M01A | BMS Panel Rough In | DPA-ITC-M01A | DPA-ITC-M01A-BMS-MSSB-02-4-002
| SUB-1 | M01A | BMS Panel Rough In | DPA-ITC-M01A | DPA-ITC-M01A-SUB-1-003
| PR-1 | M01A | BMS Panel Rough In | DPA-ITC-M01A | DPA-ITC-M01A-PR-1-004
| BMS-MSSB-01-1 | M01C | BMS Panel Fit Off | DPA-ITC-M01C | DPA-ITC-M01C-BMS-MSSB-01-1-001 |  |  | CHANGED TO M01C
| BMS-MSSB-02-4 | M01C | BMS Panel Fit Off | DPA-ITC-M01C | DPA-ITC-M01C-BMS-MSSB-02-4-002
| SUB-1 | M01C | BMS Panel Fit Off | DPA-ITC-M01C | DPA-ITC-M01C-SUB-1-003
| PR-1 | M01C | BMS Panel Fit Off | DPA-ITC-M01C | DPA-ITC-M01C-PR-1-004
| BOH-ROOM 0.4.002 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.4.002-001
| BOH-ROOM 0.4.004 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.4.004-002
| BOH-ROOM 0.4.006 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.4.006-003
| BOH-ROOM 0.4.010 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.4.010-004
| BOH-ROOM 0.4.014 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.4.014-005
| REHABILITATION-ROOM 0.2.055 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.2.055-006
| REHABILITATION-ROOM 0.2.049 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.2.049-007
| REHABILITATION-ROOM 0.2.063 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.2.063-008
| REHABILITATION-ROOM 0.2.067 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B- ROOM 0.2.067-009
| REHABILITATION-ROOM 0.2.036 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B- ROOM 0.2.036-010
| REHABILITATION-ROOM 0.2.034 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.2.034-011
| REHABILITATION-ROOM 0.2.033 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.2.033-012
| REHABILITATION-ROOM 0.2.031 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.2.031-013
| REHABILITATION-ROOM 0.2.028 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.2.028-014
| REHABILITATION-ROOM 0.2.000 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.2.000-015
| REHABILITATION-ROOM 0.2.003 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.2.003-016
| REHABILITATION-ROOM 0.2.011 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.2.011-017
| REHABILITATION-ROOM 0.2.015 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.2.015-018
| REHABILITATION-ROOM 0.2.018 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.2.018-019
| FOH-ROOM 0.1.004 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B- ROOM 0.1.004-020
| FOH-ROOM 0.1.003 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.1.003-021
| FOH-ROOM 0.1.010 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.1.010-022
| FOH-ROOM 0.1.009 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.1.009-023
| FOH-ROOM 0.1.001 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B- ROOM 0.1.001-024
| SHARED THERAPY-ROOM 0.3.008 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.3.008-025
| SHARED THERAPY-ROOM 0.3.006 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.3.006-026
| SHARED THERAPY-ROOM 0.3.013 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.3.013-027
| SHARED THERAPY-ROOM 0.3.016 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.3.016-028
| SHARED THERAPY-ROOM 0.3.017 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 0.3.017-029
| GEM THERAPY-ROOM 1.1.000 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-Mo1B-ROOM 1.1.000-030
| GEM THERAPY-ROOM 1.1.007 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 1.1.007-031
| GEM THERAPY- ROOM 1.1.010 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B- ROOM 1.1.010-032
| GEM THERAPY-ROOM 1.1.014 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 1.1.014-033
| SHARED PATIENT AREA-ROOM 1.1.020 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 1.1.020-034
| GEM THERAPY-ROOM 1.1.038 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 1.1.038-035
| GEM THERAPY- ROOM 1.1.036 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B- ROOM 1.1.036-036
| GEM THERAPY-ROOM 1.1.035 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 1.1.035-037
| GEM THERAPY-ROOM 1.1.033 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 1.1.033-038
| GEM THERAPY-ROOM 1.1.029 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 1.1.029-039
| GEM THERAPY-ROOM 1.1.022 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 1.1.022-040
| SHARED ADMINISTRATION-ROOM 1.2.002 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 1.2.002-041
| SHARED ADMINISTRATION-ROOM 1.2.014 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 1.2.014-042
| SHARED ADMINISTRATION - ROOM 1.2.013 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B- ROOM 1.2.013-043
| SHARED ADMINISTRATION- ROOM 1.2.010 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B- ROOM 1.2.010-044
| SHARED ADMINISTRATION-ROOM 1.2.000 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 1.2.000-045
| SHARED ADMINISTRATION- ROOM 1.2.008 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B- ROOM 1.2.008-046
| SHARED ADMINISTRATION-ROOM 1.2.007 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 1.2.007-047
| SHARED ADMINISTRATION- ROOM 1.2.009 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B- ROOM 1.2.009-048
| PALLIATIVE CARE-ROOM 2.1.050 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 2.1.050-049
| PALLIATIVE CARE-ROOM 2.1.058 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 2.1.058-050
| PALLIATIVE CARE- ROOM 2.1.067 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B- ROOM 2.1.067-051
| PALLIATIVE CARE-ROOM 2.1.071 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 2.1.071-052
| PALLIATIVE CARE- ROOM 2.1.075 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B- ROOM 2.1.075-053
| PALLIATIVE CARE-ROOM 2.1.038 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 2.1.038-054
| PALLIATIVE CARE-ROOM 2.1.036 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 2.1.036-055
| PALLIAIVE CARE-ROOM 2.1.035 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 2.1.035-056
| PALLIATIVE CARE-ROOM 2.1.032 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 2.1.032-057
| PALLIATIVE CARE-ROOM 2.1.029 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 2.1.029-058
| PALLIATIVE CARE-ROOM 2.1.022 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 2.1.022-059
| PALLIATIVE CARE-ROOM 2.1.000 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 2.1.000-060
| PALLIATIVE CARE-ROOM 2.1.008 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 2.1.008-061
| PALLIATIVE CARE- ROOM 2.1.011 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B- ROOM 2.1.011-062
| PALLIATIVE CARE-ROOM 2.1.016 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 2.1.016-063
| PALLIATIVE CARE -ROOM 2.1.017 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 2.1.017-064
| SHARED ADMIN-ROOM 2.2.003 | M01B | BMS Sensor | DPA-ITC-M01B | DPA-ITC-M01B-ROOM 2.2.003-065
ELECTRICAL ROUGH IN | MSSB-01-1 | M03 | MSSB Rough in | DPA-ITC-M03 | DPA-ITC-M03-MSSB-01-1-001
| MSSB-01-2 | M03 | MSSB Rough in | DPA-ITC-M03 | DPA-ITC-M03-MSSB-01-2-002
| MSSB-02-1 | M03 | MSSB Rough in | DPA-ITC-M03 | DPA-ITC-M03-MSSB-02-1-003
| MSSB-02-2 | M03 | MSSB Rough in | DPA-ITC-M03 | DPA-ITC-M03-MSSB-02-2-004
| MSSB-02-3 | M03 | MSSB Rough in | DPA-ITC-M03 | DPA-ITC-M03-MSSB-02-3-005
| MSSB-02-4 | M03 | MSSB Rough in | DPA-ITC-M03 | DPA-ITC-M03-MSSB-02-4-006
| MSSB-SUB-1 | M03 | MSSB Rough in | DPA-ITC-M03 | DPA-ITC-M03-MSSB-SUB-1-007
| MSSB-SUB-2 | M03 | MSSB Rough in | DPA-ITC-M03 | DPA-ITC-M03-MSSB-SUB-2-008
| MSSB-PR-1 | M03 | MSSB Rough in | DPA-ITC-M03 | DPA-ITC-M03-MSSB-PR-1-009
| MSSB-FPR-1 | M03 | MSSB Rough in | DPA-ITC-M03 | DPA-ITC-M03-MSSB-FPR-1-010
| IP-MSSB-1E | M03 | MSSB Rough in | DPA-ITC-M03 | DPA-ITC-M03-IP-MSSB-1E-011
ELECTRICAL FIT OFF | MSSB-01-1 | M09 | MSSB Fit off | DPA-ITC-M09 | DPA-ITC-M09-MSSB-01-1-001
| MSSB-01-2 | M09 | MSSB Fit off | DPA-ITC-M09 | DPA-ITC-M09-MSSB-01-2-002
| MSSB-02-1 | M09 | MSSB Fit off | DPA-ITC-M09 | DPA-ITC-M09-MSSB-02-1-003
| MSSB-02-2 | M09 | MSSB Fit off | DPA-ITC-M09 | DPA-ITC-M09-MSSB-02-2-004
| MSSB-02-3 | M09 | MSSB Fit off | DPA-ITC-M09 | DPA-ITC-M09-MSSB-02-3-005
| MSSB-02-4 | M09 | MSSB Fit off | DPA-ITC-M09 | DPA-ITC-M09-MSSB-02-4-006
| MSSB-SUB-1 | M09 | MSSB Fit off | DPA-ITC-M09 | DPA-ITC-M09-MSSB-SUB-1-007
| MSSB-SUB-2 | M09 | MSSB Fit off | DPA-ITC-M09 | DPA-ITC-M09-MSSB-SUB-2-008
| MSSB-PR-1 | M09 | MSSB Fit off | DPA-ITC-M09 | DPA-ITC-M09-MSSB-PR-1-009
| MSSB-FPR-1 | M09 | MSSB Fit off | DPA-ITC-M09 | DPA-ITC-M09-MSSB-FPR-1-010
| IP-MSSB-1E | M09 | MSSB Fit off | DPA-ITC-M09 | DPA-ITC-M09-IP-MSSB-1E-011
PLUMBING | PIPE CHILLER PLANT | M08 | Mechanical Plumbing Installation | DPA-ITC-M08 | DPA-ITC-M08-PIPE CHILLER PLANT - 001
| PIPE LEVEL 1 PLANT ROOM | M08 | Mechanical Plumbing Installation | DPA-ITC-M08 | DPA-ITC-M08-PIPE LEVEL 1 PLANT ROOM -002
| PIPE LEVEL 2 PLANT ROOM | M08 | Mechanical Plumbing Installation | DPA-ITC-M08 | DPA-ITC-M08-PIPE LEVEL 2 PLANT ROOM -003
| PIPE LEVEL 00 | M08 | Mechanical Plumbing Installation | DPA-ITC-M08 | DPA-ITC-M08-PIPE LEVEL 00 -004
| PIPE LEVEL 01 | M08 | Mechanical Plumbing Installation | DPA-ITC-M08 | DPA-ITC-M08-PIPE LEVEL 01-005
| PIPE LEVEL 02 | M08 | Mechanical Plumbing Installation | DPA-ITC-M08 | DPA-ITC-M08-PIPE LEVEL 02-006
DUCTWORK Rough in | AHU-00-1 | M02A | Mechanical Rough In | DPA-ITC-M02A | DPA-ITC-M02A-AHU-00-1-001
| AHU-00-2 | M02A | Mechanical Rough In | DPA-ITC-M02A | DPA-ITC-M02A-AHU-00-2-002
| AHU-00-3 | M02A | Mechanical Rough In | DPA-ITC-M02A | DPA-ITC-M02A-AHU-00-3-003
| AHU-00-4 | M02A | Mechanical Rough In | DPA-ITC-M02A | DPA-ITC-M02A-AHU-00-4-004
| AHU-01-1 | M02A | Mechanical Rough In | DPA-ITC-M02A | DPA-ITC-M02A-AHU-01-1-005
| AHU-01-2 | M02A | Mechanical Rough In | DPA-ITC-M02A | DPA-ITC-M02A-AHU-01-2-006
| AHU-01-3 | M02A | Mechanical Rough In | DPA-ITC-M02A | DPA-ITC-M02A-AHU-01-3-007
| AHU-02-1 | M02A | Mechanical Rough In | DPA-ITC-M02A | DPA-ITC-M02A-AHU-02-1-008
| GEF-00-1 | M05A | Mechanical Rough In | DPA-ITC-M05A | DPA-ITC-M05A-GEF-00-1-001
| KEF-02-1 | M05A | Mechanical Rough In | DPA-ITC-M05A | DPA-ITC-M05A-KEF-02-1-002
| TEF-02-1 | M05A | Mechanical Rough In | DPA-ITC-M05A | DPA-ITC-M05A-TEF-02-1-003
| GEF-02-1 | M05A | Mechanical Rough In | DPA-ITC-M05A | DPA-ITC-M05A-GEF-02-1-004
| TEF-02-2 | M05A | Mechanical Rough In | DPA-ITC-M05A | DPA-ITC-M05A-TEF-02-2-005
| GEF-02-2 | M05A | Mechanical Rough In | DPA-ITC-M05A | DPA-ITC-M05A-GEF-02-2-006
| KEF-02-2 | M05A | Mechanical Rough In | DPA-ITC-M05A | DPA-ITC-M05A-KEF-02-2-007
| MAF-01-1 | M05A | Mechanical Rough In | DPA-ITC-M05A | DPA-ITC-M05AMAF-01-1-008
| SAF-02-1 | M05A | Mechanical Rough In | DPA-ITC-M05A | DPA-ITC-M05A-SAF-02-1-009
| SPF-02-1 | M05A | Mechanical Rough In | DPA-ITC-M05A | DPA-ITC-M05A-SPF-02-1-010
| SPF-02-2 | M05A | Mechanical Rough In | DPA-ITC-M05A | DPA-ITC-M05A-SPF-02-2-011
| LRF-02-1 | M05A | Mechanical Rough In | DPA-ITC-M05A | DPA-ITC-M05A-LRF-02-1-012
| LRF-02-2 | M05A | Mechanical Rough In | DPA-ITC-M05A | DPA-ITC-M05A-LRF-02-2-013
| IP-GEF-07 | M05A | Mechanical Rough In | DPA-ITC-M05A | DPA-ITC-M05A-IP-GEF-07-014
| KEF-02-3 | M05A | Mechanical Rough In | DPA-ITC-M05A | DPA-ITC-M05A-KEF-02-3-014
| SAF-SUB-1 | M05A | Mechanical Rough In | DPA-ITC-M05A | DPA-ITC-M05A-SAF-SUB-1-015
| SAF-SUB-2 | M05A | Mechanical Rough In | DPA-ITC-M05A | DPA-ITC-M05A-SAF-SUB-2-016
| GEF-PR-1 | M05A | Mechanical Rough In | DPA-ITC-M05A | DPA-ITC-M05A-GEF-PR-1-017
| GEF-FPR-1 | M05A | Mechanical Rough In | DPA-ITC-M05A | DPA-ITC-M05A-GEF-FPR-1-018
| GEF-BIN-1 | M05A | Mechanical Rough In | DPA-ITC-M05A | DPA-ITC-M05A-GEF-BIN-1-019
| FCU-00-1 | M02A | Mechanical Rough In | DPA-ITC-M02A | DPA-ITC-M02A-FCU-00-1 -009
| FCU-00-2 | M02A | Mechanical Rough In | DPA-ITC-M02A | DPA-ITC-M02A-FCU-00-2 010
| FCU-MSB-01 | M02A | Mechanical Rough In | DPA-ITC-M02A | DPA-ITC-M02A-FCU-MSB-01-011
| FCU-MSB-02 | M02A | Mechanical Rough In | DPA-ITC-M02A | DPA-ITC-M02A-FCU-MSB-02-012
| FCU-MSB-03 | M02A | Mechanical Rough In | DPA-ITC-M02A | DPA-ITC-M02A-FCU-MSB-03-013
| FCU-MSB-04 | M02A | Mechanical Rough In | DPA-ITC-M02A | DPA-ITC-M02A-FCU-MSB-04-014
DUCTWORK Fit off | AHU-00-1 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-AHU-00-1-001
| AHU-00-2 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-AHU-00-2-002
| AHU-00-3 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-AHU-00-3-003
| AHU-00-4 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-AHU-00-4-004
| AHU-01-1 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-AHU-01-1-005
| AHU-01-2 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-AHU-01-2-006
| AHU-01-3 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-AHU-01-3-007
| AHU-02-1 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-AHU-02-1-008
| GEF-00-1 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-GEF-00-1-009
| KEF-02-1 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-KEF-02-1-010
| TEF-02-1 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-TEF-02-1-011
| GEF-02-1 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-GEF-02-1-012
| TEF-02-2 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-TEF-02-2-013
| GEF-02-2 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-GEF-02-2-014
| KEF-02-2 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-KEF-02-2-015
| MAF-01-1 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-MAF-01-1-016
| SAF-02-1 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-SAF-02-1-017
| SPF-02-1 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-SPF-02-1-018
| SPF-02-2 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-SPF-02-2-019
| LRF-02-1 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-LRF-02-1-020
| LRF-02-2 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-LRF-02-2-021
| IP-GEF-07 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-IP-GEF-07-022
| KEF-02-3 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-KEF-02-3-023
| SAF-SUB-1 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-SAF-SUB-1-024
| SAF-SUB-2 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-SAF-SUB-2-025
| GEF-PR-1 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-GEF-PR-1-026
| GEF-FPR-1 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-GEF-FPR-1-027
| GEF-BIN-1 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-GEF-BIN-1-028
| FCU-00-1 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-FCU-00-1 -029
| FCU-00-2 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-FCU-00-2 -030
| FCU-MSB-01 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-FCU-MSB-01-031
| FCU-MSB-02 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-FCU-MSB-02-032
| FCU-MSB-03 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-FCU-MSB-03-033
| FCU-MSB-04 | M02B | Mechanical Fit off | DPA-ITC-M02B | DPA-ITC-M02B-FCU-MSB-04-034
MECHANICAL COMMISSIONING | AHU-00-1
AHU-00-2
AHU-00-3
AHU-00-4
AHU-01-1
AHU-01-2
AHU-01-3
AHU-02-1
GEF-00-1
KEF-02-1
TEF-02-1
GEF-02-1
TEF-02-2
GEF-02-2
KEF-02-2
MAF-01-1
SAF-02-1
SPF-02-1
SPF-02-2
LRF-02-1
LRF-02-2
IP-GEF-07
KEF-02-3
SAF-SUB-1
SAF-SUB-2
GEF-PR-1
GEF-FPR-1
GEF-BIN-1
WATER BALANCING
MSSB-01-1
MSSB-01-2
MSSB-02-1
MSSB-02-2
MSSB-02-3
MSSB-02-4
MSSB-SUB-1
MSSB-SUB-2
MSSB-PR-1
MSSB-FPR-1
IP-MSSB-1E
BMS POINT TO POINT COMMISSIONING
BMS FUNCTIONAL TESTING
CU-00-1 SYSTEM - AC-00-1.1 AND AC-00-1.2
CU-00-2 SYSTEM - AC-00-2.1 AND AC-00-2.2
CU-00-3 SYSTEM - AC-00-3.1 AND AC-00-3.2
CU-00-4 SYSTEM - AC-00-4.1 AND AC-00-4.2
CU-01-1 SYSTEM - AC-01-1.1 AND AC-01-1.2
CU-01-2 SYSTEM - AC-01-2.1 AND AC-01-2.2
CU-02-1 SYSTEM - AC-02-1.1 AND AC-02-1.2
CU-02-2 SYSTEM - AC-02-2.1 AND AC-02-2.2
CU-02-3 SYSTEM - AC-02-3
CU-02-4 SYSTEM - AC-02-4
CU-02-5 SYSTEM - AC-02-5
CU-02-6 SYSTEM - AC-02-6
CU-SMSR-1 SYSTEM - AC-SMSR-1.1 AND AC-SMSR-1.2 AND AC-SMSR-1.3
CU-SMSR-2 SYSTEM - AC-SMSR-2.1 AND AC-SMSR-2.2 AND AC-SMSR-2.3
CU-PR-1 SYSTEM - AC-PR-1.1 AND AC-PR-1.2
CU-00-5 SYSTEM - AC-00-5
CU-00-6 SYSTEM - AC-00-6
MEDICAL GASSES
WATER TREATMENT
Insulation | DUCT INSULATION LEVEL 1 PLANT ROOM | M10 | Ductwork Insulation | DPA-ITC-M10 | DPA-ITC-M10-DUCT INSULATION LEVEL 1 PLANT ROOM -001
| DUCT INSULATION LEVEL 2 PLANT ROOM | M10 | Ductwork Insulation | DPA-ITC-M10 | DPA-ITC-M10-DUCT INSULATION LEVEL 2 PLANT ROOM -002
| DUCT INSULATION LEVEL 00 | M10 | Ductwork Insulation | DPA-ITC-M10 | DPA-ITC-M10-DUCT INSULATION LEVEL 00 -003
| DUCT INSULAITON LEVEL 01 | M10 | Ductwork Insulation | DPA-ITC-M10 | DPA-ITC-M10-DUCT INSULAITON LEVEL 01 -004
| DUCT INSULATION LEVEL 02 | M10 | Ductwork Insulation | DPA-ITC-M10 | DPA-ITC-M10-DUCT INSULATION LEVEL 02 -005
| PIPE INSULATION CHILLER PLANT | M11 | Pipe Insulation | DPA-ITC-M11 | DPA-ITC-M11-PIPE INSULATION CHILLER PLANT-001
| PIPE INSULATION LEVEL 1 PLANT ROOM | M11 | Pipe Insulation | DPA-ITC-M11 | DPA-ITC-M11-PIPE INSULATION LEVEL 1 PLANT ROOM-002
| PIPE INSULATION LEVEL 2 PLANT ROOM | M11 | Pipe Insulation | DPA-ITC-M11 | DPA-ITC-M11-PIPE INSULATION LEVEL 2 PLANT ROOM-003
| PIPE INSULATION LEVEL 00 | M11 | Pipe Insulation | DPA-ITC-M11 | DPA-ITC-M11-PIPE INSULATION LEVEL 00-004
| PIPE INSULATION LEVEL 01 | M11 | Pipe Insulation | DPA-ITC-M11 | DPA-ITC-M11-PIPE INSULATION LEVEL 01-005
| PIPE INSULATION LEVEL 02 | M11 | Pipe Insulation | DPA-ITC-M11 | DPA-ITC-M11-PIPE INSULATION LEVEL 02-006

## Dewpoint (hidden)
ITP Worklot Register
Subcontractor | Dewpoint
Services Discipline | ITP Name | ITP Prefix (refer next sheet for prefixes) | ITP Type | Work Lot No. | ITC no. | Status | Date | HB Review By | HB Review Date | Comments
e.g., Electrical Services | Electrical Distribution Board (DB-RENAL) | E02 | DB | PER-ITC-E02 | PER-ITC-E02-001 | Open | 2022-12-08 |  |  | Half complete, remainder to be completed by 5/12

## Mech Plumbing (hidden)
ITP Worklot Register
Subcontractor | Cold Control
Services Discipline | ITP Name | ITP Prefix (refer next sheet for prefixes) | ITP Type | Worklot No. | ITP No. | Status | Date | HB Review By | HB Review DateDate | Comments
e.g., Electrical Services | Electrical Distribution Board (DB-RENAL) | E02 | DB | PER-ITC-E02 | PER-ITC-E02-001 | Open | 2022-12-08

## Mech Elec (hidden)
ITP Worklot Register
Subcontractor | EMES
Services Discipline | ITP Name | ITP Prefix (refer next sheet for prefixes) | ITP Type | Worklot No. | ITP No. | Status | Date | HB Review By | HB Review Date | Comments
e.g., Electrical Services | Electrical Distribution Board (DB-RENAL) | E02 | DB | PER-ITC-E02 | PER-ITC-E02-001 | Open | 2022-12-08

## BMS (hidden)
ITP Worklot Register
Subcontractor | Inco Solutions
Services Discipline | ITP Name | ITP Prefix (refer next sheet for prefixes) | ITP Type | Worklot No. | ITP No. | Status | Date | HB Review By | HB Review Date | COMMENTS
e.g., Electrical Services | Electrical Distribution Board (DB-RENAL) | E02 | DB | PER-ITC-E02 | PER-ITC-E02-001 | Open | 2022-12-08

## DX (hidden)
ITP Worklot Register
Subcontractor | Airmoys
Services Discipline | ITP Name | ITP Prefix (refer next sheet for prefixes) | ITP Type | Worklot No. | ITP No. | Status | Date | HB Review By | HB Review Date | Comments | DPA Comments
e.g., Electrical Services | Electrical Distribution Board (DB-RENAL) | E02 | DB | PER-ITC-E02 | PER-ITC-E02-001 | Open | 2022-12-08

## Medgas (hidden)
ITP Worklot Register
Subcontractor | BOC
Services Discipline | ITP Name | ITP Prefix (refer next sheet for prefixes) | ITP Type | Worklot No. | ITP No. | Status | Date | HB Review By | HB Review Date | Comments
e.g., Electrical Services | Electrical Distribution Board (DB-RENAL) | E02 | DB | PER-ITC-E02 | PER-ITC-E02-001 | Open | 2022-12-08 |  |  | Half complete, remainder to be completed by 5/12