## Watermain Upgrade
Quality Control Plan |  | Site Location: _______________________________________________ |  |  |  |  | Prepared By: | Paul Loveridge Date: 28/4/22 R2
Contract No. / Project Name: 22-007 Whakatane Water Main Renewals Panel |  |  |  | Scope of Work: Installation of new water mains, valves, hydrants, and lot connecdtions
Activity | Detail of Activity | Hold Point | When/ How often | Inspection / Test Method | Acceptance Criteria / specification reference | Record required or sign and date when completed | Responsibe | Comments | Completed | Filed Contractor | Sent Engineer
Pre Start
WAP & TMP | WAP applied for & TMP written and approved | Y | Prior to work starting | N/A | Approved WAP & TMP | Approved documents received | Project Manager
SSSP and EMP | Hazards identified SSSP and EMP written and approved | Y | Prior to work starting | N/A | Approved by Engineer / Approved document on site. | NTC from Engineer | Safety Manager
Procure Materials | Order Pipe & fittings for project |  | Prior to work starting | N/A | Materials on approved materials list |  | Project Manager
Service Plans | B4U Dig request made |  | Prior to work starting | N/A | Plans of all services received | Plans on site | Site Supervisor
Letter Drop | Deliver work notification letters to affected parties in and around work area. | Y | 5 days before work starts | N/A | Delivered to affected parties |  | Site Supervisor
SSSP and EMP | SSSP and EMP Implemented |  | Daily | Documented | Documentation completed | Tool box, Daily Pre-start | Site Supervisor/Foreman
TMP | TMP implemented | Y | As required | Visual/Documented | As per approved TMP | On-Site Record | STMS
Site condition record | Record original condition of site and surroundings | Y | All affected properties | Documented by photos/video | Date stamped with location phots and videos | Site condition record + video's and photo's | Site Supervisor
Construction
Pipe Delivery | Delivery of pipe to worksite |  | As received | Visual | Meets specification, quanity as per delivery docket, no defects. |  | Site Supervisor | delivery docket checked and givewn to accounts, all pipe ends capped.
Materials Reciept | Receiving materials for fittings etc |  | As received | visual | Meets specification, quanity as per delivery docket, no defects. |  | Site Supervisor | delivery docket checked and givewn to accounts.
Weld strings | Weld pipe strings |  | When required | Visual |  | Data report from welding machine | Welder | Welder to ensure project details are entered into welder.
Weld test | Butt Weld(s) removed and sent to lab for testing | Y | Start of welding | Tensile Fracture | As per ISO 13953 | Opus Test Report | Site Supervisor
Services Marked | Mark out of underground Services | Y | Before Excavation | Visual Inspection | Marks match plans | Video/Photo Record | Site Supervisor
Locate services | Services located by hydrovacing and pot holing | Y | For pipeline | Visual Inspection | All known services located | Video/Photo Record | Site Supervisor | Any existing damage to services notified to engineer.
Allignment | Allignment of new pipeline confirmed with Engineer |  | As required | Visual Inspection |  | NTC from Engineer | Site Supervisor
Drill Plan | Plan drill shots to install pipeline | Y | Prior to drilling | Visual Inspection |  | Marked on Plan | Drilling Foreman
Pipe line construction | Pipe installed by directional drilling or open cut with tracer wire |  | Daily till copmplete | Visual Inspection | Installed as per Contract spec 2.57 & 2.58 & Engineering Code of Practice | IC201 - Pipe laying -Directional Drilling | Drilling Foreman
Archeological discovery | Accidental discovery of an archilogical site | Y | If discovered | Visual | Refer to 1.16.16 for protocols. |  | Site Supervisor
Pipe line construction | Join strings with EF Couplers, join tracer wire |  | Each join | Visual/Documented |  | IC202 - Electrofusion Weld | Welder
Pipe line construction | Construction pipe weld test |  |  | Destruction Test | Pass weld test | Opus Test | Site Supervisor | as per Engineers Request
Valves and Hydrants | Install Valves & Hydrants on new pipeline |  | As per plans | Visual Inspection | Installed as per Engineering Code of Practice | CI 204 Valve/Hydrant | Water Tech
Lot Connections | Install new lot connections to pipeline |  | Where required | Visual Inspection | Installed as per Engineering Code of Practice | CI 203 Lot connection detail | Water Tech
Commisioning
Pressure test | Pressure test new pipeline and fittings | Y | Once constructed | Re-Bound test | Succesful bounce test m7 or reference test m5 | Test Report signed by engineer | Water Tech
Flush lines | Pig all lines | Y | Once constructed | Visual Inspection | After pigging water is clear |  | Water Tech
Disenfection | Chlorinate all pipe lines and fittings | Y | Once Lines flushed | Water sample | Engineer to witness | Photo's of FAC test strips | Water Tech
Flush lines | Flush chlorinated water from lines | Y | Once successful chlorination | Water sample | Pass E-Coli Test | Lab Test Result | Site Supervisor
Water Shut down | Connect new lines to existing lines and water connections | Y | Once testing Completed | N/A | Water shut down plan accepted by WDC | Water Shut Down Notice | Site Supervisor
Project Wrap Up
Reinstatement | Reinstate all surfaces to original condition or better |  | After connections complete | Visual Inspection | As per Engineering Code of Practice |  | Site Supervisor
Final Inspection with Engineer | Site walk over with Engineer |  | Once all works completed | Visual Inspection | Acceptance by Engineer | Defects list | Site Supervisor
As Builts | Surveyor to draw up as builts |  | Once all works completed | N/A | Acceptance by Engineer as per 1.21 | As-Built Drawings | Project Manager
Practical Completion | Certificate given by Engineer |  | When requested | N/A | Given by Engineer | Practical Completion Certificate | Project Manager