## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | Quality Control Plan - Installation of new water mains, valves, hydrants, and lot connections | itp |  |  |  |  | Quality Control Plan - Installation of new water mains, valves, hydrants, and lot connections
section | Pre Start
checkpoint | WAP & TMP
label | DETAIL OF ACTIVITY - WAP applied for & TMP written and approved
label | HOLD POINT - Y
label | WHEN/HOW OFTEN - Prior to work starting
label | INSPECTION/TEST METHOD - N/A
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - Approved WAP & TMP
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - Approved documents received
label | RESPONSIBLE - Project Manager
holdpoint | HOLD POINT
checkpoint | SSSP and EMP
label | DETAIL OF ACTIVITY - Hazards identified SSSP and EMP written and approved
label | HOLD POINT - Y
label | WHEN/HOW OFTEN - Prior to work starting
label | INSPECTION/TEST METHOD - N/A
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - Approved by Engineer / Approved document on site.
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - NTC from Engineer
label | RESPONSIBLE - Safety Manager
holdpoint | HOLD POINT
checkpoint | Procure Materials
label | DETAIL OF ACTIVITY - Order Pipe & fittings for project
label | WHEN/HOW OFTEN - Prior to work starting
label | INSPECTION/TEST METHOD - N/A
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - Materials on approved materials list
label | RESPONSIBLE - Project Manager
checkpoint | Service Plans
label | DETAIL OF ACTIVITY - B4U Dig request made
label | WHEN/HOW OFTEN - Prior to work starting
label | INSPECTION/TEST METHOD - N/A
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - Plans of all services received
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - Plans on site
label | RESPONSIBLE - Site Supervisor
checkpoint | Letter Drop
label | DETAIL OF ACTIVITY - Deliver work notification letters to affected parties in and around work area.
label | HOLD POINT - Y
label | WHEN/HOW OFTEN - 5 days before work starts
label | INSPECTION/TEST METHOD - N/A
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - Delivered to affected parties
label | RESPONSIBLE - Site Supervisor
holdpoint | HOLD POINT
checkpoint | SSSP and EMP
label | DETAIL OF ACTIVITY - SSSP and EMP Implemented
label | WHEN/HOW OFTEN - Daily
label | INSPECTION/TEST METHOD - Documented
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - Documentation completed
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - Tool box, Daily Pre-start
label | RESPONSIBLE - Site Supervisor/Foreman
checkpoint | TMP
label | DETAIL OF ACTIVITY - TMP implemented
label | HOLD POINT - Y
label | WHEN/HOW OFTEN - As required
label | INSPECTION/TEST METHOD - Visual/Documented
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - As per approved TMP
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - On-Site Record
label | RESPONSIBLE - STMS
checkpoint | Site condition record
label | DETAIL OF ACTIVITY - Record original condition of site and surroundings
label | HOLD POINT - Y
label | WHEN/HOW OFTEN - All affected properties
label | INSPECTION/TEST METHOD - Documented by photos/video
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - Date stamped with location phots and videos
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - Site condition record + video's and photo's
label | RESPONSIBLE - Site Supervisor
holdpoint | HOLD POINT
section | Construction
checkpoint | Pipe Delivery
label | DETAIL OF ACTIVITY - Delivery of pipe to worksite
label | WHEN/HOW OFTEN - As received
label | INSPECTION/TEST METHOD - Visual
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - Meets specification, quanity as per delivery docket, no defects.
label | RESPONSIBLE - Site Supervisor
label | COMMENTS - delivery docket checked and givewn to accounts, all pipe ends capped.
checkpoint | Materials Reciept
label | DETAIL OF ACTIVITY - Receiving materials for fittings etc
label | WHEN/HOW OFTEN - As received
label | INSPECTION/TEST METHOD - visual
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - Meets specification, quanity as per delivery docket, no defects.
label | RESPONSIBLE - Site Supervisor
label | COMMENTS - delivery docket checked and givewn to accounts.
checkpoint | Weld strings
label | DETAIL OF ACTIVITY - Weld pipe strings
label | WHEN/HOW OFTEN - When required
label | INSPECTION/TEST METHOD - Visual
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - Data report from welding machine
label | RESPONSIBLE - Welder
label | COMMENTS - Welder to ensure project details are entered into welder.
checkpoint | Weld test
label | DETAIL OF ACTIVITY - Butt Weld(s) removed and sent to lab for testing
label | HOLD POINT - Y
label | WHEN/HOW OFTEN - Start of welding
label | INSPECTION/TEST METHOD - Tensile Fracture
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - As per ISO 13953
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - Opus Test Report
label | RESPONSIBLE - Site Supervisor
holdpoint | HOLD POINT
checkpoint | Services Marked
label | DETAIL OF ACTIVITY - Mark out of underground Services
label | HOLD POINT - Y
label | WHEN/HOW OFTEN - Before Excavation
label | INSPECTION/TEST METHOD - Visual Inspection
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - Marks match plans
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - Video/Photo Record
label | RESPONSIBLE - Site Supervisor
holdpoint | HOLD POINT
checkpoint | Locate services
label | DETAIL OF ACTIVITY - Services located by hydrovacing and pot holing
label | HOLD POINT - Y
label | WHEN/HOW OFTEN - For pipeline
label | INSPECTION/TEST METHOD - Visual Inspection
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - All known services located
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - Video/Photo Record
label | RESPONSIBLE - Site Supervisor
label | COMMENTS - Any existing damage to services notified to engineer.
holdpoint | HOLD POINT
checkpoint | Allignment
label | DETAIL OF ACTIVITY - Allignment of new pipeline confirmed with Engineer
label | WHEN/HOW OFTEN - As required
label | INSPECTION/TEST METHOD - Visual Inspection
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - NTC from Engineer
label | RESPONSIBLE - Site Supervisor
checkpoint | Drill Plan
label | DETAIL OF ACTIVITY - Plan drill shots to install pipeline
label | HOLD POINT - Y
label | WHEN/HOW OFTEN - Prior to drilling
label | INSPECTION/TEST METHOD - Visual Inspection
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - Marked on Plan
label | RESPONSIBLE - Drilling Foreman
holdpoint | HOLD POINT
checkpoint | Pipe line construction
label | DETAIL OF ACTIVITY - Pipe installed by directional drilling or open cut with tracer wire
label | WHEN/HOW OFTEN - Daily till copmplete
label | INSPECTION/TEST METHOD - Visual Inspection
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - Installed as per Contract spec 2.57 & 2.58 & Engineering Code of Practice
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - IC201 - Pipe laying -Directional Drilling
label | RESPONSIBLE - Drilling Foreman
checkpoint | Archeological discovery
label | DETAIL OF ACTIVITY - Accidental discovery of an archilogical site
label | HOLD POINT - Y
label | WHEN/HOW OFTEN - If discovered
label | INSPECTION/TEST METHOD - Visual
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - Refer to 1.16.16 for protocols.
label | RESPONSIBLE - Site Supervisor
holdpoint | HOLD POINT
checkpoint | Pipe line construction
label | DETAIL OF ACTIVITY - Join strings with EF Couplers, join tracer wire
label | WHEN/HOW OFTEN - Each join
label | INSPECTION/TEST METHOD - Visual/Documented
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - IC202 - Electrofusion Weld
label | RESPONSIBLE - Welder
checkpoint | Pipe line construction
label | DETAIL OF ACTIVITY - Construction pipe weld test
label | INSPECTION/TEST METHOD - Destruction Test
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - Pass weld test
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - Opus Test
label | RESPONSIBLE - Site Supervisor
label | COMMENTS - as per Engineers Request
checkpoint | Valves and Hydrants
label | DETAIL OF ACTIVITY - Install Valves & Hydrants on new pipeline
label | WHEN/HOW OFTEN - As per plans
label | INSPECTION/TEST METHOD - Visual Inspection
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - Installed as per Engineering Code of Practice
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - CI 204 Valve/Hydrant
label | RESPONSIBLE - Water Tech
checkpoint | Lot Connections
label | DETAIL OF ACTIVITY - Install new lot connections to pipeline
label | WHEN/HOW OFTEN - Where required
label | INSPECTION/TEST METHOD - Visual Inspection
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - Installed as per Engineering Code of Practice
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - CI 203 Lot connection detail
label | RESPONSIBLE - Water Tech
section | Commissioning
checkpoint | Pressure test
label | DETAIL OF ACTIVITY - Pressure test new pipeline and fittings
label | HOLD POINT - Y
label | WHEN/HOW OFTEN - Once constructed
label | INSPECTION/TEST METHOD - Re-Bound test
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - Succesful bounce test m7 or reference test m5
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - Test Report signed by engineer
label | RESPONSIBLE - Water Tech
holdpoint | HOLD POINT
checkpoint | Flush lines
label | DETAIL OF ACTIVITY - Pig all lines
label | HOLD POINT - Y
label | WHEN/HOW OFTEN - Once constructed
label | INSPECTION/TEST METHOD - Visual Inspection
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - After pigging water is clear
label | RESPONSIBLE - Water Tech
holdpoint | HOLD POINT
checkpoint | Disenfection
label | DETAIL OF ACTIVITY - Chlorinate all pipe lines and fittings
label | HOLD POINT - Y
label | WHEN/HOW OFTEN - Once Lines flushed
label | INSPECTION/TEST METHOD - Water sample
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - Engineer to witness
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - Photo's of FAC test strips
label | RESPONSIBLE - Water Tech
holdpoint | HOLD POINT
checkpoint | Flush lines
label | DETAIL OF ACTIVITY - Flush chlorinated water from lines
label | HOLD POINT - Y
label | WHEN/HOW OFTEN - Once successful chlorination
label | INSPECTION/TEST METHOD - Water sample
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - Pass E-Coli Test
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - Lab Test Result
label | RESPONSIBLE - Site Supervisor
holdpoint | HOLD POINT
checkpoint | Water Shut down
label | DETAIL OF ACTIVITY - Connect new lines to existing lines and water connections
label | HOLD POINT - Y
label | WHEN/HOW OFTEN - Once testing Completed
label | INSPECTION/TEST METHOD - N/A
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - Water shut down plan accepted by WDC
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - Water Shut Down Notice
label | RESPONSIBLE - Site Supervisor
holdpoint | HOLD POINT
section | Project Wrap Up
checkpoint | Reinstatement
label | DETAIL OF ACTIVITY - Reinstate all surfaces to original condition or better
label | WHEN/HOW OFTEN - After connections complete
label | INSPECTION/TEST METHOD - Visual Inspection
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - As per Engineering Code of Practice
label | RESPONSIBLE - Site Supervisor
checkpoint | Final Inspection with Engineer
label | DETAIL OF ACTIVITY - Site walk over with Engineer
label | WHEN/HOW OFTEN - Once all works completed
label | INSPECTION/TEST METHOD - Visual Inspection
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - Acceptance by Engineer
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - Defects list
label | RESPONSIBLE - Site Supervisor
checkpoint | As Builts
label | DETAIL OF ACTIVITY - Surveyor to draw up as builts
label | WHEN/HOW OFTEN - Once all works completed
label | INSPECTION/TEST METHOD - N/A
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - Acceptance by Engineer as per 1.21
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - As-Built Drawings
label | RESPONSIBLE - Project Manager
checkpoint | Practical Completion
label | DETAIL OF ACTIVITY - Certificate given by Engineer
label | WHEN/HOW OFTEN - When requested
label | INSPECTION/TEST METHOD - N/A
label | ACCEPTANCE CRITERIA/SPECIFICATION REFERENCE - Given by Engineer
label | RECORD REQUIRED OR SIGN AND DATE WHEN COMPLETED - Practical Completion Certificate
label | RESPONSIBLE - Project Manager